## Allocated TNKs FABs
Stationary container design and fabricator records as of 4 May 2026
Approval Number | Date of Registration | Name of Designer (TNK) | Name of Fabricator (FAB) | Tank Type/Design (TNK) or Register no. (FAB) | Tank Details (TNK) | HS Class Designed For (TNK) | Approval To | Conditions (Please see the approval for specific conditions of approval) | Expiry Date | Comments | Previous OSH Number (TNK)
| 1978-06-09 | Rheem |  | Aboveground Tanks | Farm Storage | 3 | Rheem |  |  |  | (28/78)
| 1980-02-25 | Rockgas |  | Transportable Tanks | transportable, E20-1 to 8 | 2d | Worley DM Ltd |  |  |  | (63/80)
LAB 4 | 1980-07-18 | Rheem |  | Farm Tank | 1000&2000 l, 111200-65/66/68 | 3 | Rheem |  |  |  | (77/80)
| 1982-11-19 | Target Ind. |  | Farm S. Tanks | Over-head P114, P116, 103, 104 | 3 | Target Ind. |  |  |  | (118/82)
| 1983-03-31 | Shell Oil |  | Integ.Tank/Disp | 7000 Litre, 900g 305 | 2d | Shell Oil |  |  |  | 122/83
108, 109 | 1983-07-27 | Bennett-Beck |  | Integ.Tank/Disp | 4015, 4150 | 2d | D MclWallace |  |  |  | 126/83
LAB 108 | 1983-07-27 | Bennett-Beck |  | Integ.Tank/Disp | 4015, 4150 | 2d | D MclWallace |  |  |  | 126/83
| 1983-10-03 | BP NZ Ltd |  | Integ.Tank/Disp. | 7499 litre, LPG 1386/1/2 | 2d | BP NZ Ltd |  |  |  | 132/83
| 1984-10-02 | BP NZ Ltd |  | Integ.Tank/Disp. | 4500 lt. LPG1385/1 | 2d | BP NZ Ltd. |  |  |  | 146/84
| 1984-12-06 | Rheem/Indeng |  | Storage Tank | 2&4 tonne, NZIG Dwg 206369 | 2d | NZIG Ltd. |  |  | see 20/77 & 24/78 | 153/85
| 1985-02-21 | Anderson |  | Storage Tank | 2&4 tonne, NZIG Dwg 206369 | 2d | NZIG Ltd |  |  |  | 152/85
| 1989-07-11 |  |  | Compartmentised Tank |  | 3 |  |  |  |  | 235/89
LAB 561 | 1990-06-08 | Hamilton MetFab |  | Aluminium Tank | 500/5001 dual | 3 | Hamilton MetFab |  |  |  | 249/90
LAB 843 | 1992-02-06 | Skellerup 1000L |  | IBC for Hydr. Peroxide |  | 5a | Skellerup 1000L |  |  |  | 295/92
| 1992-02-06 | Maskell Production Ltd. |  | Dble Wal GRP U.Stor. |  | 3 | Maskell Prod. |  |  |  | 292/92
| 1992-02-06 | Rheem NZ |  | Dual skin U.Stge Tanks |  | 3 | Rheem NZ |  |  |  | 293/92
| 1992-06-09 | I H Baily |  | IBC DG | 1000L, UN898 |  | I H Baily |  |  |  | 314/92
| 1992-11-02 |  |  | Ameron Dualoy | 3000 L | [5 empty] | 336/92
LAB 3080 | 1993-12-23 |  |  | MOBILE FLAMMABLE LIQ. TANK | Model GC30 LAB 3080 | 3 | Bland Bros.Ltd |  |  |  | 373/93
LAB 3086 | 1994-05-25 | Flow Bin |  | IBC CONTAINER |  | 3 | Electric Control |  |  |  | 386/94
TNK0816 | 1994-09-14 | Fuelquip (NZ) Ltd |  | 40,000L Portable Field Storage and dispenser units | 40,000L | Diesel (Class 3C products) | Fuelquip | Original DOL approval notification number is 397/94, granted in september 1994 by Roger Marshall. Original DoL approval contains conditions; Fuelquip and ERMA have copies of this. |  | Originally approved in 1994; entered into register 01 Oct 2008. | 397/94
| 1995-03-02 | Advanced Polymer Technology |  | NON METALLIC APT POLYTECH | DOUBLE CONTAINMENT PIPING SYSTEM | 3 | LIQUIP |  |  |  | 404/95
| 1995-06-12 | STM Engineering |  | AG TANK | 500 LITRE FORM TANK | 3 |  |  |  |  | 415/95
| 1995-06-22 | STP Flo Bin Pty Ltd |  | BULK CONTAINER | IBC | 3 |  |  |  |  | 424/95
| 1995-08-30 | BP NZ Ltd |  | Farm Tank | AST 3420 | 3 | BP |  |  |  | 432/95
| 1995-09-26 | Petroleum Equipment |  | DBL WALL PIPE |  | 3 |  |  |  |  | 435/95
| 1996-01-16 | A F Martin Ltd |  | STORAGE TANK | A & B | 3 |  |  |  |  | 443/96
| 1996-01-17 | Mainline Sheetmetals Ltd., Hamilton |  | STORAGE TANK | A & B | 3 |  |  |  |  | 444/96
| 1996-01-17 | Greentank Ltd |  | U G TANK | FIBRE GLASS | 3 | POLY CRAFT |  |  |  | 445/96
| 1996-02-07 |  |  | STM INTERGRATED |  | 3C | SMT GROUP LTD |  |  |  | 447/96
LAB 3107 | 1996-03-29 | McFarlane & Murry |  | IBC CONTAINER | FATMAC 1000 1184 Kg | 3 |  |  |  |  | 458/96
LAB 3108 | 1996-04-29 | Amtec Engineering |  | IBC CONTAINER | AMTEC 5260&2630 Kg | 3 |  |  |  |  | 459/96
| 1996-05-10 | Convault Storage |  | AG TANK | 6000 US GAL | 3C | NZ McKAY HARDGRAVE |  |  |  | 462/96
| 1996-08-30 | Multi Form Tanks |  | IBC CONTAINER MULTI FORM 1000 | HYDROGEN PEROXIDE | 5 | MULTI FORM TANKS LTD |  |  |  | 471/96
| 1996-08-30 | Hamilton Oil Services Ltd |  | AG TANKS 1) 1400 LTR | AVIATION REFUELLER DRW A0, A1, A2, A3 | 3A | HAMILTON OIL SERVICES |  |  |  | 472/96
| 1996-08-30 | Hamilton Oil Services Ltd |  | AG TANKS 2) 1400 LTR | AVIATION REFUELLER DRW B0, B1, B2 & B3 | 3B | HAMILTON OIL SERVICES |  |  |  | 472/96
| 1996-08-30 | Hamilton Oil Services Ltd |  | AG TANKS 3) 1400 LTR | DIESEL REFUELLER DRW C0, C1, C2 & C3 | 3C | HAMILTON OIL SERVICES |  |  |  | 472/96
| 1996-08-30 | Hamilton Oil Services Ltd |  | AG TANKS 4) 5000 LTR | DIESEL UNIT PORTABLE | 3C | HAMILTON OIL SERVICES |  |  |  | 472/96
| 1996-08-30 | Hamilton Oil Services Ltd |  | AG TANKS 5) 50000 LTR | TANK & BUND & SLEDGE A1, A2 & A3 |  | HAMILTON OIL SERVICES |  |  |  | 472/96
| 1996-08-30 | Hamilton Oil Services Ltd |  | AG TANKS 6) 10000 LTR | AVIATION UNIT DRW 1, 2 & 3 | 3A | HAMILTON OIL SERVICES |  |  |  | 472/96
| 1996-08-30 | Hamilton Oil Services Ltd |  | AG TANKS 7) 20000 LTR | FUEL TANK & BUND DRW 4687.20 K-1 TO 3 | 3A | HAMILTON OIL SERVICES |  |  |  | 472/96
| 1996-09-23 | A F Martin Ltd |  | AG TANKS 30000 LTR | DBL SKINNED REFUELLER | 3 | A F MARTIN LTD |  |  |  | 475/96
| 1996-09-24 | Steel Tank Manufacturing |  | AG TANKS 1) 400 LTR | STANDARD & ENVIRO | 3 | STEEL TANK MNFCTG |  |  |  | 476/96
| 1996-09-24 | Steel Tank Manufacturing |  | AG TANKS 2) 500 LTR | STANDARD & ENVIRO | 3 | STEEL TANK MNFCTG |  |  |  | 476/96
| 1996-09-24 | Steel Tank Manufacturing |  | AG TANKS 3) 10000 LTR | STANDARD & ENVIRO | 3 | STEEL TANK MNFCTG |  |  |  | 476/96
| 1996-09-24 | Steel Tank Manufacturing |  | AG TANKS 4) 2000 LTR | STANDARD & ENVIRO | 3 | STEEL TANK MNFCTG |  |  |  | 476/96
| 1996-09-24 | Steel Tank Manufacturing |  | AG TANKS 5) 5000 TO 60000 LTR | IBT | 3 | STEEL TANK MNFCTG |  |  |  | 476/96
| 1996-09-24 | Steel Tank Manufacturing |  | AG TANKS 6) DUAL AXLE TRAILER | SINGLE AXLE TRAILER TANK | 3B | STEEL TANK MNFCTG |  |  |  | 476/96
| 1996-09-24 | Hamilton Oil Services Ltd |  | AG TANKS10000 LTR | RELOCATABLE AG TANK & BUND | 3C | HAMILTON OIL SERVICES |  |  |  | 477/96
| 1996-12-10 | Volvo Truck Australia Pty |  | FUEL TANK 415 LITRE | PART NO.8139940 PO6 DRW 8139909 | 3A | VOLVO TRUCK AUSTRALIA PTY |  |  |  | 493/96
| 1997-01-01 | Envirotank |  | FIBREGLASS UGST 1200 MM DIAM UP TO 5000 LITRES | SINGLE WALL & DOUBLE WALL | 3 | MASKELL PRODUCTIONS LTD |  |  |  | 528/97
| 1997-01-01 | Envirotank |  | FIBREGLASS UGST 2000 MM DIA10000 TO 30000 LITRES |  | 3 | MASKELL PRODUCTIONS LTD |  |  |  | 528/97
| 1997-01-01 | Envirotank |  | FIBREGLASS UGST 250MM DIA20000 TO 60000 LITRES |  | 3 | MASKELL PRODUCTIONS LTD |  |  |  | 528/97
| 1997-01-01 | Envirotank |  | FIBREGLASS UGST 3000MM DIA60000 TO 110000 LITRES |  | 3 | MASKELL PRODUCTIONS LTD |  |  |  | 528/97
| 1997-01-01 | Mainline Sheetmetals Ltd., Hamilton |  | AG TANKS 1) 2000 LITRE | OVERHEAD FARM TANK | 3 | MAINLINE SHEETMETALS LTD |  |  |  | 502/97
| 1997-01-01 | Campion & Irving Ltd |  | Supervault MH and MHR Series above Ground Tanks | Specification: SWR1 9503*93-01 UFC A-11-F-1(79-7) | 3A, 3B, 3C | Campion & Irving Ltd |  |  | Manufactured under licence to Trusco Tanks Inc Application renewed 21/12/01. New Approval No: 965/01 | 510/97
| 1997-02-11 | Oilcon Ltd |  | DG STORAGE 1000 & 2000 LITRE +10000 & 20000 LITRE | ON GROUND STORAGE TANK, ON GROUND BUNDED STORAGE TANKS | 3C, 3C | OILCON LTD |  |  | FAB0075 | 494/97
| 1997-05-22 | Mainline Sheetmetals Ltd., Hamilton |  | AG TANKS 2) 2000 LITRE | ONGROUND FARM TANK | 3 | MAINLINE SHEETMETALS LTD |  |  |  | 502/97
| 1997-05-22 | Mainline Sheetmetals Ltd., Hamilton |  | AG TANKS 3) 1000 LITRE | ONGROUND FARM TANK | 3 | MAINLINE SHEETMETALS LTD |  |  |  | 502/97
| 1997-05-22 | Mainline Sheetmetals Ltd., Hamilton |  | AG TANKS 4) 1350 LITRE | TRAILER TANK | 3C | MAINLINE SHEETMETALS LTD |  |  |  | 502/97
| 1997-06-25 | A F Martin Ltd |  | UNDERGROUND TANKS (CMPTMNT) 10/10/10 x 1000 LITRES, 20/10/10 & 20/20/10 | INC DUNLOP SECONDARY CONTAINMENT | 3 | A F MARTIN LTD |  |  |  | 506/97
| 1997-07-02 | Fuel & Lubrication Systems |  | UNDERGROUND TANKS (CMPTMNT) 5000, 10000 & 15000 LITRES | INTEGRATED STEEL BUND | 3C | FUEL & LUBRICATION SYSTEMS |  |  |  | 508/97
| 1997-08-15 | OILCON LTD |  | O/HEAD AG TANK 1000 & 1350 LITRE TRAILER TANK |  | 3C | OILCON LTD |  |  | FAB0075 | 512/97
| 1997-10-06 | Maskell Production Ltd. |  | 1200 mm diameter - Up to 5,000 L 2000 mm diameter - 10,000 L to 30,000 L 2500 mm diameter - 20,000 L to 60,000 L 3000 mm diameter - 60,000 L to 110,000 L | TO ASTM D4021 | 3 | Maskell Production Ltd. | Tanks to be labelled with ASTM D4021. Manufacture and testing in accordance with terms of Owens Corning/Fluid Containment license agreement. For tanks fitted with a fluid filled interstitial space between the tank shell, inspection and testing shall be in accordance with Maskell Productions instruction for double wall tanks with annular space filled and compartmented tanks and double walled bulkheads. All other tanks are to be installed and tested in accordance with the Code of Practice for the Design, Installation and Operation of Undergound Petroleum Storage Systems. Single bulkhead compartment tanks are only approved for storage of like products. Double bulkhead with integral interstitial space between bulkheads may be used for the storage of dissimilar products. The void between the double bulkheads is to be monitored for hydrocarbon leakage. |  |  | Unknown
| 1997-11-27 | Greentank Ltd |  | FIBREGLASS UGST DOUBLE WALL | TO ASTM D4021 | 3 | Greentank Ltd |  |  |  | 529/97
| 1997-12-10 | Fuelquip Services Ltd |  | BUND TANK 5000 LITRE |  | 3C | FUELQUIP SERVICES LTD |  |  |  | 526/97
| 1997-12-10 | Fuelquip Services Ltd |  | ABOVEGROUND STATIC BUND TANK 10000 LITRE |  | 3C | FUELQUIP SERVICES LTD |  |  |  | 527/97
| 1998-01-01 | OILCON LTD |  | SLEDGE TANK 5000 LITRE |  | 3C | OILCON LTD |  |  | FAB0075 | 548/98
| 1998-01-01 |  |  | FUEL TANKS 270, 360 & 450 LTR SIDE MOUNTED DIESEL |  | 3C |  |  |  |  | 591/98
| 1998-03-02 | TNT PALLECON SYSTEMS |  | IBC CONTAINER 500 LITRE | COLLAPSIBLE HAZTAINER | 3 | TNT PALLECON SYSTEMS |  |  |  | 546/98
| 1998-04-20 | OILCON LTD |  | OVERHEAD STORAGE TANK 2000 LITRE |  | 3C | OILCON LTD |  |  | FAB0075 | 549/98
| 1998-05-04 | A F Martin Ltd |  | FARM TANK 1000 & 2000 LITRE | FOR STORAGE OF CLASS 3C | 3C | A F MARTIN LTD |  |  |  | 570/98
| 1998-06-30 | FULTON HOGAN AUCKLAND |  | A/G STORAGE TANK 81000 LTR |  | 3C | FULTON HOGAN AUCKLAND |  |  |  | 590/98
| 1998-07-13 | Greentank Ltd |  | UG STORAGE TANKS MULTI COMPARTMENT FIBREGLASS | CONTAINMENT OF DIFFERENT FUEL PRODUCTS & GRADES | 3 | Greentank Ltd |  |  |  | 594/98 445/96
| 1998-07-13 | CFS Developments Africa |  | IBC CONTAINER COLLAPSIBLE COMPOSITE |  |  | CFS DEVELOPMENT/S AFRICA |  |  |  | 607/98
| 1998-09-11 | Greentank Ltd |  | UNDERGROUND STORAGE TANKS 600, 1200, 2000, 3000, 4000 & 5000 LITRE | 48" DIAMETER SGL & DBL WALL F/GLASS | 3 | Greentank Ltd |  |  |  | 663/98
| 1998-10-20 | Greentank Ltd |  | UNDERGROUND STORAGE TANKS2,500 LITRE | 48" DIAMETER SGL & DBL WALL F/GLASS | 3 | Greentank Ltd |  |  |  | 633/98
| 1998-10-29 | Maskell Production Ltd. |  | ENVIRO TANKS | STORAGE OF ETHANOL |  | MASKELL PRODUCTIONS |  |  |  | 671/98
| 1998-12-14 | Greentank Ltd |  | UNDERGROUND STORAGE TANKS10K/10K/10K, 15K/10K/15K, 10K.15K/10K | TRIPLE COMPARTMENT DBL WALL F/GLASS | 3 | Greentank Ltd |  |  |  | 690/98
| 1998-12-14 | Greentank Ltd |  | UNDERGROUND STORAGE TANKS15K/15K/15K, 10K/20K/10K, 15K/20K/15K | TRIPLE COMPARTMENT DBL WALL F/GLASS | 3 | Greentank Ltd |  |  |  | 690/98
| 1998-12-14 | Greentank Ltd |  | UNDERGROUND STORAGE TANKS 20K/20K/10K, 10K30K/10K | TRIPLE COMPARTMENT DBL WALL F/GLASS | 3 | Greentank Ltd |  |  |  | 690/98
| 1999-03-11 | OILCON LTD |  | 5000,10000, 20000, 30000, 40000, 50000 LITRE INTEGRATED BUNDED TANK | DOUBLE SKIN AG DIESEL | 3C | OILCON LTD |  |  | FAB0075 | 718/99
| 1999-04-12 | Challenge Eng Services |  | ABOVEGROUND TANKS5000, 10000 & 20000 LTR STG TANKS | AP1650 | 3A | AMERON NZ LTD |  |  |  | 723/99
| 1999-05-26 | Greentank Ltd |  | UNDERGROUND STORAGE TANKS MULTIPLE COMP S/WALL FIBREGLASS |  | 3 | Greentank Ltd |  |  |  | 730/99
| 1999-07-19 | Corrocoat Engineering SVS |  | AG TANK400 LITRE FARM STORAGE TANK |  | 3 | CORROCOAT ENGINEERING SVS |  |  |  | 736/99
| 1999-08-16 | Greentank Ltd |  | BULK CONTAINERS 10000, 40000 LTR DBL WALL TANKS | EXTENSION TO 445/96 | 3 | Greentank Ltd |  |  |  | 745/99
| 1999-09-03 | Fuelquip Services Ltd |  | UG TANK INBOARD MONITORING COLUMN |  | 3A/B | FUELQUIP SERVICES LTD |  |  |  | 753/99
| 1999-11-19 | John Russell Engineering |  | UG TANKS SINGLE WALL STEEL UG TANKS | 5000, 10000, 15000 LITRE VARIANTS | 3 | John Russell Engineering |  |  |  | 772/99
| 1999-11-19 | FORVAN SERVICES LTD |  | 24000 LTR AG STORAGE TANK | PLUS 1200 LITRE DAY TANK | 3C | FORVAN SERVICES LTD |  |  |  | 773/99
| 1999-12-22 | Wanaka Engineering 1995 Ltd |  | 200 LTR FUEL STORAGE TANK |  | 3C | WANAKA ENGINEERING 1995 LTD |  |  |  | 785/99
| 1999-12-22 | Petroleum Services (2001) Ltd |  | 4000, 10000, 20000 LTR AG TANKS |  | 3 | PETROLEUM EQUIPMENT SVCS |  |  |  | 786/99
| 2000-04-04 | Direct Mechanical Services Ltd |  | 24000 LITRE FUEL TANK |  | 3C | DIRECT MECHANICAL SERVICES LTD |  |  |  | 808/00
| 2000-05-10 | Greentank Ltd |  | 10FT DIA UG STORAGE TANK FOR CLASS 3 |  | 3 | Greentank Ltd |  |  |  | 821/00
| 2000-06-21 | Corrocoat Engineering SVS |  | 600 LITRE FUEL STORAGE FARM TANK |  | 3 | CORROCOAT ENGINEERING SVS |  |  |  | 827/00
| 2000-08-01 | Accardian Contractors Ltd |  | 5000, 10000, 15000 Litre Ag Tanks | WITH INTEGRAL STEEL BUND PLUS AGO FUEL DISPENSOR | 3C | ACCADIAN CONTRACTORS LTD |  |  |  | 833/00
| 2000-09-19 | Bailey Tanks Ltd |  | INTERMEDIATE BULK CONTAINER - DG1000 H ISO | SGS TEST REPORT 1AA4839/03 | 5 | BAILEY TANKS LTD |  |  |  | 841/00
| 2001-02-22 | A F Martin Ltd |  | DUOCON ABOVE GROUND FIRE RATED TANKS (2HRS) | WITH SECONDARY CONTAINMENT | 3A, 3B, 3C | AF MARTIN TA/MARTIN ENGINEERING |  | Design removed 22/01/2014. No longer produced. |  | 890/01
| 2001-02-27 | Mainline Sheetmetals Ltd., Hamilton |  | 2000L O/HD FARM TANK, 2000L & 1000l ON GROUND F/T | PLUS 1350 L DIESEL TRAILER TANK | 3C | MAINLINE SHEETMETALS LTD |  |  | APPROVAL NO.502/97 REF | 892/01
| 2001-08-27 | Mainline Sheetmetals Ltd., Hamilton |  | 545 LITRE A/G FARM DIESEL FUEL TANK | STEEL DRAFTING LTD.DWG NO. 62301 | 3C | MAINLINE SHEETMETALS LTD |  |  |  | 922/01
| 2001-10-09 | Harris Flame Technology |  | 500 LITRE DOMESTIC DIESEL STORAGE TANK | APPROVAL 912/01 | 3C | HARRIS FLAME TECHNOLOGY |  |  |  | 939/01
| 2001-10-10 | Hamilton Oil Services Ltd |  | 5000L, 5000L, 7500L, 10000L & 20000L RELOCATABLE AG TANKS |  | 3 | HAMILTON OIL SERVICES LTD |  |  |  | 935/01
| 2001-12-07 | STM Group |  | 400 L ABOVEGROUND FARM TANK STANDARD & ENVIRO |  | 3A | STM GROUP |  |  | Renewal of Approval | 951/01
| 2001-12-07 | STM Group |  | 500 L ABOVEGROUND FARM TANK STANDARD & ENVIRO |  | 3A | STM GROUP |  |  | Renewal of Approval | 952/01
| 2001-12-07 | STM Group |  | 1000 L ABOVEGROUND FARM TANK STANDARD & ENVIRO |  | 3A | STM GROUP |  |  | Renewal of Approval | 953/01
| 2001-12-07 | STM Group |  | 2000 L ABOVEGROUND FARM TANK STANDARD & ENVIRO |  | 3A | STM GROUP |  |  | Renewal of Approval | 954/01
| 2001-12-07 | STM Group |  | 5000L - 6000 L ABOVEGROUND FARM TANK IBT | FUELCELL SERIES | 3A | STM GROUP |  |  | Renewal of Approval | 955/01
| 2001-12-07 | STM Group |  | DUAL AXLE TRAILER TANK | GROSS LADEN WEIGHT UNDER 2000KG | 3A | STM GROUP |  |  | Renewal of Approval | 956/01
| 2001-12-07 | STM Group |  | SINGLE AXLE TRAILER TANK | GROSS LADEN WEIGHT UNDER 2000KG | 3B | STM GROUP |  |  | Renewal of Approval | 957/01
| 2001-12-21 | Campion & Irving Ltd |  | Supervault MH and MHR Series above Ground Tanks | Specification: SWR1 9503*93-01 UFC A-11-F-1(79-7) | 3A, B, C | Campion & Irving Ltd |  |  | Renewal of Approval No 510/97 Approval renewed 21/12/06. New Approval No: TNK0610 | 965/01
| 2002-03-27 | Campion & Irving Ltd |  | HAZTANK SINGLE HAZARD CYLINDRICAL A/G FIRE RATED TANKS (2 HRS) | 750 - 110,000 litre | 3C | Campion & Irving Ltd |  |  | Approval amended 27/03/02 New Approval No: 1001/02 | 989/02
| 2002-03-27 | Campion & Irving Ltd |  | Haztank Single Hazard Cylindirical AF Fire Rated Tanks (2 hrs) | 500 - 110,000 litre |  | Campion & Irving Ltd |  |  | Amendment of Approval 1001/02 (to include 500 L) Approval amended 15/05/02 New Approval No: 1002/02 | 1001/02
| 2002-05-15 | Campion & Irving Ltd |  | Haztank Single Hazard Cylindirical AF Fire Rated Tanks (2 hrs) |  | 3C | Campion & Irving Ltd |  |  | Amendment of Approval 1001/02 (design variation) Approval amended 07/04/03 New Approval No: 1084/03 | 1002/02
| 2002-05-22 | EXOIL LTD |  | 500, 1000 & 1800 LTR AG TANKS FOR DG |  | 3C | EXOIL LTD |  |  | FARM USE ONLY | 1000/02
LAB3287 | 2002-06-28 | Sceptor Corporation |  | HDPE Marine Fuel Tanks - 12 Litre Model E3 and 22.7 Litre Model E6 | Tenov Wholesale Marine Ltd | 3 | Canada |  |  |  | 1006/02
LAB3288 | 2002-07-10 | Sceptor Corporation |  | 22.7 Litre Marine Fuel Tank | Model E6 |  | Marine Xpress Ltd |  |  |  | 1016.07.02
| 2002-08-23 | A F Martin Limited under licence to Duocon Tanks |  | Duocon Above Ground Fire Rated Tank (2 Hrs) | Sizes (US Gallons) 280, 500, 1000, 1500, 2000, 3000, 4000, 5000, 6000, 8000, 10000, 12000, 15000 & 20000 with secondary containment | 3A, 3B, 3C | A F Martin Limited under licence to Duocon Tanks |  | Design removed 22/01/2014. No longer produced. |  | 1030/02
| 2002-12-04 | A F Martin Ltd-Martin Aviation |  | Double Skinned storage tanks Refuellers for Cl.3 |  | 3 | A F Martin Ltd-Martin Aviation |  |  | Ext of Approval Not.No. 1028/02 | 1068/02
| 2003-02-11 |  |  |  | 15,000 lt Double Skin Steel U/G Tank | [5 empty] | 1102/03
| 2003-04-07 | Campion & Irving Ltd |  | Pyrotector Single Hazard Cylindrical AG Fire rated Tanks | 750 to 110,000 L with secondary containment | 3a,b,c | Campion & Irving Ltd |  |  | Amendment of Approval 1001/02 (name change from HazTank to Pyrotector) Approval renewed 21/12/06 New Approval No: TNK0611 | 1084/03
| 2003-05-13 | Greentank Ltd under licence to Xerxes Corporation |  | UG/Tank | 6' Dia Fibreglass Underground Fuel Tanks | 3 | Greentank Ltd under licence to Xerxes Corporation |  |  |  | 1097/03
| 2003-06-24 | Petroleum Services (2001) Ltd |  | A/G Tanks | 5000,1000,7,500 lt Double Skinned Tanks | 3C | Petroleum Services (2001) Ltd |  |  |  | 1101/03
| 2003-09-01 | Greentank Ltd under licence to Xerxes Corporation |  | Fibreglass UG Fuel Tank | Xerxes 8' Dia F/glass UG Fuel Tanks | 3 | Greentank Ltd under licence to Xerxes Corporation |  |  |  | 1109/03
| 2003-09-04 | Dawn Group Ltd |  | Diesel Storage Tanks | 500-7500 Lt A/G Diesel Storage Tanks | 3 | Dawn Group Ltd |  |  |  | 1111/03
| 2003-09-04 | Tropicair Heating Ltd |  | Diesel Storage Tanks | 480 Litre A/G Tank | 3 | Tropicair Heating Ltd |  |  |  | 1124/03
| 2003-09-22 | Fuel Containment Ltd (transferred to Petroleum Services Ltd on 4/11/2004) |  | Single & Double Skinned A/G Tanks | Above ground Tanks | 3A and 3C | Fuel Containment Ltd (transferred to Petroleum Services Ltd on 4/11/2004) |  |  | Extension to approval to include Class 3A by OSH 26/11/03 | 1117/03
| 2003-10-07 | Mainline Sheetmetals Ltd., Hamilton |  | A/G Tanks | A/G 10.5 cubic metre Home Heating Fuel Tank | 3 | Mainline Sheetmetals Ltd |  |  |  | 1116/03
| 2003-10-09 | Greentank Ltd |  | Underground Tank | 5898 Litre/9438 Litre Double Skin Dual Compartment Underground Fuel Tank | 3 | Greentank Ltd |  |  |  | 1123/03
| 2003-11-26 | Fuel Containment Ltd (transferred to Petroleum Services Ltd on 4/11/2004) |  | Above ground Tanks | Renewal of Approval | 3A and 3C | Fuel Containment Ltd (transferred to Petroleum Services Ltd on 4/11/2004) |  |  | Extension to approval to include Class 3A and 3C by OSH 26/11/03 | 1128/03
| 2003-12-23 | Consani Engineering (Pty) South Africa |  | ISO tank to be used as static storage vessels for LPG by Novagas Ltd | 24,600 Litre LPG Eurotainer | 3 | LPG & Safety Consultants |  |  |  | 1134/03
| 2004-01-01 | [9 empty] | 1183/04
| 2004-02-02 | Taylors Manufacturing Ltd |  | Double Skin Tank | 40,000 Litre | 3C | Taylors Manufacturing Ltd |  |  |  | 1143/04
| 2004-03-09 | STM Group |  | Skin Underground and Onground Tanks | 5000 to 60,000 Litre single Renewal of Approval | 3 | STM Group |  |  |  | 1157/04
| 2004-03-24 | Service Engineers Ltd |  | AG Tank | 10,000 Lt Single Skin Steel | 3C | Watts & Hughes Construction Co. Ltd |  |  |  | 1159/04
| 2004-03-31 | Hamilton Oil Services Ltd |  | AG Tank | Bunded Diesel Storage Tank | 3C | Hamilton Oil Services Ltd |  |  |  | 1187/04
| 2004-04-16 | Petroleum Services (2001) Ltd |  | Secondary Containment Storage Tank | A/G 20m3 | 3C | Petroleum Services (2001) Ltd |  |  |  | 1167/04
| 2004-04-20 | Service Engineers Ltd |  | Double Skin Steel Above-ground Diesel Fuel Tank | 4,500 Litre | 3C | Service Engineers |  |  |  | 1166/04
| 2004-04-30 | Fuel Containment Ltd(transferred to Petroleum Services Ltd on 4/11/2004) |  | AG Tank | 50,000 Lt Single Skin Single Compartmen & 50,000 Lt Double Skin Single Compartmentt On-ground Fuel Tanks | 3A/3C | Fuel Containment Ltd (transferred to Petroleum Services Ltd on 4/11/2004) |  |  | Fuel Containment Ltd purchased by Petroleum Services Ltd on 4 November 2004 | 1170/04
| 2004-06-09 | Greentank Ltd |  | U/G Fuel Tanks | Xerxes 8" Diameter Fibreglass U/G Fuel Tanks | 3A | Greentank Ltd |  |  |  | 1174/04
FAB0001 | 2004-06-22 |  | Greentank Limited 16 Donald Street Dunedin | [5 empty] | 2007-06-22 | Fabricator of: TNK0001, TNK1015, TNK1016
TNK 0001 | 2004-07-22 | Greentank Ltd |  | UST | 4 foot diameter glas fibre reinforced plastic double wall GRP UGST 7,500litre |  | Greentank Ltd |  |  | Fabricated by Greentank (FAB001/FAB0019) - expired
| 2004-07-26 | A F Martin Ltd |  | AG Tank | 24,000 lt Multi-Modal Tank | 3B/C | A F Martin Engineering (PN) Ltd |  |  |  | 1189/04
FAB0002 | 2004-08-26 |  | CGC Engineering ltd | Steel AG and UST | Steel above ground and below ground double wall tanks to a maximum capacity of 60,000litres AS1692 category 4 | 3 | CGC Engineering ltd |  | 2007-08-26 | CGC Engineering Ltd (TNK0503) also fabricated TNK 0002 and TNK 818 for petroleum solutions limited
TNK 0002 | 2004-11-26 | CGC Engineering ltd |  | AG Tank | 2x 200 cubic metre. Double wall steel aboveground diesel LOA 4756mmstorage tank.Shell 6mm Pl., I.D. 2375mm.Material AS3678 Gr.250 or Gr300.Welding NZS 1554.1:2000, wind speed 50m/s, Seismic coeff. 0.68. | 3.1D | CGC Engineering ltd |  |  | Fabrication of TNK 0002. Fabricated by CGC Engineering Ltd (FAB 0002) - expired
TNK0501 | 5/2/2005 & 29/8/2008 |  | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 From 19/12/2019 to 19/12/2022 Carlyon Civil Construction Ltd 3 Ellis Street Frankton, Hamilton FAB0083 | U/G Fuel Tanks | 8000, 17000, 25000, 50000 litre double wall low carbon steel/HDPE wrap underground fuel tanks. The shell is 6mm steel inner with 6mm HDPE outer. Internal diameter 2.4m. Welding to NZS 4711. | Petroleum (Unleaded) class 3.1A UN No 1203 Automotive Diesel fuel Class 3.1D UN No 1202 | Petroleum Services Limited |  | 2011-04-01 | FAB0083 (FAB0016 prior to 9/06/2019)
TNK0502 | 2005-06-26 | Duocon |  | Steel AG Tank 2 hour fire rating. | Duocon above ground fire rated tank (2 hours). Sizes (US Gallons) 280, 500, 1000, 1500, 2000, 3000, 4000, 5000, 6000, 8000, 10,000, 12,000, 15,000 and 20,000. | 3.1A, 3.1C, 3.1D | Martin Engineering (PN) Ltd |  | Design removed 22/01/2014. No longer produced. | FAB0045
TNK0504 | 2012-04-04 | Martin Engineering (Palmerston North) Ltd. 891 Tremaine Avenue PO Box 5295 Palmerston North | Martin Engineering (Palmerston North) Ltd. FAB0045 | Design Specification: AS1692 – 2006 Category 4 HSNOCOP 24 Version 2 July 2014 Reduced Secondary Containment for Certain Above Ground Stationary Tanks Safe Work Instrument 2017 | Prior to 4 June 2019: Double wall steel above ground tank. Sizes (in litres) 5,000, 10,000, 15,000, 20,000, 30,000, 40,000, 50,000, 60,000. As of 4 June 2019: Double skin –multi-hazard – 2 hour impact protected standard cylindrical, horizontal, above ground tank from 20,000 L to 60,000 L in capacity | Between 4 April 2012 and 3 September 2015 Flammable liquids having a hazard classifications of 3.1A, 3.1C or 3.1D From 3 September 2015: Classes 3.1A, 3.1B, 3.1C and 3.1D flammable liquids in accordance with Table 3.1 of HSNOCOP 24 Version 2 July 2014. As of 4 June 2019 Flammable liquids having a hazard classifications of 3.1A, 3.1B, 3.1C or 3.1D | Martin Engineering (Palmerston North) Ltd. 891 Tremaine Avenue PO Box 5295 Palmerston North | Subject to the conditions specified on Test Certificate 2015112 (issued 3/09/2015) and compliance certificate CC01978 (issued 4/06/2019). - The vent is to terminate not less than 150 mm above the tank top and is to be higher than the fill point of the tank. - Filling and discharge of the tanks is to be carried out under liquid and vapour tight connections. - All normal and emergency venting requirements of Section 7 of UL2085 are to be complied with. - Note provision for emergency venting of the interstitial space of the secondary containment structure is to be provided. The approval becomes invalid following any change to the design parameters and/or referenced Martin Engineering Drawings. | 2029-06-04 | FAB0045
TNK0506 | 2005-08-23 |  | Martin Engineering (Palmerston North) Ltd. | Steel AG Tank to AS1692:1989 Category 4 FAB0045 | 12000 L double wall steel aboveground tank for class 3.1C and 3.1D. | 3.1C, 3.1D | Martin Engineering (Palmerston North) Ltd. |  | 2008-08-23 | FAB0045 |  | .
TNK0601 | 2006-05-10 | APD Limited | APD Ltd PO Box 12663 Penrose, Auckland 1642 49 McLaughlins Road, Wiri, Auckland, 2104 FAB0032 | HDPE tank to HSNOCOP-4-1, BS EN 1778:2000 | 5,000 litre Vertical Cylindrical Above Ground Tank single skin | 6, 8 and 9 substances that do not have a flammable classifcation | APD Limited |  | 2011-05-10 | FAB0032
TNK0602 | 2006-05-10 | APD Limited | APD Ltd PO Box 12663 Penrose, Auckland 1642 49 McLaughlins Road, Wiri, Auckland, 2104 FAB0032 | HDPE tank to HSNOCOP-4-1, BS EN 1778:2000 | 1,000, 2,000, 10,000, 15,000 litre Vertical Cylindrical Above Ground Tank single skin | 6, 8 and 9 substances that do not have a flammable classifcation | APD Limited |  | 2011-05-10 | FAB0032
TNK0603 | 2006-05-31 |  | John Russell Engineering 9 Kilronan Place Wigram Christchurch | Steel AG Tank to AS 1692:1989 | 1000 L, 1200 L, 1500 L, 1800 L, 2000 L, 3000 L, 5000 L, 10,000 L, 15,000 L, & 20,000 L, on ground single skin steel tanks. | 3.1A Petrol and 3.1D Diesel. | Nymic Engineering Ltd |  | 2008-12-22 | Fabricated by John Russell Engineering (FAB0003)
TNK0604 | 2006-05-31 |  | John Russell Engineering 9 Kilronan Place Wigram Christchurch | Steel AG Tank to AS 1692:1989 | 1000 L, 1200 L, 1500 L, 1800 L, single skin steel tanks on a stand. | 3.1A Petrol and 3.1D Diesel. | Nymic Engineering Ltd |  | 2008-12-22 | Fabricated by John Russell Engineering (FAB0003)
TNK0607 | 2006-06-23 | APD Limited | APD Ltd PO Box 12663 Penrose, Auckland 1642 49 McLaughlins Road, Wiri, Auckland, 2104 FAB0032 | HDPE tank to HSNOCOP-4-1, BS EN 1778:2000 | 3,000 litre Vertical Cylindrical Above Ground Tanks | 6, 8, 9 | APD Limited |  | 2011-06-22 | FAB0032
TNK0605 | 2006-06-27 | HSM Engineering | HSM Engineering (FAB005) | Steel Tanks to AS 1682-1989 (category 5) | 10,000 L stainless steel, vertical cylinder above-ground for hazardous substance of classes 3.1B and 3.1C | 3.1B, 3.1C | HSM Engineering Ltd |  | 2011-06-27 | FAB0005 - expired
TNK0606 | 2006-06-27 | HSM Engineering | HSM Engineering (FAB005) | Steel Tanks to AS 1682-1989 (category 5) | 20,000 L stainless steel, vertical cylinder above-ground for hazardous substance of classes 3.1B and 3.1C | 3.1B, 3.1C | HSM Engineering Ltd |  | 2011-06-27 | FAB0005 - expired
FAB0003 | 2006-08-18 |  | John Russell Engineering Ltd | See Comments |  |  |  |  | 2016-07-23 | Fabricator of: TNK0603, TNK0604, TNK0800, TNK0801, TNK0802, TNK0803, TNK0804, TNK0805
FAB0005 | 2006-08-23 |  | HSM Engineering | [5 empty] | 2009-08-23 | Fabricator of: TNK0605, TNK0606
FAB0004 | 2006-08-30 |  | Armatec Environment Ltd | [5 empty] | 2009-08-30 | Fabricator of: TNK0734, TNK0735, TNK0806, TNK0853, TNK0855 TNK0880, TNK0881, TNK13028, TNK13029, TNK13030, TNK13031, TNK13032, TNK13033
FAB0006 | 2006-11-17 |  | Qingdao Jinhuanghai Container Co. Ltd, Dajinjia Qingdao China under licence from Transtank Australia | [5 empty] | 2009-11-17 | Fabricator of: TNK0715, TNK0716, TNK0717, TNK0718, TNK0719, TNK0720, TNK0721, TNK0722, TNK0723, TNK0724, TNK0725, TNK0726
TNK0610 | 2006-12-21 | Campion & Irving Ltd |  | Supervault Series | Specification: UL2085 and AS1692 | 3.1A, 3.1B, 3.1C | Campion & Irving Ltd |  | 2011-12-21 | Renewal of Approval No 965/01 FAB0008 - expired
TNK0611 | 2006-12-21 | Campion & Irving Ltd |  | Pyrotector Series | Specification: UL2080 and AS1692 | 3.1A, 3.1B, 3.1C | Campion & Irving Ltd |  | 2011-12-21 | Renewal of Approval No 1084/03 FAB0008 - expired
FAB0008 | 2007-01-12 |  | Campion & Irving Ltd 5 Tanya St Christchurch | [5 empty] | 2008-12-01 | Fabricator of: TNK0610, TNK0611
TNK0701 | 21/11/2014 15/11/2021 - Renewed | Mainline Sheetmetals Ltd. | Mainline Sheetmetals Ltd, 209 Ellis St, Frankton Hamilton 3240 PO Box 15161, Hamilton FAB0018 | Prior to 15/11/2021 Steel tanks to AS 1692: 1989 Category 2 As of 15/11/2021 AS1692: 2006, Category 2 | 590 L - Above ground single skin horizontal cylindrical overhead stationary tank Gross capacity: 589 litres for overhead tank & 570 litres for overhead split tank Maximum safe Fill Level: 560 litres for overhead tank & 541 litres for overhead split tank | Prior to 15/11/2021 3.1A, 3.1C, 3.1D As of 15/11/2021 Aviation gasoline Avgas 100 and Avgas 100LL UN No. 1203 - Class 3.1A, 6.7B Diesel - Class 3.1D, 6.7B Marine diesel fuel UN No. 1202 - Class 3.1C, 3.1D, 6.7B Petroleum (unleaded) UN No. 1203 - Class 3.1A, 6.7B | Mainline Sheetmetals Ltd. | All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to be provided in accordance with AS 1692:2006 for category 2 tanks. Optional return pipe - Drawing No.: CB-SW-1107, Sheets: 1, Date: 5/11/21, Description: Optional return pipe, Drawn by: C Besley. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture / pressure test, AS 1692:2006 Category 2, test pressure in kPa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all fill / dip tubes in accordance with the requirements of AS 1692:2006. Design Statement – Job No. 19-305 – In respect of: 590L overhead fuel tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 7/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692) Design Statement – Job No. 19-305 – In respect of: 590L split overhead fuel tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 7/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692) Anchor and foundation requirements for 590L overhead fuel tank & 590L split overhead fuel tank, with following parameters: Tank category 2, in accordance with AS 1692 Design wind speed = 56m/s (any NZ location) Design earthquake lateral force coefficient Cd(T) = 0.8g Hazard factor Z ≤ 0.45, importance level 2 and 25 years design life Minimum anchoring requirements: 1-M10 trubolt at each leg (T10085X) and 5mm thick footplate Minimum foundation requirements: 200mm thick x 450mm square concrete pad under each leg, with D10-200 EW T&B Approved to supply a burner or engine. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standard/s. | N/A | FAB0018
TNK0702 | 21/11/2014 27/07/2021 - Renewed | Mainline Sheetmetals Ltd. | Mainline Sheetmetals Ltd, 209 Ellis St, Frankton Hamilton 3240 PO Box 15161, Hamilton FAB0018 | Prior to 27/07/2021 Steel tanks to AS 1692: 1989 Category 1 As of 27/07/2021 AS1692: 2006, Category 1 | 490 L - Single skin horizontal above ground home heating stationary tank Safe Fill Level: 465 litres | Diesel domestic heating oil and Alpine diesel fuel UN No. 1202 Class 3.1C, 3.1D | Mainline Sheetmetals Ltd. | Hazardous Substances (Hazardous Property Controls) Notice 2017 - Clause 29 - Stationary container systems for domestic oil burning installations that do not exceed 2 500 L in capacity. 490 litre home heating tank: 1.6 mm electro galvanised plate shell with 2.0 mm electro galvanised ends, Material: JIS G 3316, LOA 1500 mm, Welding NZS 1554. No side of the tank shall bulge by an amount greater than 2% of the lesser dimension of that side when filled with product in service. All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to be provided in accordance with AS 1692:2006 for category 1 tanks. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 1, test pressure in Kpa and safe ﬁll height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all the fill / dip tubes in accordance with the requirements of AS 1692. Design Statement – Job No. 19-305 – In respect of: 490L home heating tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 25/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692): Anchor and foundation requirements for 490L home heating tank, with following parameters: Tank category 1, in accordance with AS 1692 Design wind speed = 56m/s (any NZ location) Design earthquake lateral force coefficient Cd(T) = 0.8g Hazard factor Z ≤ 0.45, importance level 2 and 25 years design life Minimum anchoring requirements: 1-M10 trubolt at each leg (T10085X) and 5mm thick footplate Minimum foundation requirements: 1.4m x 0.8m x 0.15m thick concrete slab, with SE72 mesh Approved for domestic oil burning installations (burner or engine). Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. | N/A | FAB0018
TNK0703 | 21/11/2014 15/11/2021 - Renewed | Mainline Sheetmetals Ltd. | Mainline Sheetmetals Ltd, 209 Ellis St, Frankton Hamilton 3240 PO Box 15161, Hamilton FAB0018 | Prior to 15/11/2021 Steel tanks to AS 1692: 1989 Category 2 As of 15/11/2021 AS 1692:2006, Category 2 | 950 L - Above ground single skin horizontal cylindrical overhead stationary tank Gross capacity: 990 litres for overhead tank & 959 litres for overhead split tank Maximum safe Fill Level: 940 litres for overhead tank & 911 litres for overhead split tank | Prior to 15/11/2021 3.1A, 3.1C, 3.1D As of 15/11/2021 Aviation gasoline Avgas 100 and Avgas 100LL UN No. 1203 - Class 3.1A, 6.7B Diesel - Class 3.1D, 6.7B Marine diesel fuel UN No. 1202 - Class 3.1C, 3.1D, 6.7B Petroleum (unleaded) UN No. 1203 - Class 3.1A, 6.7B | Mainline Sheetmetals Ltd. | All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to be provided in accordance with AS 1692:2006 for category 2 tanks. Optional return pipe - Drawing No.: CB-SW-1107, Sheets: 1, Date: 5/11/21, Description: Optional return pipe, Drawn by: C Besley. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture / pressure test, AS 1692:2006 Category 2, test pressure in kPa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all fill / dip tubes in accordance with the requirements of AS 1692:2006. Design Statement – Job No. 19-305 – In respect of: 950L overhead fuel tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 7/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692) Design Statement – Job No. 19-305 – In respect of: 950L split overhead fuel tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 7/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692) Anchor and foundation requirements for 950L overhead fuel tank & 950L split overhead fuel tank, with following parameters: Tank category 2, in accordance with AS 1692 Design wind speed = 56m/s (any NZ location) Design earthquake lateral force coefficient Cd(T) = 0.8g Hazard factor Z ≤ 0.45, importance level 2 and 25 years design life Minimum anchoring requirements: 1-M10 trubolt at each leg (T10085X) and 5mm thick footplate Minimum foundation requirements: 300mm thick x 500mm square concrete pad under each leg, with D10-200 EW T&B Approved to supply a burner or engine. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standard/s. | N/A | FAB0018
TNK0704 | 21/11/2014 15/11/2021 - Renewed | Mainline Sheetmetals Ltd. | Mainline Sheetmetals Ltd, 209 Ellis St, Frankton Hamilton 3240 PO Box 15161, Hamilton FAB0018 | Prior to 15/11/2021 Steel tanks to AS 1692: 1989 Category 2 As of 15/11/2021 AS 1692:2006, Category 2 | 1400 L - Above ground single skin horizontal cylindrical overhead stationary tank Gross capacity: 1408 litres for overhead tank & 1364 litres for overhead split tank Maximum safe Fill Level: 1338 litres for overhead tank & 1296 litres for overhead split tank | Prior to 15/11/2021 3.1A, 3.1C, 3.1D As of 15/11/2021 Aviation gasoline Avgas 100 and Avgas 100LL UN No. 1203 - Class 3.1A, 6.7B Diesel - Class 3.1D, 6.7B Marine diesel fuel UN No. 1202 - Class 3.1C, 3.1D, 6.7B Petroleum (unleaded) UN No. 1203 - Class 3.1A, 6.7B | Mainline Sheetmetals Ltd. | All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to be provided in accordance with AS 1692:2006 for category 2 tanks. Optional return pipe - Drawing No.: CB-SW-1107, Sheets: 1, Date: 5/11/21, Description: Optional return pipe, Drawn by: C Besley. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture / pressure test, AS 1692:2006 Category 2, test pressure in kPa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all fill / dip tubes in accordance with the requirements of AS 1692:2006. Design Statement – Job No. 19-305 – In respect of: 1400L overhead fuel tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 7/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692) Design Statement – Job No. 19-305 – In respect of: 1400L split overhead fuel tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 7/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692) Anchor and foundation requirements for 1400L overhead fuel tank & 1400L split overhead fuel tank, with following parameters: Tank category 2, in accordance with AS 1692 Design wind speed = 56m/s (any NZ location) Design earthquake lateral force coefficient Cd(T) = 0.8g Hazard factor Z ≤ 0.45, importance level 2 and 25 years design life Minimum anchoring requirements: 1-M10 trubolt at each leg (T10085X) and 5mm thick footplate Minimum foundation requirements: 300mm thick x 600mm square concrete pad under each leg, with D10-200 EW T&B Approved to supply a burner or engine. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standard/s. | N/A | FAB0018
TNK0705 | 21/11/2014 15/11/2021 - Renewed | Mainline Sheetmetals Ltd. | Mainline Sheetmetals Ltd, 209 Ellis St, Frankton Hamilton 3240 PO Box 15161, Hamilton FAB0018 | Prior to 15/11/2021 Steel tanks to AS 1692: 1989 Category 2 As of 15/11/2021 AS 1692:2006, Category 2 | 1950 L - Above ground single skin horizontal cylindrical overhead stationary tank Gross capacity: 1976 litres for overhead tank & 1915 litres for overhead split tank Maximum safe Fill Level: 1877 litres for overhead tank & 1819 litres for overhead split tank | Prior to 15/11/2021 3.1A, 3.1C, 3.1D As of 15/11/2021 Aviation gasoline Avgas 100 and Avgas 100LL UN No. 1203 - Class 3.1A, 6.7B Diesel - Class 3.1D, 6.7B Marine diesel fuel UN No. 1202 - Class 3.1C, 3.1D, 6.7B Petroleum (unleaded) UN No. 1203 - Class 3.1A, 6.7B | Mainline Sheetmetals Ltd. | All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to be provided in accordance with AS 1692:2006 for category 2 tanks. Optional return pipe - Drawing No.: CB-SW-1107, Sheets: 1, Date: 5/11/21, Description: Optional return pipe, Drawn by: C Besley. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture / pressure test, AS 1692:2006 Category 2, test pressure in kPa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all fill / dip tubes in accordance with the requirements of AS 1692:2006. Design Statement – Job No. 19-305 – In respect of: 1950L overhead fuel tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 7/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692) Design Statement – Job No. 19-305 – In respect of: 1950L split overhead fuel tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 7/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692) Anchor and foundation requirements for 1950L overhead fuel tank & 1950L split overhead fuel tank, with following parameters: Tank category 2, in accordance with AS 1692 Design wind speed = 56m/s (any NZ location) Design earthquake lateral force coefficient Cd(T) = 0.8g Hazard factor Z ≤ 0.45, importance level 2 and 25 years design life Minimum anchoring requirements: 1-M10 trubolt at each leg (T10085X) and 5mm thick footplate Minimum foundation requirements: 300mm thick x 650mm square concrete pad under each leg, with D10-200 EW T&B Approved to supply a burner or engine. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standard/s. | N/A | FAB0018
TNK0706 | 21/11/2014 15/11/2021 - Renewed 17/04/2025 - Renewed | Mainline Sheetmetals Ltd. | Mainline Sheetmetals Ltd, 209 Ellis St, Frankton Hamilton 3240 PO Box 15161, Hamilton FAB0018 | Prior to 15/11/2021 Steel tanks to AS 1692: 1989 Category 2 As of 15/11/2021 AS 1692:2006, Category 2 | 590 L - Above ground single skin horizontal cylindrical ground stationary tank Safe Fill Level: 560 litres | Prior to 15/11/2021 3.1A, 3.1C, 3.1D As of 15/11/2021 Aviation gasoline Avgas 100 and Avgas 100LL UN No. 1203 - Class 3.1A, 6.7B Diesel - Class 3.1D, 6.7B Marine diesel fuel UN No. 1202 - Class 3.1C, 3.1D, 6.7B Petroleum (unleaded) UN No. 1203 - Class 3.1A, 6.7B | Mainline Sheetmetals Ltd. | All tanks are to be manufactured strictly in accordance with AS 1692:2006, Category 2 as applicable. Secondary containment subject to installed stationary container system compliance certificates. All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to beprovided in accordance with AS 1692:2006 for category 2 tanks. It is Mainline Sheetmetals Ltd's responsibility to ensure the correct size vents are fitted. Optional return pipe - Drawing No.: CB-SW-1107, Sheets: 1, Date: 5/11/21, Description: Optional return pipe, Drawn by: C Besley. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture / pressure test, AS 1692:2006 Category 2, test pressure in kPa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all fill / dip tubes in accordance with the requirements of AS 1692:2006. Design Statement – Job No. 19-305 – In respect of: 590L ground tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 25/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692). Design Statement, issued by: Stiles and Hooker Ltd, to: Mainline Sheetmetals Ltd, in respect of: 590L Split Ground Tank. Tank design to AS1692, seismic and wind loading to AS/NZS1170, structure to AS/NZS3404. Signed by Roger Baker (CMEngNZ), dated 14/06/2022. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standard/s. | N/A | FAB0018
TNK0707 | 21/11/2014 15/11/2021 - Renewed 17/04/2025 - Renewed | Mainline Sheetmetals Ltd. | Mainline Sheetmetals Ltd, 209 Ellis St, Frankton Hamilton 3240 PO Box 15161, Hamilton FAB0018 | Prior to 15/11/2021 Steel tanks to AS 1692: 1989 Category 2 As of 15/11/2021 AS 1692:2006, Category 2 | 950 L - Above ground single skin horizontal cylindrical ground stationary tank Safe Fill Level: 940 litres | Prior to 15/11/2021 3.1A, 3.1C, 3.1D As of 15/11/2021 Aviation gasoline Avgas 100 and Avgas 100LL UN No. 1203 - Class 3.1A, 6.7B Diesel - Class 3.1D, 6.7B Marine diesel fuel UN No. 1202 - Class 3.1C, 3.1D, 6.7B Petroleum (unleaded) UN No. 1203 - Class 3.1A, 6.7B | Mainline Sheetmetals Ltd. | All tanks are to be manufactured strictly in accordance with AS 1692:2006, Category 2 as applicable. Secondary containment subject to installed stationary container system compliance certificates. All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to be provided in accordance with AS 1692:2006 for category 2 tanks. It is Mainline Sheetmetals Ltd's responsibility to ensure the correct size vents are fitted. Optional return pipe - Drawing No.: CB-SW-1107, Sheets: 1, Date: 5/11/21, Description: Optional return pipe, Drawn by: C Besley. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture / pressure test, AS 1692:2006 Category 2, test pressure in kPa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all fill / dip tubes in accordance with the requirements of AS 1692:2006. Design Statement – Job No. 19-305 – In respect of: 950L ground tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 25/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692). Design Statement, issued by: Stiles and Hooker Ltd, to: Mainline Sheetmetals Ltd, in respect of: 950L Split Ground Tank. Tank design to AS1692, seismic and wind loading to AS/NZS1170, structure to AS/NZS3404. Signed by Roger Baker (CMEngNZ), dated 14/06/2022. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standard/s. | N/A | FAB0018
TNK0708 | 21/11/2014 15/11/2021 - Renewed 17/04/2025 - Renewed | Mainline Sheetmetals Ltd. | Mainline Sheetmetals Ltd, 209 Ellis St, Frankton Hamilton 3240 PO Box 15161, Hamilton FAB0018 | Prior to 15/11/2021 Steel tanks to AS 1692: 1989 Category 2 As of 15/11/2021 AS 1692:2006, Category 2 | 1400 L - Above ground single skin horizontal cylindrical ground stationary tank Safe Fill Level: 1338 litres | Prior to 15/11/2021 3.1A, 3.1C, 3.1D As of 15/11/2021 Aviation gasoline Avgas 100 and Avgas 100LL UN No. 1203 - Class 3.1A, 6.7B Diesel - Class 3.1D, 6.7B Marine diesel fuel UN No. 1202 - Class 3.1C, 3.1D, 6.7B Petroleum (unleaded) UN No. 1203 - Class 3.1A, 6.7B | Mainline Sheetmetals Ltd. | All tanks are to be manufactured strictly in accordance with AS 1692:2006, Category 2 as applicable. Secondary containment subject to installed stationary container system compliance certificates. All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to be provided in accordance with AS 1692:2006 for category 2 tanks. It is Mainline Sheetmetals Ltd's responsibility to ensure the correct size vents are fitted. Optional return pipe - Drawing No.: CB-SW-1107, Sheets: 1, Date: 5/11/21, Description: Optional return pipe, Drawn by: C Besley. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture / pressure test, AS 1692:2006 Category 2, test pressure in kPa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all fill / dip tubes in accordance with the requirements of AS 1692:2006. Design Statement – Job No. 19-305 – In respect of: 1400L ground tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 7/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692). Design Statement, issued by: Stiles and Hooker Ltd, to: Mainline Sheetmetals Ltd, in respect of: 1400L Split Ground Tank. Tank design to AS1692, seismic and wind loading to AS/NZS1170, structure to AS/NZS3404. Signed by Roger Baker (CMEngNZ), dated 14/06/2022. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standard/s. | N/A | FAB0018
TNK0709 | 21/11/2014 15/11/2021 - Renewed 17/04/2025 - Renewed | Mainline Sheetmetals Ltd. | Mainline Sheetmetals Ltd, 209 Ellis St, Frankton Hamilton 3240 PO Box 15161, Hamilton FAB0018 | Prior to 15/11/2021 Steel tanks to AS 1692: 1989 Category 2 As of 15/11/2021 AS 1692:2006, Category 2 | 1950 L - Above ground single skin horizontal cylindrical ground stationary tank Safe Fill Level: 1877 litres | Prior to 15/11/2021 3.1A, 3.1C, 3.1D As of 15/11/2021 Aviation gasoline Avgas 100 and Avgas 100LL UN No. 1203 - Class 3.1A, 6.7B Diesel - Class 3.1D, 6.7B Marine diesel fuel UN No. 1202 - Class 3.1C, 3.1D, 6.7B Petroleum (unleaded) UN No. 1203 - Class 3.1A, 6.7B | Mainline Sheetmetals Ltd. | All tanks are to be manufactured strictly in accordance with AS 1692:2006, Category 2 as applicable. Secondary containment subject to installed stationary container system compliance certificates. All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to beprovided in accordance with AS 1692:2006 for category 2 tanks. It is Mainline Sheetmetals Ltd's responsibility to ensure the correct size vents are fitted. Optional return pipe - Drawing No.: CB-SW-1107, Sheets: 1, Date: 5/11/21, Description: Optional return pipe, Drawn by: C Besley. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture / pressuretest, AS 1692:2006 Category 2, test pressure in kPa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all fill / dip tubes in accordance with the requirements of AS 1692:2006. Design Statement – Job No. 19-305 – In respect of: 1950L ground tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 7/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692). Design Statement, issued by: Stiles and Hooker Ltd, to: Mainline Sheetmetals Ltd, in respect of: 1950L Split Ground Tank. Tank design to AS1692, seismic and wind loading to AS/NZS1170, structure to AS/NZS3404. Signed by Roger Baker (CMEngNZ), dated 14/06/2022. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standard/s. | N/A | FAB0018
TNK0710 | 21/11/2014 27/07/2021 - Renewed | Mainline Sheetmetals Ltd. | Mainline Sheetmetals Ltd, 209 Ellis St, Frankton Hamilton 3240 PO Box 15161, Hamilton FAB0018 | Prior to 27/07/2021 Steel tanks to AS 1692: 1989 Category 2 As of 27/07/2021 AS 1692:2006, Category 2 | 590 L - Single skin horizontal cylindrical above ground boiler stationary tank Safe Fill Level: 560 litres | Prior to 27/07/2021 3.1A, 3.1C, 3.1D As of 27/07/2021 Diesel 3.1D, 6.7B | Mainline Sheetmetals Ltd. | 590 litre single skin, single compartment aboveground diesel storage boiler tank. Diameter 0.777m x 1.268m long x 3mm Gr250 mild steel shell and ends. All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to be provided in accordance with AS 1692:2006 for category 2 tanks. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe ﬁll height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all the fill / dip tubes in accordance with the requirements of AS 1692. Design Statement – Job No. 19-305 – In respect of: 590L single skin boiler tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 25/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692): Anchor and foundation requirements for 590L single skin boiler tank, with following parameters: Tank category 2, in accordance with AS 1692 Design wind speed = 56m/s (any NZ location) Design earthquake lateral force coefficient Cd(T) = 0.8g Hazard factor Z ≤ 0.45, importance level 2 and 25 years design life Minimum anchoring requirements: 1-M10 trubolt at each leg (T10085X) and 5mm thick footplate Minimum foundation requirements: 1.4m x 1m x 0.15m thick concrete slab, with SE72 mesh Approved to supply a burner or engine (boiler). Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. | N/A | FAB0018
TNK0711 | 21/11/2014 27/07/2021 - Renewed | Mainline Sheetmetals Ltd. | Mainline Sheetmetals Ltd, 209 Ellis St, Frankton Hamilton 3240 PO Box 15161, Hamilton FAB0018 | Prior to 27/07/2021 Steel tanks to AS 1692: 1989 Category 2 As of 27/07/2021 AS 1692:2006, Category 2 | 950 L - Single skin horizontal cylindrical above ground boiler stationary tank Safe Fill Level: 940 litres | Prior to 27/07/2021 3.1A, 3.1C, 3.1D As of 27/07/2021 Diesel 3.1D, 6.7B | Mainline Sheetmetals Ltd. | 950 litre single skin, single compartment aboveground diesel storage boiler tank. Diameter 1.006m x 1.268m long x 3mm Gr250 mild steel shell and ends. All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to be provided in accordance with AS 1692:2006 for category 2 tanks. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe ﬁll height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all the fill / dip tubes in accordance with the requirements of AS 1692. Design Statement – Job No. 19-305 – In respect of: 950L single skin boiler tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 25/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692): Anchor and foundation requirements for 950L single skin boiler tank, with following parameters: Tank category 2, in accordance with AS 1692 Design wind speed = 56m/s (any NZ location) Design earthquake lateral force coefficient Cd(T) = 0.8g Hazard factor Z ≤ 0.45, importance level 2 and 25 years design life Minimum anchoring requirements: 1-M10 trubolt at each leg (T10085X) and 5mm thick footplate Minimum foundation requirements: 1.4m x 1.2m x 0.15m thick concrete slab, with SE72 mesh Approved to supply a burner or engine (boiler). Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. | N/A | FAB0018
TNK0712 | 21/11/2014 27/07/2021 - Renewed | Mainline Sheetmetals Ltd. | Mainline Sheetmetals Ltd, 209 Ellis St, Frankton Hamilton 3240 PO Box 15161, Hamilton FAB0018 | Prior to 27/07/2021 Steel tanks to AS 1692: 1989 Category 2 As of 27/07/2021 AS 1692:2006, Category 2 | 1400 L - Single skin horizontal cylindrical above ground boiler stationary tank Safe Fill Level: 1338 litres | Prior to 27/07/2021 3.1A, 3.1C, 3.1D As of 27/07/2021 Diesel 3.1D, 6.7B | Mainline Sheetmetals Ltd. | 1400 litre single skin, single compartment aboveground diesel storage boiler tank. Diameter 1.078m x 1.558m long x 3mm Gr250 mild steel shell and ends. All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to be provided in accordance with AS 1692:2006 for category 2 tanks. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe ﬁll height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all the fill / dip tubes in accordance with the requirements of AS 1692. Design Statement – Job No. 19-305 – In respect of: 1400L single skin boiler tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 7/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692): Anchor and foundation requirements for 1400L single skin boiler tank, with following parameters: Tank category 2, in accordance with AS 1692 Design wind speed = 56m/s (any NZ location) Design earthquake lateral force coefficient Cd(T) = 0.8g Hazard factor Z ≤ 0.45, importance level 2 and 25 years design life Minimum anchoring requirements: 1-M10 trubolt at each leg (T10085X) and 5mm thick footplate Minimum foundation requirements: 1.9m x 2.3m x 0.15m thick concrete slab, with SE72 mesh Approved to supply a burner or engine (boiler). Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. | N/A | FAB0018
TNK0713 | 21/11/2014 27/07/2021 - Renewed | Mainline Sheetmetals Ltd. | Mainline Sheetmetals Ltd, 209 Ellis St, Frankton Hamilton 3240 PO Box 15161, Hamilton FAB0018 | Prior to 27/07/2021 Steel tanks to AS 1692: 1989 Category 2 As of 27/07/2021 AS 1692:2006, Category 2 | 1950 L - Single skin horizontal cylindrical above ground boiler stationary tank Safe Fill Level: 1877 litres | Prior to 27/07/2021 3.1A, 3.1C, 3.1D As of 27/07/2021 Diesel 3.1D, 6.7B | Mainline Sheetmetals Ltd. | 1950 litre single skin, single compartment aboveground diesel storage boiler tank. Diameter 1.276m x 1.558m long x 3mm Gr250 mild steel shell and ends. All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to be provided in accordance with AS 1692:2006 for category 2 tanks. It is Mainline Sheetmetals Ltd's responsibility to ensure the correct size vents are fitted. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe ﬁll height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all the fill / dip tubes in accordance with the requirements of AS 1692. Design Statement – Job No. 19-305 – In respect of: 1950L single skin boiler tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 7/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692): Anchor and foundation requirements for 1950L single skin boiler tank, with following parameters: Tank category 2, in accordance with AS 1692 Design wind speed = 56m/s (any NZ location) Design earthquake lateral force coefficient Cd(T) = 0.8g Hazard factor Z ≤ 0.45, importance level 2 and 25 years design life Minimum anchoring requirements: 1-M10 trubolt at each leg (T10085X) and 5mm thick footplate Minimum foundation requirements: 2m x 2.3m x 0.15m thick concrete slab, with SE72 mesh Approved to supply a burner or engine (boiler). Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. | N/A | FAB0018
TNK0714 | 2014-11-21 | Mainline Sheetmetals Ltd., Hamilton | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161 FAB0018 | Steel tanks to AS 1692: 1989 Category 4 | 5000 litre boiler tank | 3.1A, 3.1C, 3.1D | Mainline Sheetmetals Ltd. | SEE CURRENT TEST CERTIFICATE FOR APPROVAL CONDITIONS | 2019-05-18 | FAB0018
TNK0715 | 2007-03-04 | Transtank | Quingdao Jinhuanghai Container Co Ltd | Double walled steel tanks to AS1692: 2006 Cat 3 | Transtank 2,500 litre tank | Diesel | Quingdao Jinhuanghai Container Co Ltd Transtank, China Division |  | 2012-03-04 | Manufactured by Quingdao Jinhuanghai Container Co Ltd (FAB0006) under licence from Trankstank. FAB0006 - expired
TNK0716 | 2007-03-04 | Transtank | Quingdao Jinhuanghai Container Co Ltd | Double walled steel tanks to AS1692: 2006 Cat 3 | Transtank 4,500 litre tank | Diesel | Quingdao Jinhuanghai Container Co Ltd Transtank, China Division |  | 2012-03-04 | Manufactured by Quingdao Jinhuanghai Container Co Ltd (FAB0006) under licence from Trankstank. FAB0006 - expired
TNK0717 | 2007-03-04 | Transtank | Quingdao Jinhuanghai Container Co Ltd | Double walled steel tanks to AS1692: 2006 Cat 3 | Transtank 10,000 litre tank | Diesel | Quingdao Jinhuanghai Container Co Ltd Transtank, China Division |  | 2012-03-04 | Manufactured by Quingdao Jinhuanghai Container Co Ltd (FAB0006) under licence from Trankstank. FAB0006 - expired
TNK0718 | 2007-03-04 | Transtank | Quingdao Jinhuanghai Container Co Ltd | Double walled steel tanks to AS1692: 2006 Cat 3 | Transtank 12,000 litre tank | Diesel | Quingdao Jinhuanghai Container Co Ltd Transtank, China Division |  | 2012-03-04 | Manufactured by Quingdao Jinhuanghai Container Co Ltd (FAB0006) under licence from Trankstank. FAB0006 - expired
TNK0719 | 2007-03-04 | Transtank | Quingdao Jinhuanghai Container Co Ltd | Double walled steel tanks to AS1692: 2006 Cat 3 | Transtank 20,000 litre tank | Diesel | Quingdao Jinhuanghai Container Co Ltd Transtank, China Division |  | 2012-03-04 | Manufactured by Quingdao Jinhuanghai Container Co Ltd (FAB0006) under licence from Trankstank. FAB0006 - expired
TNK0720 | 2007-03-04 | Transtank | Quingdao Jinhuanghai Container Co Ltd | Double walled steel tanks to AS1692: 2006 Cat 3 | Transtank 30,000 litre tank | Diesel | Quingdao Jinhuanghai Container Co Ltd Transtank, China Division |  | 2012-03-04 | Manufactured by Quingdao Jinhuanghai Container Co Ltd (FAB0006) under licence from Trankstank. FAB0006 - expired
TNK0721 | 2007-03-04 | Transtank | Quingdao Jinhuanghai Container Co Ltd | Double walled steel tanks to AS1692: 2006 Cat 3 | Transtank 55,000 litre tank | Diesel | Quingdao Jinhuanghai Container Co Ltd Transtank, China Division |  | 2012-03-04 | Manufactured by Quingdao Jinhuanghai Container Co Ltd (FAB0006) under licence from Trankstank. FAB0006 - expired
TNK0722 | 2007-03-04 | Transtank | Quingdao Jinhuanghai Container Co Ltd | Double walled steel tanks to AS1692: 2006 Cat 3 | Transtank 68,000 litre tank | Diesel | Quingdao Jinhuanghai Container Co Ltd Transtank, China Division |  | 2012-03-04 | Manufactured by Quingdao Jinhuanghai Container Co Ltd (FAB0006) under licence from Trankstank. FAB0006 - expired
TNK0723 | 2007-03-04 | Transtank | Quingdao Jinhuanghai Container Co Ltd | Double walled steel tanks to AS1692: 2006 Cat 3 | Transtank 80,000 litre tank | Diesel | Quingdao Jinhuanghai Container Co Ltd Transtank, China Division |  | 2012-03-04 | Manufactured by Quingdao Jinhuanghai Container Co Ltd (FAB0006) under licence from Trankstank. FAB0006 - expired
TNK0724 | 2007-03-04 | Transtank | Quingdao Jinhuanghai Container Co Ltd | Double walled steel tanks to AS1692: 2006 Cat 3 | Transtank 85,000 litre tank | Diesel | Quingdao Jinhuanghai Container Co Ltd Transtank, China Division |  | 2012-03-04 | Manufactured by Quingdao Jinhuanghai Container Co Ltd (FAB0006) under licence from Trankstank. FAB0006 - expired
TNK0725 | 2007-03-04 | Transtank | Quingdao Jinhuanghai Container Co Ltd | Double walled steel tanks to AS1692: 2006 Cat 3 | Transtank 100,000 litre tank | Diesel | Quingdao Jinhuanghai Container Co Ltd Transtank, China Division |  | 2012-03-04 | Manufactured by Quingdao Jinhuanghai Container Co Ltd (FAB0006) under licence from Trankstank. FAB0006 - expired
TNK0726 | 2007-03-04 | Transtank | Quingdao Jinhuanghai Container Co Ltd | Double walled steel tanks to AS1692: 2006 Cat 3 | Transtank 110,000 litre tank | Diesel | Quingdao Jinhuanghai Container Co Ltd Transtank, China Division |  | 2012-03-04 | Manufactured by Quingdao Jinhuanghai Container Co Ltd (FAB0006) under licence from Trankstank. FAB0006 - expired
FAB0009 | 2007-03-13 |  | Alan Poulsen Engineering Ltd 10 Kitchener Street Dunedin | AS 1692-2006, HSNOCOP24-1, 03-08 | Up to 100,000 L tanks | Approved for stationary tanks for flammable liquids 3.1A, 3.1B, 3.1C or 3.1D as approved. | Alan Poulsen Engineering Ltd | Fabrication, inspection and testing in accordance with AS1692-2006, RSC SWI 2017 and approved design drawings. Allocation of individual tank serial numbers. Retention of individual tank QA records. | 2023-07-17 | Fabricator of: TNK0730, TNK0741, TNK0742, TNK0872
TNK0730 | 2007-03-13 | Alan Poulsen Engineering Ltd 10 Kitchener Street Dunedin PO Box 238 Dunedin 9054 | Prior to 24/09/2024 Alan Poulsen Engineering Ltd 10 Kitchener Street Dunedin FAB0009 As of 24/09/2024 PETROLEUM SOLUTIONS 2024 LIMITED 10 Kitchener Street, Dunedin Central, Dunedin, 9016 PO Box 238, Dunedin, Dunedin Central, Dunedin, 9054 FAB0099 | Above Ground Tanks (Single and Double skinned) to AS 1692-2006 Category 4 | Description: General Arrangement - Horizontal Double/Single Skin Cylindrical Tanks Design Specification: AS1692: 2006, Category 4 Tank Type: Above Ground Stationary Tank Name of Designer: Ross Dickson Capacity: 500 to 60,000 Litres Compartments: 1 | Prior to 24/04/2020 Petrol Diesel As of 24/04/2020 Class 3.1A, 3.1B, 3.1C or 3.1D in Single Skin configuration. 3.1D in Double Skin configuration. Classes 6.1A, 9. | Alan Poulsen Engineering Ltd 10 Kitchener Street Dunedin PO Box 238 Dunedin 9054 | Specific venting design required for each individual installation. Design approved to supply an engine or burner. Re-certification required following any change to the design parameters and / or referenced Alan Poulsen Engineering Limited Drawings. | 2030-04-24 | FAB0009 (authorised for class 3 substances only) FAB0099
TNK0727 | 2007-03-24 | Hubbards Machinery (2005) Ltd |  | Steel Tanks to AS1692: 2006 Cat 3 | 506 litre tank | Petroleum (unleaded) Avgas 100 and 100LL Diesel Fuel (automotive) Diesel Fuel (marine) | Hubbards Machinery (2005) Ltd |  | 2012-03-04 | Chase up FAB number. Name now Tank leasing limited.
TNK0728 | 2007-03-24 | Hubbards Machinery (2005) Ltd |  | Steel Tanks to AS1692: 2006 Cat 3 | 1048 litre tank | Petroleum (unleaded) Avgas 100 and 100LL Diesel Fuel (automotive) Diesel Fuel (marine) | Hubbards Machinery (2005) Ltd |  | 2012-03-04 | Chase up FAB number
TNK0729 | 2007-03-24 | Hubbards Machinery (2005) Ltd |  | Steel Tanks to AS1692: 2006 Cat 3 | 1985 litre tank | Petroleum (unleaded) Avgas 100 and 100LL Diesel Fuel (automotive) Diesel Fuel (marine) | Hubbards Machinery (2005) Ltd |  | 2012-03-04 | Chase up FAB number
FAB0010 | 2007-04-16 |  | Stainless Engineering Co Ltd 17 Neil Park Drive East Tamaki Auckland | [5 empty] | 2010-04-16 | Expired - No listed TNK numbers
TNK0734 | 2007-05-04 | Armatec Environmental Ltd |  | Above Ground tanks to AS 2634:1983 & BS 4994: 1987 | 5,000 litres | Sodium Hydroxide Sodium Hypochlorite |  |  | 2012-05-04 | Fabricated by Armatec Environmental Ltd (FAB004) - expired
TNK0735 | 2007-05-04 | Armatec Environmental Ltd |  | Above Ground tanks to AS 2634:1983 & BS 4994: 1987 | 1,200 litres | Hydrogen Peroxide Peracetic Acid |  |  | 2012-05-04 | Fabricated by Armatec Environmental Ltd (FAB004) - expired
TNK0733 | 2007-05-17 | Service Engineers Ltd |  | Stainless Steel Above Ground tanks to AS1692 Category 5 | 12,000 Litres | Sodium Hydroxide Aluminium sulphate |  |  | 2012-05-17 | Fabricated by Service Engineers Ltd (FAB011) - expired
FAB0011 | 2007-05-18 |  | Service Engineers Ltd 50 - 52 Porana Rd Takapuna Auckland | [5 empty] | 2010-05-18 | Fabricator of: TNK0733, TNK0858, TNK0859, TNK0860, TNK13073
TNK0743 | 2007-05-30 | Taylors Manufacturing Ltd |  | Double skin steel storage tank. 8,500 L to 10,000l. Located within concrete vault unit | AS 1692. 6mm mild steel plate | 3.1C and 3.1D | Taylors Manufacturing Ltd |  | 2012-05-30 | FAB0048
TNK0744 | 2007-05-30 | Taylors Manufacturing Ltd |  | Double skin steel storage tank. 500 L to 2,000l. Located within concrete vault unit | AS 1692. 6mm mild steel plate | 3.1C and 3.1D | Taylors Manufacturing Ltd |  | 2012-05-30 | FAB0048
TNK0745 | 2007-05-30 | Taylors Manufacturing Ltd |  | Double skin steel storage tank. 4,000 L to 8,000l. Located within concrete vault unit | AS 1692. 6mm mild steel plate | 3.1C and 3.1D | Taylors Manufacturing Ltd |  | 2012-05-30 | FAB0048
TNK0746a | 2007-05-30 | Taylors Manufacturing Ltd |  | Double skin steel storage tank. 2,500 L to 5,000l. Located within concrete vault unit | AS 1692. 6mm mild steel plate | 3.1C and 3.1D | Taylors Manufacturing Ltd |  | 2012-05-30 | FAB0048 TNK number allocated to two entries, assigned TNK0746a
TNK0736 | 2007-06-07 | Filtration Technology Ltd |  | Above ground tanks to AS1692-2006/Specific Design | 10,000 litres | Acetic Acid |  |  | 2022-06-07 | Fabricted by Filtration Technology - unable to find Fab number
TNK0746b | 2007-06-29 | ETECH NZ Ltd |  | Stainless Steel Tanks to AS1692:2006 Category 3 | 500 litres |  |  |  | 2012-06-29 | FAB0028 - expired TNK number allocated to two entries, assigned TNK0746b
TNK0737 | 2007-07-17 | Filtration Technology Ltd |  | Above ground tanks to AS1692-2006/Specific Design | 7,500 litres | Methanol |  |  | 2022-07-17 | Fabricted by Filtration Technology - unable to find Fab number
TNK0732 | 2007-07-27 | Hubbards Machinery (2005) Ltd |  | Steel Tanks to AS1692: 2006 Cat 3 | Dual compartment tanks (1480 L and 500 L) | Petrol Diesel Fuel automotive and marine | Hubbards Machinery (2005) Ltd |  | 2012-05-12 | Hubbards Machinery (2005) Ltd Missing Fab
TNK0747 | 2007-07-27 | ETECH NZ Ltd |  | Stainless Steel Tanks to AS1692:2006 Category 3 | 250 litres |  |  |  | 2012-07-27 | FAB0028 - expired
FAB0012 | 2007-08-16 |  | TP Engineering 256 Roscommon Rd Wiri Manakau City | [5 empty] | 2010-08-16 | Fabricator of: TNK0740, TNK13043
TNK0738 | 2007-08-30 | Mainline Sheetmetals Ltd., Hamilton | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161 FAB0018 | Above ground single compartment storage tanks to AS 1692-2006 Class 4 | 10,000 litres | Diesel | Mainline Sheet Metals, Hamilton |  | 2017-08-22 | FAB0018
TNK0739 | 2007-08-30 | Mainline Sheetmetals Ltd., Hamilton | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161 FAB0018 | Above ground single compartment storage tanks to AS 1692-2006 Class 4 | 6800 litres | Diesel | Mainline Sheet Metals, Hamilton |  | 2017-08-22 | FAB0018
TNK0731 | 2007-09-12 | Fuelquip Services Ltd |  | Transcube Steel tanks to AS1692: 2006 Cat 2 | 450 L | Class 3.1A flammable liquids |  | 1. When used in temporary installations the hose connecting tank to any generator: a. must meet ISO 7840-A1; and b. is limited to diesel use only; and c. must be protected; and d. must be a maximum length of 5 metres; and e. must meet the requirements of clauses 58(2)(a)(iii) and 58(2)(a)(iv) of Schedule 8 of the Hazardous Substances (Dangerous Goods and Scheduled Toxic Substances) Transfer Notice 2004 2. The maximum length of time a temporary installation can be in place is 30 calendar days. 3. If being transported while full these tanks are classified as transportable containers and must meet the requirements of regulations 30 and 31 of the Hazardous Substances (Tank Wagons and Transportable Containers) Regulations 2004. | 2012-05-06 | Unsure of FAB number
TNK0740 | 2007-09-18 | Meo Engineering Group |  | Double skin steel horizontal cylinderical above ground tank to AS 1692: 2006 Class 4 | 30,000 litres | Narrow cut kerosene Low aromatic white spirits |  |  | 2012-09-18 | Fabricated by TP Engineering (FAB0012) - expired
TNK0741 | 2007-11-05 | Alan Poulsen Engineering Ltd 10 Kitchener Street Dunedin | Prior to 24/09/2024 Alan Poulsen Engineering Ltd 10 Kitchener Street Dunedin FAB0009 As of 24/09/2024 PETROLEUM SOLUTIONS 2024 LIMITED 10 Kitchener Street, Dunedin Central, Dunedin, 9016 PO Box 238, Dunedin, Dunedin Central, Dunedin, 9054 FAB0099 | Carbon Steel Tanks to AS1692 | 1,000 L | 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Alan Poulsen Engineering Ltd 10 Kitchener Street Dunedin PO Box 238 Dunedin 9054 |  |  | Concrete Secondary Containers manufactured by Allied Concrete, Gore. FAB0009 FAB0099
TNK0742 | 2007-11-05 | Alan Poulsen Engineering Ltd 10 Kitchener Street Dunedin | Prior to 24/09/2024 Alan Poulsen Engineering Ltd 10 Kitchener Street Dunedin FAB0009 As of 24/09/2024 PETROLEUM SOLUTIONS 2024 LIMITED 10 Kitchener Street, Dunedin Central, Dunedin, 9016 PO Box 238, Dunedin, Dunedin Central, Dunedin, 9054 FAB0099 | Carbon Steel Tanks to AS1692 | 2,500 L | 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Alan Poulsen Engineering Ltd 10 Kitchener Street Dunedin PO Box 238 Dunedin 9054 |  |  | Concrete Secondary Containers manufactured by Allied Concrete, Gore. FAB0009 FAB0099
TNK0848 | 2008-02-12 | Balance Agri-Nutrients Ltd Southport NZ Ltd Site Bluff |  | 7,698 m3 Above Ground Tank | API 650: tenth Edition, Addendum 1, Jan 2000 Tank ID: SBT100 Year 2002 Capacity: 7,698 m3 | Classes 6.1D, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A, 9.1D | Balance Agri-Nutrients Ltd Southport NZ Ltd Site Bluff | This certificate becomes invalid following any change of service or to the original design parameters |  | Unsure of FAB number
TNK0801 | 2008-02-21 |  | John Russell Engineering (FAB0003 expired 23/07/2016) NYMIC Engineering Ltd (FAB0023 as of 14/06/2016) | Mild Steel Tanks to AS 1692: 2006, Category 2 | 1,800 litre | Diesel | John Russell Engineering Ltd |  |  | Fabricated by John Russell Engineering (FAB0003) Fabricated by NYMIC Engineering Ltd (FAB0023) as of 14/06/2016
TNK0802 | 2008-02-21 |  | John Russell Engineering (FAB0003 expired 23/07/2016) NYMIC Engineering Ltd (FAB0023 as of 14/06/2016) | Mild Steel Tanks to AS 1692: 2006, Category 4 | 3,000 litre | Diesel | John Russell Engineering Ltd |  |  | Fabricated by John Russell Engineering (FAB0003) Fabricated by NYMIC Engineering Ltd (FAB0023) as of 14/06/2016
TNK0803 | 2008-02-21 |  | John Russell Engineering (FAB0003 expired 23/07/2016) NYMIC Engineering Ltd (FAB0023 as of 14/06/2016) | Mild Steel Tanks to AS 1692: 2006, Category 4 | 5,000 litre | Diesel | John Russell Engineering Ltd |  |  | Fabricated by John Russell Engineering (FAB0003) Fabricated by NYMIC Engineering Ltd (FAB0023) as of 14/06/2016
TNK0804 | 2008-02-21 |  | John Russell Engineering (FAB0003 expired 23/07/2016) NYMIC Engineering Ltd (FAB0023 as of 14/06/2016) | Mild Steel Tanks to AS 1692: 2006, Category 4 | 10,000 litre | Diesel | John Russell Engineering Ltd |  |  | Fabricated by John Russell Engineering (FAB0003) Fabricated by NYMIC Engineering Ltd (FAB0023) as of 14/06/2016
TNK0805 | 2008-02-21 |  | John Russell Engineering (FAB0003 expired 23/07/2016) NYMIC Engineering Ltd (FAB0023 as of 14/06/2016) | Mild Steel Tanks to AS 1692: 2006, Category 4 | 19,600 litre | Diesel | John Russell Engineering Ltd |  |  | Fabricated by John Russell Engineering (FAB0003) Fabricated by NYMIC Engineering Ltd (FAB0023) as of 14/06/2016
TNK0806 | 2008-03-25 |  | Armatec Environment Ltd | Cylinderical above ground process containers to BS 4994:1987 | 1800 litre | Sodium hydroxide Calcium hydroxide |  |  |  | Fabricated by Armatec Environmental Ltd (FAB004) - expired
TNK0807 | 2008-03-31 | Oilcon Limited |  | Sledge Tanks to AS1692:2006, Category 4 | 5,000 - 50,000 litre | 3.1D, 6.1E, 6.3B, 6.B, 9.1B |  |  |  | FAB0075
TNK0808 | 2008-03-31 | Oilcon Limited |  | Fixed Base Tanks to AS1692:2006, Category 5 | 5,000 - 50,000 litre | 3.1D, 6.1E, 6.3B, 6.B, 9.1B |  |  |  | FAB0075
TNK0809 | 2008-04-14 |  | HSM Engineering | Stainless Steel vertical cylinderical above ground tanks to AS 1692, Category 5 | 24,000 litre | Sodium hydroxide Sodium hypochlorite Nitric Acid 1.5% |  |  | 2013-04-14 | Fabricated by HSM Engineering Ltd (FAB005) - expired
TNK0812 | 2008-05-01 | Transtank | Prior to 30/04/2021: Quingdao Jinhuanghai Container Co Ltd FAB0006 As of 30/04/2021: APD Ltd PO Box 12663 Penrose, Auckland 1642 49 McLaughlins Road, Wiri, Auckland, 2104 FAB0032 | Double walled steel tanks to AS1692: 2006 Cat 3 | Transtank 96,400 litre tank | Diesel | Quingdao Jinhuanghai Container Co Ltd Transtank, China Division |  | 2013-05-01 | Prior to 30/04/2021: Manufactured by Quingdao Jinhuanghai Container Co Ltd (FAB0006) under licence from Trankstank - expired As of 30/04/2021: APD Ltd PO Box 12663 Penrose, Auckland 1642 49 McLaughlins Road, Wiri, Auckland, 2104 (FAB0032)
TNK0811 | 2008-05-09 |  | Martin Engineering (Palmerston North) Ltd. | Above ground tanks to AS 1692: 2006 Category 4 FAB0045 | 3,000 litre | Diesel | Martin Engineering (Palmerston North) Ltd. |  | 2013-05-09 | FAB0045
TNK0810 | 2008-05-14 |  | Martin Engineering (Palmerston North) Ltd. | Steel above ground tanks to AS 1692: 2006 Category 4 FAB0045 | 1,000 litre | Diesel | Martin Engineering (Palmerston North) Ltd. |  | 2013-05-14 | FAB0045
TNK0813 | 2008-05-30 |  | Martin Engineering (Palmerston North) Ltd. | Steel above ground tank to AS 1692: 2006 Category 4 FAB0045 | 15,000 litres | Diesel | Martin Engineering (Palmerston North) Ltd. |  | 2013-05-30 | FAB0045
TNK0849 | 2008-06-03 | Mercer Stainless Ltd Corbett Road Bell Block New Plymouth |  | 3,000 litre Above Ground Tank | AS 1692 - 2006, Specific Design Tank ID: NP08-15456-1 Manufacture Year: 2008 Capacity: 3,000 litres | Nitric Acid, 0.5 - 10% aqueous solution 6.1E, 6.9B, 8.1A, 8.2C, 8.3A | Mercer Stainless Ltd Corbett Road Bell Block New Plymouth | This certificate becomes invalid following any change of service or to the original design parameters and / or Mercer drawing number 13877, Rev B, Sheet A2 dated 20/03/2008 |  | Unsure of Fab number
TNK0850 | 2008-06-04 | Mercer Stainless Ltd Corbett Road Bell Block New Plymouth |  | 3,000 litre Above Ground Tank | AS 1692 - 2006, Specific Design Tank ID: NP08-15456-2 Manufacture Year: 2008 Capacity: 3,000 litres | Sodium Hydroxide, 0.5 - 2% aqueous solution 6.1E, 6.3A, 6.4A | Mercer Stainless Ltd Corbett Road Bell Block New Plymouth | This certificate becomes invalid following any change of service or to the original design parameters and / or Mercer drawing number 13880, Rev B, Sheet A2 dated 20/03/2008 |  | Unsure of Fab number
TNK0815 | 2008-06-15 | APD Ltd PO Box 12663 Auckland |  | Aboveground Tank to HSNOCOP 4-2, BS EN1778, BS EN 12573 | Up to 20,000 L safe fill limit polyethylene/polypropylene vertical cylindrical above-ground tanks | 5.1, 6.1, 6.3, 6.4, 6.5, 6.6, 6.7, 6.8, 6.9, 8.1, 8.2, 8.3, 9.1, 9.2, 9.3, 9.4, with NIL Flammable Content | APD Limited | Subject to the conditions specified on the Test Certificate ST5221Ren | 2018-06-14 | FAB0032 prior to 30/4/2021
FAB0013 | 2008-06-20 |  | Shidao U-Fuel Equipment Manufacturing Co, PRC, First Industrial Park of Shidao Development Area Roncheng, Shandong Province 264309 Peoples Republic of China | AS 1692 Category 4 | 114,000L |  | HazTec Ltd, Silverdale, Auckland Nth |  | 2011-06-20 | Fabricator of: TNK0814
TNK0814 | 2008-06-20 | Shidao U-Fuel Equipment Manufacturing Co, PRC |  | AS 1692 Cat. 4 | U-Fuel 40,000L 2.29 metre dia. X 9.72 metre o.l. single or double compartment containerised refueling units and box stations for diesel fuel only. | Diesel with a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | U-Fuel Holdings New Zealand Ltd | Subject to the conditions specified on the Test Certificate ST5303Ren | 2018-07-06 | Fabricated by Shidao U-Fuel Equipment Manufacturing Co (FAB013)
TNK0852 | 2008-07-03 |  | HSM Engineering NZ Ltd PO Box 58 455 Greenmount Auckland | 15,000 litre Single Skin Steel Vertical Cylindrical Above-Ground Tank for ASA ASAPHONIC (TDI-XYLENE) | AS 1692 Category 5 Location: Sleepyhead, Auckland | 6.1A, 6.3A, 6.4A, 6.5A, 6.5B, 6.7B, 6.9A, 9.1C, 9.3B | HSM Engineering NZ Ltd PO Box 58 455 Greenmount Auckland | Drawing Reference: HSM Engineering No. 1723/2 | 2013-07-03 | FAB0005 - expired
FAB0032 | 2008-07-21 |  | APD Ltd PO Box 12663 Penrose, Auckland 1642 49 McLaughlins Road, Wiri, Auckland, 2104 | BS EN 12573 and Thermoplastic stationary tanks – Safe Work Instrument 2017 (previously included HSNOCOP 4-3) Pre - 9/04/2024 Includes tanks with internal liners in accordance with AS 2634 or BS EN 13121 Post - 9/04/2024 Includes tanks with internal liners in accordance with ASME RTP-1-2019 | Vertical cylindrical above ground thermoplastic stationary tanks Capacity: up to 60,000 litres | Class 5, 6, 8 and 9 substances | APD Ltd PO Box 12663 Penrose, Auckland 1642 49 McLaughlins Road, Wiri, Auckland, 2104 | Allocation of unique individual tank serial number to be stamped on each individual tank and recorded. Retention of individual tank fabrication, testing records and QA records for each tank. WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the compliance certifier who issued the certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2027-04-09 | Fabricator of: Prior to 30/04/2021 TNK0815 Pre - 9/04/2024 TNK0601, TNK0602, TNK0607, TNK 0812, TNK0862, TNK19015 Post - 9/04/204 TNK19015, TNK20449
TNK0853 | 2008-07-31 |  | Armatec Environment Ltd (Approved Fabricator No. FAB0004) | Armatec 5000 L GRP 1830 mm Dia x 2700 mm Hi Vertical Cylindrical Above - Ground tank for Nitric/Sulphuric/Phosphoric Acids (Ecolab AC300E Soln) | AS 2634 & BS 4994 Location: Fonterra, Hawera | 6.1D, 6.7A, 6.9A, 6.9B, 8.1A, 8.2B, 8.2C, 8.3A, 9.1D, 9.3C | Armatec Environmental Ltd PO Box 2046 Fitzroy New Plymouth | Armatec Environmental Ltd E3465-04 Sheet 1 rev. 2 | 2013-07-31 | FAB0004 - expired
TNK0854 | 2008-08-13 | Orica New Zealand Ltd 308 Morrinsville-Walton Road Morrinsville |  | 13,660 litre Above Ground Process Container | AS 1692-2006, Specific Design | 6.1A, 6.3A, 6.4A, 8.2C, 8.3A, 9.3B | Orica New Zealand Ltd 308 Morrinsville-Walton Road Morrinsville | Must be as per drawing numbers MVCH/M/24/005/012, Sheets 1 to 6, Rev 0 |  | Unsure of FAB number
TNK0865 | 2008-08-13 | Orica New Zealand Ltd 308 Morrinsville-Walton Road Morrinsville |  | 13,660 litre Above Ground Process Container | AS 1692-2006, Specific Design Manufacture Year: 2008 | The storage & transfer of classes 6.1A, 6.3A, 6.4A, 8.2C, 8.3A, 9.3B |  | This certificate becomes invalid following any change to the original design parameters and / or drawing numbers MVCH/M/24/005/012, Sheets 1 to 6, Rev 0 |  | Unsure of FAB number
FAB0014 | 1/09/2008 26/07/2012 26/7/2015 |  | Advanced Fuel Tanks N.Z. Ltd 5 Tanya St, Bromley, Christchurch | Above ground steel stationary containers (flammables) as listed below: Supervault FL, SWRI 93-01, AS1692 & UL142 Supervault MH, SWRI 95-03, AS1692 & UL142 Protector Double Wall SWRI 97-04, AS1692 & UL142 Vanguard AS1692 Portaqube AS1692 | Refence: TNK0872, 0873, 0874, 0875, 0876, 0882, 12004, 13010, 13011, 13012, 13013, 13014, 13015, 13016, 13017, 13058, 16017, 17011, 17012, 17021, 17024 | Class 3.1A, B, C & D | Advanced Fuel Tanks N.Z Ltd |  | 2018-07-26 | Fabricator of : TNKs 0872, 0873, 0874, 0875, 0876, 0882, 12004, 13010, 13011, 13012, 13013, 13014, 13015, 13016, 13017, 13058, 16017, 17024 | TNK0610 TNK0611
TNK0855 | 2008-09-23 |  | Armatec Environment Ltd (Approved Fabricator No. FAB0004) | 20,000 litre Fi-glass Vertical Cylindrical Above-ground Tank for Sodium Hydroxide 46% | AS 2634 / BS4994 NZ Steel, Glenbrook | 6.1D, 8.1A, 8.2B, 8.3A, 9.1D | Armatec Environmental Ltd PO Box 2046 Fitzroy New Plymouth | Armatec Environmental Ltd E3476-04 Sheet 1 Rev. 0 | 2013-09-23 | FAB0004 - expired
TNK0817 | 2008-10-31 | Norske Skog Tasman, Fletcher Avenue, Kawerau | HSM Engineering Ltd, 11 Neales Road, East Tamaki, PO Box 58-455, Greenmount, Manukau 2141 | Aboveground Storage & Transfer H2O2 Tank to API 650, 11th Edition, Appendix S | 66,000L H2O2 Storage Tank | Up to 70% H2O2 | HSM Engineering Ltd | As per drawing EM-002--01, Rev 0, 22 Oct 08 | NA | FAB0005 - expired
TNK0818 | 2008-11-20 |  | Petroleum Soutions Ltd, PO Box 97 310 South Auckland Mail Centre Manukau City Auckland | 850 L Double Skin Steel Horizontal Rectanular Above-ground Diesel Day Tank | 850L, To AS1692 Category 3 | Classes 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petroleum Services Ltd | Drawing reference PSL 10023 850 DW | 2013-11-20 | FAB002. Tank intended for Various Locations
FAB0016 | 21/11/2008 & 11/05/2012 & 24/10/2012 & 24/01/2013 & 8/12/2013 & 10/06/2016 |  | Petroleum Services (2001) Limited 15 Manchester Pl, PO Box 20185, Hamilton, and 21 Midhurst St Palmerston North |  | Up to 110,000 L Design specification: AS1692 - 2006 Reference: TNK0501, 0826, 0827, 0842, 0843, 0844, 0845, 1001, 1017, 11006, 12023, 13044, 15003, 16019, 17001, 17002, 17009. | Class 3.1A, 3.1B, 3.1C, 3.1D hazardous substances |  |  | 2019-06-09 | Head office and fabrication workshop is in Hamilton. Second fabrication workshop in in Palmerston North. Fabricator of: TNKs 0501, 826, 827, 842, 843, 844, 845, 1001, 1017, 11006, 12023, 13044, 15003, 16019, 17001, 17002, 17009.
TNK0856 | 2008-12-12 | Impac Solutions, Fonterra Waitoa, Allen Street, Morrinsville |  | 6,230 litre Above Ground Tank | AS 1692 | 6.1D, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A, 9.1D | Impac Solutions Fonterra Waitoa Allen Street Morrinsville | Must be as per drawing MAS Design Drawing CC/APTERAPA/02 Sheets 1 & 2, Rev A, dated 11/6/97. | 2013-12-12 | Unsure of FAB
TNK0819 | 2009-01-23 |  | FAB0017 | Double Skin storage tank, 10,000L | Double Skin storage tank, 10,000L, to AS 1692-2006 | Diesel of Classification 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | WMC Engineering LTD | There must be no change to the original design parameters and / or drawing number 69-001-A001, Sheets 1-4 inc, Rev A |  | FAB0017 - expired
FAB0017 | 2009-01-23 |  | WMC Engineering Limited, 23 Waverly St, Waipawa | TNK0819 | Storage and transfer of diesel 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Diesel of Classification 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | WMC Engineering LTD | Subject to the implementation of the recommendations contained in Trasfield Worley Audit Findings dated 18 August 2008. | 2009-12-31 | Fabricator of: TNK0819
TNK0857 | 2009-02-03 |  | HSM Engineering Ltd | Fitzroy Project Services 12,000 litres Vertical Cylindrical Single Skin Steel above Ground Tank for Marine Diesel Fuel | AS 1692:2006 Category 5, API 650 App. J Location: HMNZ Naval Base, Devonport | 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fitzroy Project Services PO Box 58 096 Greenmount Auckland | Must be as per drawing FPS 139517-480 through 490 Rev.1 dated June 2008 (Tank No. 0507 NFI Project) | 2014-02-03 | FAB0005 - expired
FAB0033 | 2009-02-16 |  | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 | Design Standards: AS1692, BS EN14015, API650, API620 | Above ground carbon steel and stainless steel tanks Capacity: up to 150,000 litres Reference: TNK20000, TNK20001, TNK20003, TNK20081, TNK20085, TNK20105, , TNK20114, TNK20115, TNK20116, TNK20117, TNK20152, TNK20153, TNK20154, TNK20155, TNK20156, TNK20199, TNK20200, TNK20210, TNK20333, TNK20464, TNK20465, TNK20490 | Flammable Liquids, Oxidising Liquids, Toxic Liquids, Corrosive Liquids, Eco-Toxic Liquids |  | This approval applies to designs for which TNK numbers have been registered with ERMA/EPA/WorkSafe New Zealand. Allocation of individual tank serial numbers. Retention of individual tank QA records. | 2026-09-24 | Fabricator of: TNK20000, TNK20001, TNK20003, TNK20081, TNK20085, TNK20105, TNK20114, TNK20115, TNK20116, TNK20117, TNK20152, TNK20155, TNK20156, TNK20199, TNK20200, TNK20210, TNK20333, TNK20464, TNK20465, TNK20490
FAB0034 | 2009-02-16 |  | Contract Mechanical Services Ltd 11 Harvard Way PO Box 4442 Mount Maunganui 3149 | Above ground Carbon Steel & Stainless Steel Tanks | Design Standards: AP1650 & AS1692 Maximum Size: 150,000 litres | Flammable Liquids, Oxidising Liquids, Toxic Liquids, Corrosive Liquids, Eco-Toxic Liquids |  |  | 2012-02-15 | Fabricator of: Unknown
FAB0018 | 2009-02-24 |  | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161 FAB0018 | AS 1692-2006 | Approved for the shop fabrication of steel tanks in accordance with AS 1692-2006 for Classes 3.1A, B, C or D hazardous substances for which TNK numbers have been registered with ERMA / EPA / WorkSafe New Zealand. Reference: TNK0701, TNK0702, TNK0703, TNK0704, TNK0705, TNK0706, TNK0707, TNK0708, TNK0709, TNK0710, TNK0711, TNK0712, TNK0713, TNK0714, TNK0738, TNK0739, TNK1011, TNK1012, TNK11014, TNK11015, TNK11016, TNK11017, TNK11018, TNK12020, TNK12021, TNK18001, TNK18002, TNK19005, TNK19017, TNK20036, TNK20432 | Class 3.1A - 3.1D substances | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161 | Prior to 18/10/2019: Welding carried out to NZS 4711 standard, by AS2980: 2007 certified welders. All aboveground storage tanks certified to NZS4203:1992. Seismic and wind loading to NZS 1170.5 and NZS1170.2. As of 20/12/2019: No conditions As of 26/01/2023: Allocation of unique individual tank serial number to be stamped on each individual tank and recorded. Retention of individual tank fabrication, testing records and QA records for each tank. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2029-02-13 | Fabricator of: Prior to 18/10/2019 TNK No.: 0701 - 0714, 0738, 0739, 1011, 1012, 11014, 11015, 11016, 11017, 11018, 12020, 12021, 18001, 18002, 19005, 19017. TAN No.: 09005, 10045, 09004, 13065 As of 26/01/2023: TNK0701, TNK0702, TNK0703, TNK0704,TNK0705, TNK0706, TNK0707, TNK0708,TNK0709, TNK0710, TNK0711, TNK0712,TNK0713, TNK0714, TNK0738, TNK0739,TNK1011, TNK1012, TNK11014, TNK11015,TNK11016, TNK11017, TNK11018,TNK12020, TNK12021, TNK20036 As of 13/02/2026: TNK0701, TNK0702, TNK0703, TNK0704, TNK0705, TNK0706, TNK0707, TNK0708, TNK0709, TNK0710, TNK0711, TNK0712, TNK0713, TNK0714, TNK0738, TNK0739, TNK1011, TNK1012, TNK11014, TNK11015, TNK11016, TNK11017, TNK11018, TNK12020, TNK12021, TNK18001, TNK18002, TNK19005, TNK19017, TNK20036, TNK20432
FAB0019 | 2009-02-24 |  | Greentank Ltd 16 Donald Street Kaikorai Valley Dunedin | Greentank fire retardant double wall fiberglass above ground diesel tank | Design Code: ULC-ORD-C80.1-2000 above ground non metallic tank for oil burner fuel. ASTM D2563, HSNO COP17-1. LIMITED TO 250 - 1200L | Class 3.1D diesel fuel (automotive gas oil, marine diesel oil) low flashpoint diesel (low flash domestic heating oil and alpine diesel) |  | Invalid if pipelines or tank repaired, altered, or chage of service. Manufactures plate to be attached to each tank. Where required, installers must obtain location and stationary container certificates. Unless surrendered or revoked beforehand, this certificate shall remain in force until the expiry date stated below, at which time it may be renewed by an authorised Test Certifier. Certificate must be produced at the request of an Enforcement Officer appointed under the HSNO Act 1996. | 2012-02-19 | Fabricator of: TNK0001, TNK1015, TNK1016
FAB0020 | 2009-03-16 |  | Ross Irving Ltd 56 Lismore Street Phillipstown Christchurch | AS1692-2006 Manufactured in 2009 | Shop fabrication of steel tanks for Class 3 substances in accordance with AS 1692-2006 | Class 3 |  | Subject to the implementation of the recommendations contained in Trasfield Worley Audit Findings dated 6 March 2009. | 2009-08-31 | Unknown TNK numbers
TNK0820 | 2009-03-18 | Mercer Stainless Ltd Corbett Road Bell Block New Plymouth |  | AS 1692-2006 Category 5 5135L Manufactured 2009 | Tank ID: T-9512 5,135L For Methanol; Classes 3.1B, 6.1D, 6.4A, 6.8B, 6.9A, 9.3C | Methanol; Classes 3.1B, 6.1D, 6.4A, 6.8B, 6.9A, 9.3C |  | Invalid following any change to the original design parameters and/or Mercer Drawing Number 13695, Sheet A1, Rev B dated 17/2/09 |  | Unsure of FAB number
FAB0021 | 2009-03-23 |  | RX Plastics Limited Ashburton Branch Maronan Road Ashburton | RX Plastics - Rotationally Moulded Polyethaylene (PE) above ground stationary tank for chemicals | AS/NZS4766 HSNO COP 12-1 Limited to 250-25,000L Drawings: Transfield Worley: 608/5.1 to 5.4 Seismic Restraint SAI Global: COP/5001/1101/20001/32001/52501/75001/10kl/25kl 1-9 COP Tank Spec | Class 5,6,9 with no flammable or explosive classification (i.e. No Class 1-4 substances) | Steve Hollings, RX Plastics Ltd | Manufactureers plate to be attached to each tank. | 2012-03-19 | Approval is limited to tanks built to the drawings listed. Unable to locate TNK numbers
FAB0022 | 2009-03-23 |  | RX Plastics Limited Hamilton Branch SHW1 & Horotiu Road Hamilton | RX Plastics - Rotationally Moulded Polyethaylene (PE) above ground stationary tank for chemicals | AS/NZS4766 HSNO COP 12-1 Limited to 250-25,000L Drawings: Transfield Worley: 608/5.1 to 5.4 Seismic Restraint SAI Global: COP/5001/1101/20001/32001/52501/75001/10kl/25kl 1-9 COP Tank Spec | Class 5,6,9 with no flammable or explosive classification (i.e. No Class 1-4 substances) | Steve Hollings, RX Plastics Ltd | Manufactureers plate to be attached to each tank. | 2012-03-19 | Approval is limited to tanks built to the drawings listed. Unable to locate TNK numbers
FAB0023 | 2009-04-02 |  | NYMIC Engineering Ltd 9 Kilronan Place Wigram Christchurch | AS1692-2006 Categories 1 to 5 inclusive HSNOCOP 24-1 | Up to 150,000L. Reference: TNK 0801, 0802, 0803, 0804, 0805, 0822, 0830, 1004, 1005, 1006, 1007, 1009, 1018, 10035, 10036, 11001, 11008, 11009, 11010, 11011, 12011, 13004, 13038, 13039, 13040, 13056, 13075, 13076, 15005, 15006; 15019; 15020, 15021, 16008, 16011, 16013, 16022,17003, 17005, 17006, 17007, 17016, 18014, 18015, 18045, 18046, 18047, 18048, 18049, 18050, 19004, 19016, 20031, 20111, 20112, TNK20306 Prior to 16/07/2022 Fabricators of Tankwagons: TAN09054, TAN15023, TAN15056, TAN15057, TAN17080 | Class 3.1A, 3.1B, 3.1C and 3.1D flammable liquids. | NYMIC Engineering Ltd 9 Kilronan Place Wigram Christchurch | The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2025-12-07 | Approval is limited to tanks built to the drawings listed. Fabricator of: TNK 0801, 0802, 0803, 0804, 0805, 0822, 0830, 1004, 1005, 1006, 1007, 1009, 1018, 10035, 10036, 11001, 11008, 11009, 11010, 11011, 12011, 13004, 13038, 13039, 13040, 13056, 13075, 13076, 15005, 15006; 15019; 15020, 15021, 16008, 16011, 16013, 16022,17003, 17005, 17006, 17007, 17016, 18014, 18015, 18045, 18046, 18047, 18048, 18049, 18050, 19004, 19016, 20031, 20111, 20112, TNK20306 Prior to 16/07/2022 Fabricators of Tankwagons: TAN09054, TAN15023, TAN15056, TAN15057, TAN17080
TNK0858 | 2009-04-06 | Fitzroy Project Services PO Box 58 096 Greenmount Auckland |  | Fitzroy Project Services 55,000 litre Vertical Cylindrical Single Skin Steel Above-ground Tank for Oily Bilge Water (OBW) | AS 1692:2006 Category 5, API 650 APP. J HMNZ Naval Base, Devonport | Not classified | Services Engineers Ltd | FPS 139517-495 Rev.2 & 498 Rev. 2 dated July 2008 (Tank Nos. 1200, 1201 & 1202 NFI Project) | 2014-04-06 | Fabricated by Services Engineers - FAB0011 - expired
TNK0859 | 2009-04-06 | Fitzroy Project Services PO Box 58 096 Greenmount Auckland |  | Fitzroy Project Services 5,500 litre Vertical Cylindrical Single Skin Steel Above-ground Tank for Waste Oil & Sludge | AS 1692:2006 Category 5, API 650 APP. J HMNZ Naval Base, Devonport | Not classified | Services Engineers Ltd | FPS 139517-520 Rev.2, 521 Rev. 1, 522 Rev. 1, 523 Rev.2 & 524 Rev. 1 dated August 2008 (Tank Nos. 1203 & 1206 NFI Project) | 2014-04-06 | Fabricated by Services Engineers - FAB0011 - expired
TNK0860 | 2009-04-06 | Fitzroy Project Services PO Box 58 096 Greenmount Auckland |  | Fitzroy Project Services 1,500 litre Vertical Cylindrical Single Skin Steel Above Ground Tank for Wastewater & Treated Effluent | AS 1692:2006 Category 5, API 650 APP. J HMNZ Naval Base, Devonport | Not classified | Services Engineers Ltd | FPS 139517-510 Rev. 2, 511 Rev. 1, 512 Rev. 1, 513 Rev. 2 & 514 Rev. 1 dated August 2008 (Tank Nos. 1204 & 1205 NFI Project) | 2014-04-06 | Fabricated by Services Engineers - FAB0011 - expired
FAB0024 | 2009-05-04 |  | Scotts Engineering Co Ltd 510 Cranford Street Christchurch ph 03 352 9015 | Tanks for the storage and transfer of diesel or fuel oil supplying a boiler, to AS1692-2006 (or equivalent). Up to 150,000L | AS1692-2006 (or equivalent) Up to 150,000L | Diesel of Classification 3.1D, 6.1E, 6.3B, 6.7B, 9.1B, or Fuel Oil; used for the storage and transfer to a boiler |  | Approval is for the fabrication of tanks used for the storage and transfer of diesel or fuel oil supplying a boiler. Subject to the implementation of recommendations contained in Transfield Worley's Audit Report dated 4/05/2009. | 2009-11-04 | Unsure of any TNK numbers
TNK0822 | 2009-05-05 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | Elevated above ground farm tanks, for the storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Designed to AS1692 - 2006 Categories 4, 500 to 2000L In accordance with Drawings SHF-MG-0001; sheets 1-4 inclusive; Rev 1A; dated 03/09 and SHF-SG-0001; sheet 1 of 1; Rev 1A; dated 04/09. | Diesel classification 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Southern Heating Fuels Ltd 61 Hayton Road Sockburn Christchurch (03) 343 6478 | Certificate becomes invalid following any chage to the original design parameters and/or drawing numbers quoted |  | FAB0023
TNK0823 | 2009-05-07 | Mercer Stainless Ltd Corbett Road Bell Block New Plymouth |  | AS1692:2006, Cat 5 15,500 L manufacture year 2009 Tank ID: 14246 | Designed to AS1692:2006, Cat 5 size: 15,500 L Design is to be as per the conditions and details contained on Mercer Drawing No. 14246, sheet A2, Rev E, dated 10/07/09 | Blended Acid cleaner Reflux R400 of classification 6.1D, 6.9B, 8.1A, 8.2B, 8.3A, 9.3C |  | Design is to be as per the conditions and details contained on Mercer Drawing No. 14246, sheet A2, Rev E, dated 10/07/09, and is to contain Blended Acid cleaner Reflux R400 of classification 6.1D, 6.9B, 8.1A, 8.2B, 8.3A, 9.3C. |  | Test Certificate 253 Supersedes 243. TC 253 issued to reflect minor amendments to Mercer Drawing 14246. Unsure of FAB number
TNK0824 | 2009-05-08 | Mercer Stainless Ltd Corbett Road Bell Block New Plymouth |  | AS1692:2006, Cat 5 size: 21,040L manufacture year 2009 Tank ID: 14245 | Designed to AS1692:2006, Cat 5 size: 21,000 L Design is to be as per the conditions and details contained on Mercer Drawing No. 14245, sheet A2, Rev E, dated 10/07/09 | 60% Nitric Acid of Class 6.1D, 6.9B, 8.1A, 8.2B, 8.3A |  | Design is to be as per the conditions and details contained on Mercer Drawing No. 14245, sheet A2, Rev B, dated 01/05/09, and is to contain 60% Nitric Acid of Class 6.1D, 6.9B, 8.1A, 8.2B, 8.3A |  | Test Certificate 254 Supersedes 244. TC 254 issued to reflect minor amendments to Mercer Drawing 14245. Unsure of FAB number
FAB0035 | 2009-05-15 |  | Plastics Constructions Ltd 26 Fremlin Place Avondale Auckland |  | AS2634 and BS4994 Maximum Capacity: 20,000 litres |  |  |  | 2012-05-15 | Fabricator of: TNK0861, TNK 0878, TNK0879, TNK13020, TNK13034, TNK13034, TNK13036, TNK13042, TNK13047, TNK13048, TNK13049, TNK13054, TNK13055
TNK0861 | 2009-05-15 | Plastics Constructions Ltd 26 Fremlin Place Avondale Auckland |  | 10,000 L Single Skin Copolymer Polypropylene Vertical Cylindrical Above-ground Tank for Sodium Hydroxide | BS 4994 Affco Tanning Ltd, Wiri | 6.1D, 8.1A, 8.2B, 8.3A, 9.1D, 9.3C | Plastics Constructions Ltd | Drawing Reference: PCL MOI | 2014-05-15 | FAB0035 - expired
TNK0825 | 2009-05-18 | Scott Sheetmetal Co. Cnr Railway and Ontario Streets Gore (03) 208 5381 |  | AS 1692-2006, Cat 3 capacity 503 &944 L | Designed to AS1692:2006, Cat 3 size: 503 & 944 L As per drawing 659, Version 3 and approved internal QA procedures | Diesel having classification 3.1D, 6.1E, 6.3B, 6.7B, 9.1B |  | For the storage and transfer of Diesel. Approval subject to compliance with AS1692, approved tank drawing no. 659, v3, and approved internal QA procedures |  | FAB0025
FAB0025 | 2011-12-14 |  | Scott Sheetmetal Co. Cnr Railway and Ontario Streets Gore (03) 208 5381 | Tank Construction Code: AS 1692-2006 | Capacity: Up to 5,000 litres Reference: TNK0825 | Approved for: The shop fabrication of steel tanks for Class 3.1D hazardous substances for which TNK numbers have been registered with the EPA |  | Approval is for fabrication of TNK0825 (as per drawing number 659, sheet 1 of 1, v3) only | 2014-12-31 | Fabricator of: TNK0825 and TNK 12002
TNK0862 | 2009-06-05 | APD Ltd PO Box 12663 Auckland 1642 | APD Ltd PO Box 12663 Penrose, Auckland 1642 49 McLaughlins Road, Wiri, Auckland, 2104 FAB0032 | 2 x 1650 L Rectangular Thermoplastic Polypropylene Process Containers for Nitric Acid, Chromic Acid, Hydrofluoric Acid, Fluoroboric Acid and Sulphuric Acid in Aqueous Solutions | BS EN 12573 & EN 1778 Arkro Coatings Ltd, Auckland | 6.1C, 6.1E, 6.3A, 6.3B, 6.4A, 6.8B, 6.9B, 8.1A, 8.2C, 8.3A, 9.1D, 9.3B | APD Ltd | APD 8258/000/000 Rev. B dated 05/06/2009 | 2009-06-05 | FAB0032
TNK0826 | 2009-06-08 | Petroleum Services Ltd 2 Kaimiro Street Hamilton (07) 850 6440 | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS-1692:2006, Cat 4 capcity 33,500L | Designed to AS1692:2006, Cat 4 Capacity: 33,500 L | Diesel having classification 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petroleum Services Limited | Design & fabrication details contained in AS 1692 and approved PSL drawings listed under 'Tank Design' |  | FAB0083 (FAB0016 prior to 9/06/2019)
FAB0036 | 2009-06-09 |  | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland 1060 | Manufacture of fibre reinforced underground tanks for Flammable and Combustible Liquids to UL1316: 2018 | Capacity: 1,000 L – 110,000 L 3m ID tank design reference: TNK19029, TNK 19030, TNK19031, TNK 19032, TNK 19033, TNK 19034, TNK 19035, TNK 19036, TNK 19037, TNK 19038, TNK 19039, TNK 19040, TNK 19041 and TNK 19042. 2.5m ID tank design reference: TNK19043, TNK 19044, TNK 19045, TNK 19046, TNK 19047, TNK 19048, TNK 19049, TNK 19050, TNK 19051, TNK 19052, TNK 19053, TNK 19054 and TNK 19055. 2m ID tank designs: TNK 19056, TNK 19057, TNK 19058, TNK 19059 and TNK 19060. 1.2m ID tank designs: TNK 19061, TNK 19062, TNK 19063, TNK 19064 and TNK 19065. | Pre 14/08/2023 Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. As of 14/08/2023 Petrol / Diesel UN No. 1203 / 3082. Max sg 0.832. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland 1060 | Tanks are to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of these tank designs are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway. All tanks to be fitted with hydroguard monitoring systems. Design performance tests are accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Worksafe NZ registered tank design register TNK numbers are to be glassed in the manway risers. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the compliance certifier who issued the certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2026-08-14 | Fabricator of: TNK19029, TNK 19030, TNK19031, TNK 19032, TNK 19033, TNK 19034, TNK 19035, TNK 19036, TNK 19037, TNK 19038, TNK 19039, TNK 19040, TNK 19041, TNK 19042, TNK19043, TNK 19044, TNK 19045, TNK 19046, TNK 19047, TNK 19048, TNK 19049, TNK 19050, TNK 19051, TNK 19052, TNK 19053, TNK 19054, TNK 19055, TNK 19056, TNK 19057, TNK 19058, TNK 19059, TNK 19060, TNK 19061, TNK 19062, TNK 19063, TNK 19064, TNK 19065.
FAB0028 | 2009-07-23 |  | Etech NZ Ltd 130 Kaimanawa St Palmerston North ph 06 355 4550 | TNK20194, TNK20195, TNK20196, TNK20526, TNK20527, TNK20528, TNK20529 | See listing for 500L TNK0746 and 250L TNK0747 | Class 3, 6, and 8 hazardous liquids | ETECH NZ Ltd Palmerston North | Approved for the construction of steel tanks designed and constructed to to BS EN 12285:1 and AS 1692. Tanks are suitable for the storage of hazardous liquids with hazard classes of 3, 6, & 8. The following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the fabricator for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2029-02-18 | Fabricator of: TNK0746, TNK0747, TNK0831, TNK0832, TNK0833, TNK0834, TNK0835, TNK0836, TNK0837, TNK0838, TNK0839, TNK0840, TNK10033, TNK10034, TNK20194, TNK20195, TNK20196, TNK20526, TNK20527, TNK20528, TNK20529
TNK0863 | 2009-07-24 | Mercer Stainless Ltd Fonterra Dairy Factory State Highway 1 Edendale |  | 30,900 litres Above Ground Tank | AS1692, Specific Design | Nitric Acid, 0.5 - 10% aqueous solution 6.1E, 6.9B, 8.1A, 8.2C, 8.3A |  | This certificate becomes invalid following any change to the original design parameters and / or Mercer Stainless Ltd GA drawing number 14052, Rev C, Sheet A1. |  | Unsure of FAB number
TNK0864 | 2009-07-27 | ECL Design Services, Division of: Fuelquip (NZ) Limited PO Box 33-192 Petone Wellington |  | Double skin steel storage tank and dispenser unit. Ser No. 01F6NJ | Design Ref: Fuelquip 40,000 litre PUFF unit Capacity: 40,000 litres Design Spec: AS 1692:2006 Cat 4 (primary tank). Reg 60 Cl 3 DG Regs Material: 6mm mild steel plate primary. 5mm secondary unit | Class 3.1D flammable liquids | Fuelquip Services Ltd. | Dwg FTS21000A-FTS21048A (05/06/1998). Design Review - D.N. Undrill. Cert No. FQST090713. 13/07/2009 | 2014-07-27 | Unsure of FAB number
FAB0027 | 2012-07-21 |  | PK Engineering (Nelson) Ltd | TNK13062, 13086, 13087, 13088, 13089, 13090, 13091 | 40,000 L, 50,000 L, 60,000 L, 70,000 L, 80,000 L, 90,000 L, 100,000 L double wall single compartment aboveground diesel storage tanks. | Class 3.1D flammable liquids | PK Engineering (Nelson) Ltd | The following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the fabricator for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2018-02-19 | Fabricator no longer approved for fabrication of TNK0828. Fabricator of: TNK13062, 13086, 13087, 13088, 13089, 13090, 13091.
TNK0828 | 2009-07-29 | PK Engineering (Nelson) Ltd 46A Factory Road Brightwater |  | Steel AG tanks to AS 1692:2006 | Design Ref: PKE-2240-40. 40,000L PUFF unit Substances: Class 3.1D flammable liquids Capacity: 40,000L Double skin storage tank To AS 1692:2006 Cat 4 (primary tank). HSNOCOP 24-1 Material: 8mm mild steel plate 250mPa Grade 43 primary Drwg Ref No. Design review - PWE Engineering Ltd. Cert No. 5775-14282 | Class 3.1D |  |  | 2014-07-29 | FAB0027 based on Test Certificate SCS F 101
TNK0866 | 2009-08-20 | Mercer Stainless Limited PO Box 6020 Christchurch |  | Above ground Stainless Steel Stationary Container | Design Spec: AS 1692:2006 Cat 5 Material: 4mm Stainless Steel 304 Plate Capacity: 5,000 litres Manufacture Date: 20 August 2009 | Caustic Soda > 5% aqueous solution. Class - 6.1D, 8.1A, 8.2B, 8.3A, 9.1D | Mercer Stainless Ltd | DWG Ref No: Mercer Stainless Ltd DWG No 14452, Rev B (7/8/09) | 2014-08-20 | Unsure of FAB number
TNK0867 | 2009-08-20 | Mercer Stainless Limited PO Box 6020 Christchurch |  | Above ground Stainless Steel Stationary Container | Design Spec: AS 1692:2006 Cat 5 Material: 4mm Stainless Steel 316 Plate Capacity: 5,000 litres Manufacture Date: 20 August 2009 | Sulphuric Acid 98%; Class 6.1D; 6.7A; 6.9A; 8.1A; 8.2B; 8.3A; 9.1D | Mercer Stainless Ltd | DWG Ref No: Mercer Stainless Ltd DWG No 14447, Rev B (7/8/09) | 2014-08-20 | Unsure of FAB number
TNK0829 | 8/29/2009 & 4/4/2012 |  | Martin Engineering (Palmerston North) Ltd. | AS1692-2006, Category 4 HSNOCOP 24-1 (March 2008) multi hazard rated (2 hour) tanks to UL 2085 :1997 FAB0045 | 80,000L single compartment aboveground, Integral bunded diesel storage tank. | Class 3.1D | Martin Engineering (Palmerston North) Ltd. | See test certificate The vent is to terminate not less than 150mm above the top and is to be higher than the fill point of the tank. Filliing and discharge of the tanks is to be carried out under liquid and vapour tight connections. | 2015-04-04 | Subject to any updates to HSNOCOP 24-1. FAB0045
FAB0037 | 2009-09-14 |  | Transtak Engineering and Equipment 30 Hau Road Motueka 7120 Nelson | Fuel storage / trailer tanks to AS 1692 | Single wall steel / aluminium storage tanks Mild steel plate. Grade 5502 / 5083 aluminium plate AS 1692 Cat 1-4 (as applicable) 430 litre Home heating oil unit Tank trailer units up to 1,500 litres 2,000 – 20,000 litre A/G fuel storage tanks |  | Transtak Engineering and Equipment | Transtak Engineering and Equipment. CH 34-831. HSC 9901. HSC9915. HSC TW202 | 2012-09-14 | Fabricator of: TNK0868, TNK0869, TNK0870 and TNK0871
TNK0868 | 2009-09-14 | Transtak Engineering and Equipment 30 Hau Road Motueka 7120 Nelson |  | TKE Skid Tank. Above ground storage tank. HSC 9915 | AS 1692 (primary tank) 6mm mild steel end plates. 5mm mild steel shell Single skin steel storage tank (skid unit) Capacity 15,000 litres | Class 3.1D flammable liquids | Transtak Engineering and Equipment |  | 2014-09-14 | FAB0037 - expired
TNK0869 | 2009-09-14 | Transtak Engineering and Equipment 30 Hau Road Motueka 7120 Nelson |  | TKE Home Heating Oil Tank. HSC 9902 | AS 1692 Cat 1 (primary tank) 2.0mm mild steel. 3.0mm Grade 5052 aluminium (alternative). Single skin steel storage tank Capacity 430 litres | Class 3.1D flammable liquids | Transtak Engineering and Equipment |  | 2014-09-14 | FAB0037 - expired
TNK0870 | 2009-09-14 | Transtak Engineering and Equipment 30 Hau Road Motueka 7120 Nelson |  | TKE Tandem Trailer Unit. HSC 9901 | AS 1692 Cat 1 (primary tank) 25.0mm Grade 5052 aluminium (shell). 6.0mm Grade 5083 (ends) Single skin trailer tank unit Capacity 1,500 litres | Class 3.1D flammable liquids | Transtak Engineering and Equipment |  | 2014-09-14 | FAB0037 - expired
TNK0871 | 2009-09-14 | Transtak Engineering and Equipment 30 Hau Road Motueka 7120 Nelson |  | TKE Trailer refuel unit. (Dual compartment). TW202 | AS 1692 (primary tank) Mild Steel Plate Single skin trailer tank unit Capacity: 250 litres 3.1A, 1,100 litres 3.1D | Class 3.1A / 3.1D flammable liquids | Transtak Engineering and Equipment |  | 2014-09-14 | FAB0037 - expired
TNK0872 | 2009-09-15 | Alan Poulsen Engineering Ltd 10 Kitchener Street Dunedin | Prior to 24/09/2024 Alan Poulsen Engineering Ltd 10 Kitchener Street Dunedin FAB0009 As of 24/09/2024 PETROLEUM SOLUTIONS 2024 LIMITED 10 Kitchener Street, Dunedin Central, Dunedin, 9016 PO Box 238, Dunedin, Dunedin Central, Dunedin, 9054 FAB0099 | AS 1692: 2006, Category 3 Manufacture Year: 2009 | 7,400 L above ground tank | 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Alan Poulsen Engineering Ltd 10 Kitchener Street Dunedin PO Box 238 Dunedin 9054 | This certificate beomes invalid following any change to the original design parameters and / or drawing number APD-MV-001, Sheet 1 of 1, Rev 0, dated 09.09. |  | FAB0009 FAB0099
TNK0873 | 2009-09-22 | Advanced Fuel Tanks NZ Limited PO Box 41 029 Christchurch | Advanced Fuel Tanks NZ Limited 5 Tanya St, Bromley, Christchurch | Above ground Steel Stationary Container | AS 1692 6mm Carbon Steel Manufacture Date: 05/10/2009 | Flammable liquids - Diesel Additive Class 3.1B | Advanced Fuel Tanks N.Z Ltd | Chapman Oulsnam & Associates Dwg No 1226/7 issue A. Design Review PS4-O'Loughlin Taylor Spence Ltd 5/10/09. | 2014-09-22 | FAB0014
TNK0874 | 2009-09-22 | Advanced Fuel Tanks NZ Limited PO Box 41 029 Christchurch | Advanced Fuel Tanks NZ Limited 5 Tanya St, Bromley, Christchurch | Above ground Steel Stationary Container | AS 1692 6mm Carbon Steel Manufacture Date: 05/10/2009 | Flammable liquids - Diesel Additive Class 3.1B | Advanced Fuel Tanks N.Z Ltd | Chapman Oulsnam & Associates Dwg No 1226/7 issue A. Design Review PS4-O'Loughlin Taylor Spence Ltd 5/10/09. | 2014-09-22 | FAB0014
TNK0875 | 2009-09-22 | Advanced Fuel Tanks NZ Limited PO Box 41 029 Christchurch | Advanced Fuel Tanks NZ Limited 5 Tanya St, Bromley, Christchurch | Above ground Steel Stationary Container | AS 1692 6mm Carbon Steel Manufacture Date: 05/10/2009 | Flammable liquids - Diesel Additive Class 3.1B | Advanced Fuel Tanks N.Z Ltd | Chapman Oulsnam & Associates Dwg No 1226/7 issue A. Design Review PS4-O'Loughlin Taylor Spence Ltd 5/10/09. | 2014-09-22 | FAB0014
TNK0876 | 2009-09-22 | Advanced Fuel Tanks NZ Limited PO Box 41 029 Christchurch | Advanced Fuel Tanks NZ Limited 5 Tanya St, Bromley, Christchurch | Above ground Steel Stationary Container | AS 1692 6mm Carbon Steel Manufacture Date: 05/10/2009 | Flammable liquids - Diesel Additive Class 3.1B | Advanced Fuel Tanks N.Z Ltd | Chapman Oulsnam & Associates Dwg No 1226/7 issue A. Design Review PS4-O'Loughlin Taylor Spence Ltd 5/10/09. | 2014-09-22 | FAB0014
TNK0877 | 2009-10-05 | Direct Mechanical Services Ltd PO Box 97 494 South Auckland Mail Centre Manukau City |  | 250 litre - 1,200 litre Double Skin Steel Rectangular Diesel Above - ground Tanks | AS 1692 Cat. 3 Various Locations | 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Direct Mechanical Services Ltd | DMS FS 102 Rev.3 dated 24/9/2002 | 2014-10-05 | Unsure of FAB number
TNK0878 | 2009-10-05 | Plastics Constructions Ltd 26 Fremlin Place Avondale Auckland |  | 3,500 L Copolymer Polypropylene Horizontal Rectangular Storage Tank for Hydrochloric Acid | BS 4994 Chemwaste Industries, Auckland | 6.1B, 8.1A, 8.2B, 8.3A, 9.1D, 9.3C | Plastics Constructions Ltd | PCL 3004 | 2014-10-05 | FAB0035 - expired
TNK0879 | 2009-10-05 | Plastics Constructions Ltd 26 Fremlin Place Avondale Auckland |  | 8,400 L Copolymer Polypropylene Vertical Cylindrical Above-Ground Storage Tank for Sodium Hydroxide | BS 4994 Chemical Feed Solutions, Auckland | 6.1D, 8.1A, 82.B, 8.3A, 9.1D, 9.3C | Plastics Constructions Ltd | PCL 3003 | 2014-10-05 | FAB0035 - expired
TNK0830 | 2009-10-12 | NYMIC Engineering Ltd. |  | 2 compartments - 7000L each To AS 1692, Cat 4 FAB0023 | To AS1692, Cat 4 2 x 7000L Compartments Manufacture year 2009 For the storage and transfer of Premium Motor Spirit of Classification 3.1A, 6.1E, 6.3B, 6.7B, 9.1B Drawing E E 2809, Sheet 1 to 17 dated 03.04.2009 | Premium Motor Spirit - Class 3.1A, 6.1E, 6.3B, 6.7B, 9.1B |  | Approval becomes invalid following any changes to the origianl design parameters and/or drawing E E 2809, Sheet 1of 17 dated 03.04.2009 | Design removed 22/01/2014. No longer produced. | FAB0023
TNK0880 | 2009-11-02 | Armatec Environmental Ltd PO Box 3046 Fitzroy New Plymouth |  | 28,000 L Fi-glass Vertical Cylindrical Above-ground Tank for Waste Hydrochloric Acid | AS 2634 / BS4994 Perry Metal Protection, Lower Hutt | 6.1B, 8.1A, 8.2B, 8.3A, 9.1D, 9.3C | Armatec Environmental Ltd (Approved Fabricator No. FAB 0004) | Armatec Environmental Ltd E3334-04 Sheet 1-1 Rev. 1 | 2014-11-02 | FAB 0004 - Expired
TNK0881 | 2009-11-02 | Armatec Environmental Ltd PO Box 3046 Fitzroy New Plymouth |  | 5,000 L Fi-glass Vertical Cylindrical Above-ground Tank for Sodium Hypochlorite | AS 2634 / BS4994 Kapuni Water Treatment Plant, South Taranaki | 5.1.1B, 6.1E, 8.2C, 8.3A, 9.1A | Armatec Environmental Ltd (Approved Fabricator No. FAB 0004) | Armatec Environmental Ltd E3551-04 Sheet 1 Rev. 1 | 2014-11-02 | FAB 0004 - Expired
TNK0841 | 2009-11-13 | Matrixx Consultants Ltd 103 Wharf Street P O Box 886 Tauranga ph 07 577 9845 |  | AS 1692-2006, Category 4 | AS 1692-2006, Category 4 Capacity 10,700L Year 2009 Design parameters and or drawing number 1718-37--00, Rev B dated 5/11/09 | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B |  | Must be as per drawing number 1718-37-00, Rev B dated 5/11/09 |  | Unsure of FAB number
TNK0882 | 2009-11-25 | Advanced Fuel Tanks NZ Limited PO Box 41 029 Christchurch | Advanced Fuel Tanks NZ Limited 5 Tanya St, Bromley, Christchurch | Above ground single skin steel Stationary Container | AS 1692 6mm Carbon Steel Max Capacity: 20,000 litres Manufacture Date: October 2009 | Flammable liquids - Diesel Additive Class 3.1D | Advanced Fuel Tanks N.Z Ltd | Pipetech Dwg No A1-WT/N-125. Design Review PS4 - O'Loughlin Taylor Spence Ltd 11/11/09 | 2014-11-25 | FAB0014
TNK0831 | 2009-12-06 | ETECH NZ Ltd Palmerston North | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 3 | Working Vol 227 L single compartment. Aboveground marine specimen formalin fixing tanks T4 and T5. 595 mm wide x 500 mm high x 1396 mm long x 2 mm 316 L stainless steel shell thickness. Formaldehyde Class 3.1D, 8.2C, UN No 2209 | Formaldehyde Class 3.1D, 8.2C, UN No 2209 |  | Must be as per orignal drawings Drg. 2911 T45 M3 Rev. 2 | 2019-12-06 | FAB0028 - expired
TNK0832 | 2009-12-06 | ETECH NZ Ltd Palmerston North | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 3 | Working Vol 465 L single compartment. Aboveground marine specimen formalin fixing tanks T2 and T3. 600 mm wide x 500 mm high x 1994 mm long x 2 mm 316 L stainless steel shell thickness. Formaldehyde Class 3.1D, 8.2C, UN No 2209 | Formaldehyde Class 3.1D, 8.2C, UN No 2209 |  | Must be as per orignal drawings Drg. 2713 T2/ M2 Rev. C | 2019-12-06 | FAB0028 expired
TNK0833 | 2009-12-06 | ETECH NZ Ltd Palmerston North | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 3 | Working Vol 226 L single compartment. Aboveground marine specimen formalin fixing tanks T1. 591 mm wide x 500 mm high x 1000 mm long x 2 mm 316 L stainless steel shell thickness. Formaldehyde Class 3.1D, 8.2C, UN No 2209 | Formaldehyde Class 3.1D, 8.2C, UN No 2209 |  | Must be as per orignal drawings Drg. 2817 T1/ M1 Rev. 2 | 2019-12-06 | FAB0028 - expired
TNK0834 | 2009-12-06 | ETECH NZ Ltd Palmerston North | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 3 | Working Vol 196 L single compartment. Aboveground marine specimen formalin room stepping tanks T1, T2, T3 and T4. 840 mm wide x 450 mm high x 1196 mm long x 2 mm 316 L stainless steel shell thickness. Isoproponol Class 3.1B UN No 1219 | Isoproponol Class 3.1B UN No 1219 |  | Must be as per orignal drawings Drg. 2911 ST1 M1 Rev. 5 | 2019-12-06 | FAB0028 - expired
TNK0835 | 2009-12-06 | ETECH NZ Ltd Palmerston North | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 3 | Working Vol 2230 L single compartment. Aboveground marine specimen tank 48B. 1822 mm wide x 600 mm high x 3652 mm long x 4 mm 304 L stainless steel shell thickness. Isoproponol Class 3.1B UN No 1219 | Isoproponol Class 3.1B UN No 1219 |  | Must be as per orignal drawings Drg. 2911 48B M1 Rev.2 | 2019-12-06 | FAB0028 - expired
TNK0836 | 2009-12-06 | ETECH NZ Ltd Palmerston North | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 3 | Working Vol 1056 L single compartment. Aboveground marine specimen tank M04. 1000 mm wide x 500 mm high x 4000 mm long x 4 mm T304 stainless steel shell thickness. Isoproponol Class 3.1B UN No 1219 | Isoproponol Class 3.1B UN No 1219 |  | Must be as per orignal drawings Drg. 2911 M04/1 Rev.2 | 2019-12-06 | FAB0028 - expired
TNK0837 | 2009-12-06 | ETECH NZ Ltd Palmerston North | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 3 | Working Vol 505 L single compartment. Aboveground marine specimen tank T7. 1095 mm wide x 450 mm high x 1995 mm long x 2.5 mm 316 L stainless steel shell thickness. Isoproponol Class 3.1B UN No 1219 and Formaldehyde Class 3.1D, 8.2C, UN2209 | Isoproponol Class 3.1B UN No 1219 and Formaldehyde Class 3.1 D, 8.2C, UN No 2209 |  | Must be as per orignal drawings Drg. 2911 T7/M1 Rev.B | 2019-12-06 | FAB0028 - expired
TNK0838 | 2009-12-06 | ETECH NZ Ltd Palmerston North | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 3 | Working Vol 554 L single compartment. Aboveground marine specimen tank M9 and M10. 800 mm wide x 600 mm high x 2100 mm long x 2.5 mm 304 L stainless steel shell thickness. Isoproponol Class 3.1B UN No 1219 | Isoproponol Class 3.1B UN No 1219 |  | Must be as per orignal drawings Drg. 2911 M9/1 Rev.4 | 2019-12-06 | FAB0028 - expired
TNK0839 | 2009-12-06 | ETECH NZ Ltd Palmerston North | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 3 | Working Vol 666 L single compartment. Aboveground marine specimen tank MM1 and MM2. 1000 mm wide x 600 mm high x 2040 mm long x 2.5 mm 304 L stainless steel shell thickness. Isoproponol Class 3.1B UN No 1219 | Isoproponol Class 3.1B UN No 1219 |  | Must be as per orignal drawings Drg. 2911 MM1/1 Rev.2 | 2019-12-06 | FAB0028 - expired
TNK0840 | 2009-12-06 | ETECH NZ Ltd Palmerston North | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 3 | Working Vol 1115 L single compartment. Aboveground marine specimen tanks 48A and 48C. 1830 mm wide x 541 mm high x 1830 mm long x 2.5 mm 304 L stainless steel shell thickness. Isoproponol Class 3.1B UN No 1219 | Isoproponol Class 3.1B UN No 1219 |  | Must be as per orignal drawings Drg. 2911 48A/1 Rev.2 | 2019-12-06 | FAB0028 - expired
TNK0842 | 2009-12-08 | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692-2006, Category 4 As of 1 August 2019: AS1692 – 2006, Category 4 & Reduced Secondary Containment Safe Work Instrument 2017 (Impact Protected) | 50,000 L skid tank Year: 2009 Serial no: 24765 | Jet A-1 Aviation Turbine Fuel having a hazard classification of 3.1C, 6.1E, 6.3B, 9.1B | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Amended on 1 August 2019 as per compliance certificate 191547 | 2029-07-31 | FAB0083 (FAB0016 prior to 9/06/2019)
FAB0030 | 2009-12-12 |  | All Purpose Engineering Ltd 129 Crinan St Invercargill | TNK0847 | See listing TNK0847 | Class 3.1D |  | Please see test certificate for full set of conditions. Approval is for fabrication of TNK0847 (as per drawing KM-Mechanical Dwg No 1237-01) | 2012-12-12 | Fabricator of: TNK0847
TNK0847 | 2009-12-12 | All Purpose Engineering Ltd 129 Crinan St Invercargill | FAB00030 | 500L, 1000L, 2000L above ground steel stationary containers | AS1692:2006. AS1554 series, AS/NZS1170 500L, 1000L, 2000L above ground steel stationary containers; 3 mm mild steel | Class 3.1D |  | As per drawing KM-Mechanical Dwg No 1237-01 Design Review: Kenington Consulting PS2 - 2/11/2009 Please see test certificate for full set of conditions. | 2012-12-12 | FAB0030
TNK0843 | 2009-12-14 | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692-2006, Category 4 As of 1 August 2019: AS1692 – 2006, Category 4 & Reduced Secondary Containment Safe Work Instrument 2017 (Impact Protected) | 26,000 L to 67,000 L double skin above ground tanks 2800 mm outside diameter Year: 2009 | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Amended on 1 August 2019 as per compliance certificate 191547 | 2029-07-31 | FAB0083 (FAB0016 prior to 9/06/2019)
TNK0883 | 2009-12-14 | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692-2006, Category 4 | 4,510,000 to 20,000 litres above ground tank design | 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petroleum Services (2001) Ltd |  | N/A | FAB0083 (FAB0016 prior to 9/06/2019)
TNK1001 | 2010-01-19 | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692-2006, Category 4 | 10,000 L Underground stationary diesel storage tank | The Storage and Transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petroleum Services (2001) Ltd | Must be as per drawing numbers 10kL DS UP V2a.dwg, Rev A dated 29/09/09, Sheets 1 to 10 incl. |  | FAB0083 (FAB0016 prior to 9/06/2019)
TNK0844 | 2010-01-29 | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692-2006, Category 4 As of 1 August 2019: AS1692 – 2006, Category 4 & Reduced Secondary Containment Safe Work Instrument 2017 (Impact Protected) | 10,000 L to 60,000 L double skin above ground tanks 2400 mm outside diameter | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petroleum Services (2001) Ltd | Amended on 1 August 2019 as per compliance certificate 191547 | 2029-07-31 | FAB0083 (FAB0016 prior to 9/06/2019)
TNK0845 | 2009-12-15 | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | 4,500 to 20,000L double skin above ground tanks | AS 1692-2006, Category 4 1900mm outside diameter Capacity 4,500 to 20,000 L Year 2009 | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petroleum Services Limited | Must be as per drawing number 1900mmBuild DS Ped SP MW V2, Rev A. sheets 1-7 dated 03/12/2009 |  | FAB0083 (FAB0016 prior to 9/06/2019)
FAB0015 | 1 April 2005/ 29 August 2008 |  | Martin Engineering (Palmerston North) Ltd. | Steel aboveground double wall class 3 flammable liquid storage tanks | Up to 55,000L | Class 3 flammable liquids | Martin Engineering (Palmerston North) Ltd. | Please see approval | 2011-04-01 | Extension of previously issued Fabricator approval (in 2005)
TNK1002 | 2010-03-16 | Mercer Stainless Ltd Corbett Road Bell Block New Plymouth |  | 76,000 L, to API650, 11th Ed, Add 1, App J, M & S | Tank ID: D5-FA-701 API650, 11th Ed, Add 1, App J, M & S Manufacture year: 2010 Drawing no: Mercer14563 to 14607 | Urea, >26% in water, Class 6.1D, 6.3B, 6.4A, 9.3C |  | Approval is invalid if any change to Mercer design calulations D5-FA-701 and/ drawing numbers 14563 to 14607 inclusive |  | Unsure of FAB number
TNK1003 | 2010-03-16 | Mercer Stainless Ltd Corbett Road Bell Block New Plymouth |  | 76,000 L, to API650, 11th Ed, Add 1, App J, M & S | Tank ID: D5-FA-702 API650, 11th Ed, Add 1, App J, M & S Manufacture year: 2010 Drawing no: Mercer 14564 to 14607 | Urea, >26% in water, Class 6.1D, 6.3B, 6.4A, 9.3C |  | Approval is invalid if any change to Mercer design calulations D5-FA-702 and/ drawing numbers 14564 to 14607 inclusive |  | Unsure of FAB number
TNK1004 | 2010-03-17 | NYMIC Engineering Ltd. |  | 5,359 L, Double skin tank To AS1692-2006, Cat 4 FAB0023 | TANK ID: serial no. Construction code: AS 1692-2006, Cat 4 Drawing No: 1001019-00, Sheets 1-3 incl, Rev A dated 15/2/10 Manufacture year: Nameplate | Storage and tranfer of Diesel, Class 3.1D, 6.1E, 6.3B, 6.7B, 9.1B |  | Approval is invalid if any change to drawing numbers 1001019-00, Sheet 1-3 Inclu, Rev A, Dated 15/2/10. |  | FAB0023
TNK1005 | 2010-03-23 | NYMIC Engineering Ltd. |  | 2000 L, To AS 1692 FAB0023 | TANK ID: serial no. Construction code: AS 1692 Drawing No: 1002007-00, Sheets 1-3 incl, Rev A dated 23/2/10 Manufacture year: Nameplate | Storage and tranfer of Diesel, Class 3.1D, 6.1E, 6.3B, 6.7B, 9.1B |  | Approval is invalid if any change to drawing numbers 1002007-00, Sheet 1-3 Inclu, Rev A, Dated 23/2/10. |  | FAB0023
TNK1006 | 2010-03-23 | NYMIC Engineering Ltd. |  | 500 L To AS 1692 FAB0023 | TANK ID: serial no. Construction code: AS 1692 Drawing No: 1002007-00, Sheets 1-3 incl, Rev A dated 23/2/10 Manufacture year: Nameplate | Storage and tranfer of Diesel, Class 3.1D, 6.1E, 6.3B, 6.7B, 9.1B |  | Approval is invalid if any change to drawing numbers 1002007-00, Sheet 1-3 Inclu, Rev A, Dated 23/2/10. |  | FAB0023
TNK1007 | 2010-03-23 | NYMIC Engineering Ltd. |  | 1000 L To AS 1692 FAB0023 | TANK ID: serial no. Construction code: AS 1692 Drawing No: 1002007-00, Sheets 1-3 incl, Rev A dated 23/2/10 Manufacture year: Nameplate | Storage and tranfer of Diesel, Class 3.1D, 6.1E, 6.3B, 6.7B, 9.1B |  | Approval is invalid if any change to drawing numbers 1002007-00, Sheet 1-3 Inclu, Rev A, Dated 23/2/10. |  | FAB0023
TNK1009 | 2010-04-06 | NYMIC Engineering Ltd. |  | 10,000L AS 1692, Cat 4 FAB0023 | TANK ID: serial no. Construction code: AS 1692 Cat 4 Drawing No: 1002002-00, Sheets 1-3 incl, Rev A dated 11/03/10 Manufacture year: Nameplate | Storage and tranfer of Automotive or low flash point Diesel, having a classification of 3.1D, 3.1C |  | Approval is invalid if any change to drawing numbers 1002002-00, Sheet 1-3 Inclu, Rev A, Dated 11/03/10. |  | FAB0023
FAB0038 | 2010-04-12 |  | WMC Engineering Limited, 23 Waverly St, Waipawa | TNK1010 | TNK1010 | The Storage and Transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B |  |  |  | Fabricator of: TNK1010
TNK1010 | 2010-04-12 | WMC Engineering Ltd 23 Waverly Street Waipawa | FAB0038 | 4400L AS1692-2006 | Tank Construction Code: AS 1692-2006, Category 3 Capacity: 4,400L Manufacture Year: Nameplate | The Storage and Transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B |  | This certificate bcomes invalid follwing any changes to the original design parameters and/or drawing numbers WMC-250, Shts 1-5, Rev A, dated 17/03/10 and WMC-200, Shts 1-5, Rev A, Dated 10/02/10 |  | FAB0038 - expired
TNK1011 | 2010-03-26 | Mainline Sheetmetals Ltd., Hamilton | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161 FAB0018 | FAB0018 Design specification: AS1692 -2006, Category 4 | 10,000 L single compartment aboveground double wall diesel storage tank. 3600 mm long, 1.84m diameter, 6 mm Gr250 mild steel shell and secondary containment. | Class 3.1D flammable liquids | Mainline Sheetmetals Ltd Hamilton | 1. TNK1011 must be marked on nameplate in addition to the Manufacturers serial number, date of manufacture/ pressure test, AS1692-2006 Class 4, test pressure in Kpa. All other markings to comply with HSNO Regulations. 2. The vent is to terminate not less than 150mm above the tank top and is to be higher than the fill point of the tank. 3. Filing and discharge of the tanks is to be carried out under liquid and vapour tight connections. 4. This design approval is valid for a period of 5 years from teh date listed above. This designverification certificate may be withdrawn at any stage should the tanks fail in service or develop faults. Must be as per drawing number Drg. 01 Issue C. | 2031-03-10 | FAB0018
TNK1012 | 2010-03-26 | Mainline Sheetmetals Ltd., Hamilton | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161 FAB0018 | AS1692-2006, Category 4 | Description: 4,800 litres double skin above ground cylindrical horizontal stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Mainline Sheetmetals Limited - Cam Besley Capacity: 4,879 Litres Compartments: 1 Maximum Safe Fill Level: 4,724 Litres Diameter 1.84 m x 1.8 m long x 5 mm Gr250 mild steel shell end and secondary containment. | Name: Diesel Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161 | Approved For: The storage and transfer of diesel only, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved for supplying an engine or burner. References: Compliant with AS 1692:2006, Category 4. 4,800 litres double skin above ground cylindrical horizontal stationary tank achieves 110% secondary containment. Design Statement: 25-095, Issued by: Stiles and Hooker Ltd, Issued to: Mainline Sheetmetals Ltd, In Respect of: 4800L Double Skin Boiler Tank. Tankdesign to AS1692, seismic and wind loading to AS/NZS1170, structure to AS/NZS3404. Signed by Roger Baker (CMEngNZ), dated 30/06/2025. Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced Mainline Sheetmetals Limited drawings or applicable standard/s. |  | FAB0018
TNK1013 | 2010-05-07 | PK Engineering (Nelson) Ltd 46A Factory Road Brightwater | FAB0039 |  | Design Ref: NPD PUFF /Transportable Sled 4900 L Substance: Class 3.1D (Diesel Fule Oil) Flammable Liquids only Capacity: Range within 2000L - 5000L Facility: Sledge mounted double skin steel storage tank. Configured as a road transportable unit - UN Model Regs & LTSA Reqs Design Spec: AS 1692: 2006 Cat 4 (primary tank). UN MOdel Regs Pt 6.7 Material: 6mm mild steel plate 250 mPa. Per 6.6.2.4.1 UN Model Regs. Designer: PK Engineering (Nelson) Ltd Dwg Ref No: Design Review - PWE Engineering Ltd. Cert No. 5775 - 14946 PDE 4.9 2850 A0000 |  |  | This certificate becomes invalid following any changes to the original design parameters and/or drawing numbers: Design Review - PWE Engineering Ltd. Cert No. 5775 - 14946 PDE 4.9 2850 A0000 | 2013-05-06 | FAB0039 - expired
FAB0039 | 2010-05-07 |  | PK Engineering (Nelson) Ltd 46A Factory Road Brightwater | NPD PUFF transportable Stel AG tanks to AS 1692:2006 | Type: NPD PUFF transportable Steel AG tanks to AS 1692:2006 Design: PKE 4.9 2850 A0000 Substances: Class 3.1D Flammable liquids. (Diesel Fuel Oil) Capacity: 2000-5000L Max Tank Details: Double wall steel sled storage tanks. Transportable units. Design Spec: AS 1692: 2006 Cat 4 (primary tank). UN Model Regs CH6.7 Design Cert: PK Engineering (Nelson) Ltd. SCS D 14 Design Review: PWE Engineering Ltd | Substances: Class 3.1D Flammable liquids. (Diesel Fuel Oil) |  |  | 2013-05-06 | Fabricator of: TNK1013 FAB0039 replaced by FAB0027
TNK1014 | 2010-05-27 | Gilkison & Engineering Maintenance 2004 Ltd 77 Bond St Invercargill 9840 |  | Above ground steel stationary containers | Fabricator: FAB0040 Design Spec AS1692:2006, AS/NZS 1170 DWG Ref: KM-Mecanical Dwg No 1331-01 RA 1000L c/w pump cat 1 1331-210&11 RA 2000L cw/pump cat2 1331-20&21 RA 2x1000L dual compartment cw/pump cat 2 1331-30&31 RA 2000L cat 2 1331-40 RB 1000L cat 2 1331-50 RB 500L cat 2 Design review: Kenington consulting PS2 - 13/4/10 Material: Mild Steel (Plate thickness as per AS1692) Capacity: 500L, 1000L dual compartment & 2000L | Subs: Class 3.1A & D, petrol/Diesel |  |  |  | FAB0040
FAB0040 | 2010-05-27 |  | Gilkison & Engineering Maintenance (2004) Ltd 77 Bond Street, West Invercargill, 9810 | Tank Construction Code: AS 1692 - 2006, Category 4 | Capacity: Up to 50,000 L Reference: TNK1014 & TNK12025 | Hazardous liquids Class 3.1A, B, C & D up to 50,000 L capacity. |  | Fabrication and testing compliance with AS 1692-2006, approved for construction drawings & approved internal QA procedures. Applies only to designs for which approved TNK numbers have been registered with ERMA / EPA / WorkSafe.Allocation of unique serial numbers.Retention of individual QA records. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the compliance certifier who issued the compliance certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2023-08-25 | Fabricator of: TNK1014, TNK12025
TNK1015 | 2010-06-11 | Greentank Ltd PO Box 2152 South Dunedin 9044 | FAB0001 | Underground Xerxes 8 ft Dia - dual compartment, Double wall fibreglass stationary container | Type: Underground Xerxes 8 ft Dia - dual compartment, Double wall fibreglass stationary container Manufacturer: FAB0001 Design Spec: UL 1316 & ASTM D4021 Dwg Ref: Greentank PWM DWG NO 8ft Dia D.W.T 10,000/25,000L - Sept 09 Design review: Xerxes Corporation Material: Fibreglass Capacity: 10,000-25,000L | Subs: Flammable liquids - Class 3.1A, C & D | Greentank Ltd |  |  | FAB0001/FAB0019 - expired
TNK1016 | 2010-06-11 | Greentank Ltd PO Box 2152 South Dunedin 9044 | FAB0001 | Underground Xerxes 4 ft Dia - Double wall fibreglass stationary container | Type: Underground Xerxes 4 ft Dia - Double wall fibreglass stationary container Manufacturer: FAB0001 Design Spec: UL 1316 & ASTM D4021 Dwg Ref: Greentank PWM DWG NO 4ft Dia D.W.T - Sept 09 Design review: Xerxes Corporation Material: Fibre glass Capacity: 1500L | Subs: Flammable liquids - Class 3.1D diesel fuel | Greentank Ltd |  |  | FAB0001/FAB0019 - expired
TNK1017 | 2010-07-30 | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692-2006, Category 4 | 2434 L, 2819 L, 5175 L double skin diesel fuel tank. | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petroleum Services (2001) Ltd | Approval is invalid following any changes to design parameters and or drawing numbers 1450mm DS Feet V2a, Rev A, Sheets 1-7 incl. | N/A | FAB0083 (FAB0016 prior to 9/06/2019)
TNK1018 | 2010-07-09 | NYMIC Engineering Ltd. |  | 5250L Double skin Diesel fuel tank FAB0023 | AS1692, Cat 4 Capacity 5250L, Drgs 1006021-00, sheets 1-3 incl. Rev A dated 23.06.2010 | Automotive or low flash point diesel having a hazard classification of 3.1 D or 3.1C | NYMC Engineering | Approval is invalid following any changes to design parameters and or Drgs 1006021-00, sheets 1-3 incl. Rev A dated 23.06.2010 |  | FAB0023
TNK1019 | 2010-07-12 | REL Engineering 130 Collins Road Hamilton | RES (2013) LIMITED FAB0043 | AS1692, Cat 4 | Capacity 10,000 L Tank ID: REL704 10000L horizontal above ground tank | Automotive Engine Lubricating Oil Class 9.1D | REL Engineering | Approval is invalid following any changes to design parameters and or drgs 1006-0YY-01S & 02S dated 14/06/2010 |  | FAB0043
TNK1020 | 2010-07-12 | REL Engineering 130 Collins Road Hamilton | RES (2013) LIMITED FAB0043 | AS1692, Cat 4 | Capacity 30,000 L Tank ID: REL704A 30000L horizontal above ground tank | Automotive Engine Lubricating Oil Class 9.1D | REL Engineering | Approval is invalid following any changes to design parameters and or Drgs 1006-0XX-01S & 02S dated 12 & 13/06/2010 |  | FAB0043
TNK1021 | 2010-09-03 |  | Martin Engineering (Palmerston North) Ltd. | 1000 litre Steel AS1692 - 2006 Cat. 3 tank FAB0045 | aboveground single skin diesel storage tank, 1.5 m long x 1.2 m high x 3mm. Gr250 mild steel shell and ends | 3.1D | Martin Engineering (Palmerston North) Ltd. | See test certertificate for full conditions. The vent is to terminate not less than 150mm above the top. Filliing and discharge of the tanks is to be carried out under liquid ad vapour tight connections. | 2015-09-03 | FAB0045
TNK1022 | 2010-09-28 |  | Martin Engineering (Palmerston North) Ltd. | AS1692: 1989 Cat.4 tank HSNOCOP 24-1 (March 2008) multi hazard rated (2 hour) tanks to UL 2085 :1997 FAB0045 | 7,500 litre double wall steel aboveground fuel storage tanks. Shell 6mm Pl. Inner and outer. I.D. 1900mm. O.D.1922mm. Material Low carbon steel. Welding NZS 4711, LOA Inner 2850mm. LOA Outer 3000mm. | Tanks - suitable for storage of: Petrolium (unleaded) UN No. 1203 Class 3.1A Aviation gasoline Avgas 100 and Avgas 100LL Diesel fuel automotive and marine diesel fuel Class 3.1D and 3.1C Kerosene including Jet A-1, aviation turbine fuels Class 3.1C | Martin Engineering (Palmerston North) Ltd. | See test certificate for full conditions. Filliing and discharge of the tanks is to be carried out under liquid and vapour tight connections. | 2015-04-04 | Subject to any updates to HSNOCOP 24-1. FAB0045
FAB0041 | 2010-09-28 |  | Amtec Engineering Ltd, New Plymouth | IBC Construction Code: UN Model Regs Tank Code 31A | Capacity: Up to 1,500 litres | Classes 3.1A to 3.1D hazardous substances | Amtec Engineering Ltd, New Plymouth | Fabrication, inspection, testing and labelling in accordance with the UN Model Regulations. Retention of individual QA records. Serial fabrication by Amtec Engineering Ltd under their approved fabricator number FAB0041. | 2020-01-14
FAB0042 | 2010-09-28 | Amtec Engineering Ltd, New Plymouth |  | AS 1692-2006, Category 3 | Capicity 500-5,000 litres | Approved for: The shop fabrication of steel tanks for Class 3 hazardous substances in accordance with AS 1692-2006 | Amtec Engineering Ltd, New Plymouth |  | 2013-09-27 | Unsure of any TNK numbers
TNK10023 | 2010-10-07 | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 |  | AS 1692-2006, Category 3 | Capacity 5,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 |  | N/A | Fabricated by Western Global UK (FAB0053)
TNK10024 | 2010-11-01 | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 | Przedsiebiorstwo Wielobranzowe, SKALA sp.j. | AS 1962-2006, Category 3 | Capacity 5,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 |  | N/A | FAB0053/FAB0064
FAB0043 | 2010-11-10 |  | RES (2013) Ltd formally Rukuhia Engineering Ltd | AS 1692-2006 | Steel tanks up to 60,000 litres | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Pre - 8 November 2023 RES (2013) Ltd 8-10 Chesterfield St, Greymouth As of 8 Novermber 2023 RES (2013) Ltd 40 Ellis Street, Frankton, Hamilton, 3204 | As of 8 November 2023 WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the compliance certifier who issued the compliance certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2025-08-22 | Fabricator of: TNK12012 IS ASSIGNED TO FAB0043 (dated 30-05-2012). TNK 11002, 11003, 11011, 11019, 11023, 11025, 11026, 11032, 13005 TNK1019, 1020, 11002, 11011, 11019, 11023, 11025, 11026, 11032, 12012, 13005.
TNK10025 | 2010-11-05 | Nelson Reliance Engineering Co. (2008) Ltd PO Box 5005 Port Nelson |  | AS 1692-2006, Category 3 | Capacity 1,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Nelson Reliance Engineering Co. (2008) Ltd PO Box 5005 Port Nelson |  | N/A | Unsure of Fabricator
TNK10026 | 2010-11-05 | Nelson Reliance Engineering Co. (2008) Ltd PO Box 5005 Port Nelson |  | AS 1692-2006, Category 3 | Capacity 1,000 litres | Approved for: The storage and transfer of petrol having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Nelson Reliance Engineering Co. (2008) Ltd PO Box 5005 Port Nelson |  | N/A | Unsure of Fabricator
TNK10027 | 2010-11-05 | Nelson Reliance Engineering Co. (2008) Ltd PO Box 5005 Port Nelson |  | AS 1692-2006, Category 3 | Capacity 2,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Nelson Reliance Engineering Co. (2008) Ltd PO Box 5005 Port Nelson |  | N/A | Unsure of Fabricator
TNK10028 | 2010-11-05 | Nelson Reliance Engineering Co. (2008) Ltd PO Box 5005 Port Nelson |  | AS 1692-2006, Category 3 | Capacity 5,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Nelson Reliance Engineering Co. (2008) Ltd PO Box 5005 Port Nelson |  | N/A | Unsure of Fabricator
TNK10029 | 2010-11-05 | Nelson Reliance Engineering Co. (2008) Ltd PO Box 5005 Port Nelson |  | AS 1692-2006, Category 3 | Capacity 10,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Nelson Reliance Engineering Co. (2008) Ltd PO Box 5005 Port Nelson |  | N/A | Unsure of Fabricator
TNK10030 | 2010-11-05 | Nelson Reliance Engineering Co. (2008) Ltd PO Box 5005 Port Nelson |  | AS 1692-2006, Category 3 | Capacity 2,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Nelson Reliance Engineering Co. (2008) Ltd PO Box 5005 Port Nelson |  | N/A | Unsure of Fabricator
TNK10031 | 2010-11-10 | The New Zealand Refining Company Limited Crude & Product Jetties NZRC Whangarei |  | AS 1692-2006, Cat 4 | Capacity 5,580 litres | Approved for: The storage and transfer of flammable liquids having hazard classifications of 3.1A, 3.1B, 3.1C, 3.1D, 6.1E, 6.3B, 6.7B, 6.8B, 9.1B, 9.1C Tank ID: D3704 | The New Zealand Refining Company Limited Crude & Product Jetties NZRC Whangarei |  | N/A | Unsure of Fabricator
TNK10032 | 2010-11-10 | The New Zealand Refining Company Limited Crude & Product Jetties NZRC Whangarei |  | AS 1692-2006, Cat 4 | Capacity 5,580 litres | Approved for: The storage and transfer of flammable liquids having hazard classifications of 3.1A, 3.1B, 3.1C, 3.1D, 6.1E, 6.3B, 6.7B, 6.8B, 9.1B, 9.1C Tank ID: D3705 | The New Zealand Refining Company Limited Crude & Product Jetties NZRC Whangarei |  | N/A | Unsure of Fabricator
TNK10033 | 2010-11-10 | ETECH NZ Ltd Palmerston North |  | AS 1692-2006, Category 3 | Working volume 200 litres single compartment aboveground marine specimen tank. 657.6mm wide x 450mm high x 1219mm long x 1.2mm T304 stainless steel shell thickness | The single compartment marine storage tanks are approved for the storage of flammable liquids - 70/30 Ethanol/Water or 50/50 Isopropyl alcohol/water. Safe fill height 430mm | ETECH NZ Ltd Palmerston North |  | 2015-11-05 | FAB0028 - expired
TNK10034 | 2010-11-10 | ETECH NZ Ltd Palmerston North |  | AS 1692-2006, Category 3 | Working volume 500 litres single compartment aboveground marine specimen tanks. 657.6mm wide x 450mm high x 2050mm long x 1.2mm 2B 304 stainless steel shell thickness. 70/30 Ethanol/water or 50/50 Isopropyl alcohol/water. Safe fill height 430mm. | The single compartment marine storage tanks are approved for the storage of flammable liquids - 70/30 Ethanol/Water or 50/50 Isopropyl alcohol/water. Safe fill height 430mm | ETECH NZ Ltd Palmerston North |  | 2015-11-05 | FAB0028 - expired
TNK10035 | 2010-11-08 | NYMIC Engineering Ltd. |  | AS 1692-2006, Category 4 FAB0023 | Capacity 10,000 litres | Approved for: The storage and transfer of automotive or low flash point diesel having a hazard classification of 3.1D or 3.1C. | NYMIC Engineering |  | N/A | FAB0023
TNK10036 | 2010-12-07 | NYMIC Engineering Ltd. |  | AS 1692-2006, Category 4 FAB0023 | Capacity 21,710 litres | Approved for: The storage and transfer of automotive or low flash point diesel having a hazard classification of 3.1D or 3.1C. | NYMIC Engineering |  | N/A | FAB0023
TNK11001 | 2011-01-24 | NYMIC Engineering Ltd. |  | AS 1692 - 2006 Catergory 4 FAB0023 | Capacity 30,925 litres | Approved for: The storage and transfer of automotive or low flash point diesel having a hazard classification of 3.1D or 3.1C | NYMIC Engineering |  | N/A | FAB0023
TNK11002 | 2011-01-31 | RES (2013) Ltd 130 Collins Road Hamilton 3245 | RES (2013) LIMITED FAB0043 | AS 1692-2006 Catergory 3/ HSNOCOP 24-1, 3/08 | Capacity 4970 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B | RES (2013) Ltd 130 Collins Road Hamilton 3245 |  | N/A | FAB0043
TNK11003 | 2011-01-31 | RES (2013) Ltd 130 Collins Road Hamilton 3245 | RES (2013) LIMITED FAB0043 | AS 1692-2006 Catergory 3/ HSNOCOP 24-1, 3/08 | Capacity 3,300 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B | RES (2013) Ltd 130 Collins Road Hamilton 3245 |  | N/A | FAB0043
TNK11004 | 2011-02-24 | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 |  | AS 1692 - 2006 Category 3 | Capacity 4,950 litres Envirobulka EBD50 double-skinned above-ground | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 |  | N/A | Fabricated by Western Global UK (FAB0053)
TNK11005 | 2011-02-24 | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 |  | AS 1692 - 2006 Category 3 | Capacity 10,450 litres Envirobulka EBD100 double-skinned above-ground | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B or 9.1B | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 |  | N/A | Fabricated by Western Global UK (FAB0053)
TNK11006 | 2011-03-04 | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692-2006, Cat. 4 / HSNOCOP 24-1, 3/08 As of 1 August 2019: AS1692 – 2006, Category 4 & Reduced Secondary Containment Safe Work Instrument 2017 (Impact Protected) | 77,500 L to 100,000 L | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B or 9.1B | Petroleum Services (2001) Ltd | Amended on 1 August 2019 as per compliance certificate 191547 | 2029-07-31 | FAB0083 (FAB0016 prior to 9/06/2019)
TNK11007 | 2011-03-18 | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 |  | AS 1692 - 2006 Category 3 | Capacity 2,650 Envirobulka EBD25 double-skinned above-ground | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B or 9.1B | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 |  | N/A | Fabricated by Western Global UK (FAB0053)
TNK11008 | 2011-04-07 | NYMIC Engineering Ltd. |  | AS 1692-2006, Category 4 FAB0023 | Capacity: 5,067 litres | Approved for: The storage and transfer of automotive or low flash point diesel having a hazard classification of 3.1D or 3.1C. | NYMIC Engineering |  | N/A | FAB0023
TNK11009 | 2011-05-11 | NYMIC Engineering Ltd. |  | AS 1692-2006, Category 5 FAB0023 | Capacity: 27,480 litres | Approved for: The storage and transfer of solvent based timber treatment preservative having a Hazard Classification of 3.1C, 6.1E, 6.3B, 6.5A, 6.5B, 6.9B, 9.1A, 9.4B | NYMIC Engineering |  | N/A | FAB0023
TNK11010 | 2011-05-11 | NYMIC Engineering Ltd. |  | AS 1692-2006, Category 5 FAB0023 | Capacity: 14,960 litres | Approved for: The storage and transfer of solvent based timber treatment preservative having a Hazard Classification of 3.1C, 6.1E, 6.3B, 6.5A, 6.5B, 6.9B, 9.1A, 9.4B | NYMIC Engineering |  | N/A | FAB0023
TNK11011 | 2011-05-20 | RES (2013) Ltd 130 Collins Road Hamilton 3245 | RES (2013) LIMITED FAB0043 | AS 1692-2006, Category 4 | Capacity: 21,426 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B or 9.1B | RES (2013) Ltd 130 Collins Road Hamilton 3245 |  | N/A | FAB0043
TNK11012 | 2011-05-12 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0046 | AS1692 – 2006, Category 5 | 50,000 litre aboveground CCA wood preservative storage tank, 3.762 m. Outside dia. x 4.80 m. High 6 mm. Gr250 mild steel shell, floor and roof. | Approved for: The storage of Class 8 subsidiary Class 6.1 Tim Tech CX Oxide copper chrome arsenic wood preservative diluted in water | Martin Engineering (Palmerston North) Ltd. |  | 2016-05-12 | FAB0046
FAB0044 | 2011-02-17 | Mansfield Installations Limited 34 Armstrong Street Palmerston North 0274 427 631 |  | AS1692:2006 |  | Above ground steel Stationary Containers with integral secondary containment. Class 3.1D - Diesel | Mansfield Installations Limited 34 Armstrong Street Palmerston North 0274 427 631 |  | 2014-02-17 | Fabricator of: TNK11013
TNK11013 | 2011-02-17 | Mansfield Installations Limited 34 Armstrong Street Palmerston North 0274 427 631 |  | AS1692:2006 | Capacity: 500 litres to 5000 litres | Material: Mild Steel (Plate thickness as per AS 1692) Substances certified for storage: 3.1D | Mansfield Installations Limited 34 Armstrong Street Palmerston North 0274 427 631 |  | 2014-02-17 | FAB0044
TNK11014 | 29/04/2011 27/07/2021 - Renewal | Mainline Sheetmetals Ltd., Hamilton | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161, Hamilton, 3240 FAB0018 | AS1692-2006, Category 2 | 495 L - Double skin horizontal cylindrical above ground boiler stationary tank Capacity: 494 litre Safe Fill Level: 469 litres | Name: Diesel only Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Mainline Sheet Metals, Hamilton | 110% secondary containment achieved. 495 litre double skin, single compartment aboveground diesel storage boiler tank. Outer diameter 0.777m., Inner diameter 0.730m x 1.268m long x 3mm Gr250 mild steel shell and ends inner and outer. All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to be provided in accordance with AS 1692:2006 for category 2 tanks. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe ﬁll height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all the fill / dip tubes in accordance with the requirements of AS 1692. Design Statement – Job No. 19-305 – In respect of: 495L double skin boiler tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 25/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692): Anchor and foundation requirements for 495L double skin boiler tank, with following parameters: Tank category 2, in accordance with AS 1692 Design wind speed = 56m/s (any NZ location) Design earthquake lateral force coefficient Cd(T) = 0.8g Hazard factor Z ≤ 0.45, importance level 2 and 25 years design life Minimum anchoring requirements: 1-M10 trubolt at each leg (T10085X) and 5mm thick footplate Minimum foundation requirements: 1.4m x 1m x 0.15m thick concrete slab, with SE72 mesh. Approved to supply a burner or engine (boiler). Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. | N/A | FAB0018
TNK11015 | 29/04/2011 27/07/2021 - Renewal | Mainline Sheetmetals Ltd., Hamilton | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161, Hamilton, 3240 FAB0018 | AS1692-2006, Category 2 | 950 L - Double skin horizontal cylindrical above ground boiler stationary tank Capacity: 943 litres Safe Fill Level: 896 litres | Name: Diesel only Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Mainline Sheet Metals, Hamilton | 110% secondary containment achieved. 950 litre double skin, single compartment aboveground diesel storage boiler tank. Outer diameter 1.078m., Inner diameter 1.002m x 1.248m long x 3mm Gr250 mild steel shell and ends inner and outer. All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to be provided in accordance with AS 1692:2006 for category 2 tanks. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe ﬁll height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all the fill / dip tubes in accordance with the requirements of AS 1692. Design Statement – Job No. 19-305 – In respect of: 950L double skin boiler tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 25/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692): Anchor and foundation requirements for 950L double skin boiler tank, with following parameters: Tank category 2, in accordance with AS 1692 Design wind speed = 56m/s (any NZ location) Design earthquake lateral force coefficient Cd(T) = 0.8g Hazard factor Z ≤ 0.45, importance level 2 and 25 years design life Minimum anchoring requirements: 1-M10 trubolt at each leg (T10085X) and 5mm thick footplate Minimum foundation requirements: 1.4m x 1.2m x 0.15m thick concrete slab, with SE72 mesh. Approved to supply a burner or engine (boiler). Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. | N/A | FAB0018
TNK11016 | 29/04/2011 27/07/2021 - Renewal | Mainline Sheetmetals Ltd., Hamilton | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161, Hamilton, 3240 FAB0018 | AS1692-2006, Category 2 | 1800 L - Double skin horizontal cylindrical above ground boiler stationary tank Capacity: 1825 litres Safe Fill Level: 1733 litres | Name: Diesel only Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Mainline Sheet Metals, Hamilton | 110% secondary containment achieved. 1800 litre double skin, single compartment aboveground diesel storage boiler tank. Outer diameter 1.276m., Inner diameter 1.242m x 1.558m long x 3mm Gr250 mild steel shell and ends inner and outer. All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to be provided in accordance with AS 1692:2006 for category 2 tanks. It is Mainline Sheetmetals Ltd's responsibility to ensure the correct size vents are fitted. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe ﬁll height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all the fill / dip tubes in accordance with the requirements of AS 1692. Design Statement – Job No. 19-305 – In respect of: 1800L double skin boiler tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 23/09/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692): Anchor and foundation requirements for 1800L double skin boiler tank, with following parameters: Tank category 2, in accordance with AS 1692 Design wind speed = 56m/s (any NZ location) Design earthquake lateral force coefficient Cd(T) = 0.8g Hazard factor Z ≤ 0.45, importance level 2 and 25 years design life Minimum anchoring requirements: 1-M10 trubolt at each leg (T10085X) and 5mm thick footplate Minimum foundation requirements: 2m x 2.3m x 0.15m thick concrete slab, with SE72 mesh. Approved to supply a burner or engine (boiler). Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. | N/A | FAB0018
TNK11017 | 2011-04-29 | Mainline Sheetmetals Ltd., Hamilton | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161 FAB0018 | AS1692-2006, Category 4 | Description: 3,000 litres double skin above ground cylindrical horizontal stationary tank Design Specification: AS 1692-2006 and 2017 SWI for Reduced Secondary Containment for Tanks Tank Type: Above Ground Stationary Tank Name of Designer: Mainline Sheetmetals Limited - Cam Besley Capacity: 2,943 Litres Compartments: 1 Maximum Safe Fill Level: 2,805 Litres | Name: Diesel Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161 | The 50 mm. diameter vent is to terminate not less than 150 mm. above the tank top. Filling and discharge of the tanks is to be carried out under liquid and vapour tight connections. Approved for supplying an engine or burner. Locations of installed tanks as stipulated as per Health and Safety at Work (Hazardous Substances—Reduced Secondary Containment for Certain Above Ground Stationary Tanks) Safe Work Instrument 2017 - Can be installed in all locations expect aerodrome. Design Statement, issued by: Stiles and Hooker Ltd, to: Mainline Sheetmetals Ltd, in respect of: 3000L Double Skin Boiler Tank. Tank design to AS1692, seismic and wind loading to AS/NZS1170, structure to AS/NZS3404. Signed by Roger Baker (CMEngNZ), dated 14/06/22. Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced Mainline Sheetmetals Limited drawings or applicable standard/s. | 2028-01-26 | FAB0018
TNK11018 | 2011-04-29 | Mainline Sheetmetals Ltd., Hamilton | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161 FAB0018 | AS1692-2006, Category 2 | 1800 litre double wall single compartment aboveground diesel storage boiler tank. Outer diameter 1.26m., Inner diameter 1.00m x 1.56m long x 3mm Gr250 mild steel shell and ends inner and outer. | Approved for the storage of Class 3.1D flammable liquids | Mainline Sheet Metals, Hamilton |  | 2016-05-09 | FAB0018
TNK11019 | 2011-07-20 | RES (2013) Ltd 130 Collins Road Hamilton 3245 | RES (2013) LIMITED FAB0043 | AS1692-2006, Category 4 | Capacity: 48,925 litres | Approved for the storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B & 9.1B | RES (2013) Ltd 130 Collins Road Hamilton 3245 |  | N/A | FAB0043
TNK11020 | 2011-07-25 | Roadrunner Manufacturing (NZ) Ltd 53 Bridge Street Bulls 4818 |  | AS1692-1989, Category 1 | Capacity: 499 litres | Approved for 3.1D, 6.1E, 6.3B, 6.7B & 9.1B | Roadrunner Manufacturing (NZ) Ltd 53 Bridge Street Bulls 4818 |  | N/A | Unsure of FAB number
TNK11021 | 2011-08-03 | Mercer Stainless Corbett Road Bell Block New Plymouth 4373 |  | AS1692-2006, Category 5 | Capacity: 13,000 litres | Approved for: 98% sulphuric acid having a hazard classification of 6.1D, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A & 9.1D | Mercer Stainless Corbett Road Bell Block New Plymouth 4373 |  | NA | Unsure of FAB number
TNK11022 | 2011-08-02 | Stockton Alliance Mining c/- Solid Energy NZ Ltd 2 Dole Street Ngakawau Westport 7822 |  | Design Code: UN Model Regulations, Chapter 6.5 | ID: 141274/31 Equipment #: Model SQDNA400-X1 Capacity: 400 litres Manufacture Year: 2010 | Approved for: The road transport and transfer of diesel only having a Hazard Classification of 3.1D, 6.1E, 6.3B, 6.7B & 9.1B | Stockton Alliance Mining c/- Solid Energy NZ Ltd 2 Dole Street Ngakawau Westport 7822 |  | N/A | Unsure of FAB number
FAB0045 | 14/08/2011 21/10/2021 - Renewal 3/03/2025 - Renewal |  | Martin Engineering (Palmerston North) Ltd. PO Box 5295, Terrace End, Palmerston North, 4441 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 | Design Specification: AS1692, BS EN 14015, API650, UL142 | Capacity: Up to 150,000 litres As of 3/03/2025: This fabricator is limited to the fabrication of: TNK0504, TNK11024, TNK13063, TNK13064, TNK13065, TNK13066, TNK13067, TNK13068, TNK13069, TNK13070, TNK13071, TNK13072, TNK16020, TNK17008, TNK18035, TNK18037, TNK18055, TNK18056, TNK18057, TNK18058, TNK18059, TNK19018, TNK20002, TNK20005, TNK20015, TNK20016, TNK20037, TNK20280, TNK20281, TNK20282, TNK20335, TNK20360, TNK20563. | Storage of Classes 3.1 A-D flammable liquids |  | Fabrication, inspection and testing in accordance with the speciﬁed tank design and fabrication code, approved tank design drawings and approved for construction drawings. Allocation of individual tank serial numbers. Retention of individual tank QA records. In addition to the conditions specified on Compliance Certificate 6412-0002, the following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2028-03-03 | Fabricator of: TNK0502, TNK0504, TNK0506, TNK0810, TNK0811, TNK0813, TNK0829, TNK1021, TNK1022, TNK11024, TNK12024, TNK13001, TNK13024, TNK13025, TNK13026, TNK13059, TNK13063, TNK13064, TNK13065, TNK13066, TNK13067, TNK13068, TNK13069, TNK13070, TNK13071, TNK13072, TNK13079, TNK13080, TNK13081, TNK13082, TNK13083, TNK13084, TNK16020, TNK17008, TNK18035, TNK18037, TNK18055, TNK18056, TNK18057, TNK18058, TNK18059, TNK19018, TNK20002, TNK20005, TNK20015, TNK20016, TNK20335, TNK20360, TNK20281 As of 3/03/2025: TNK0504, TNK11024, TNK13063, TNK13064, TNK13065, TNK13066, TNK13067, TNK13068, TNK13069, TNK13070, TNK13071, TNK13072, TNK16020, TNK17008, TNK18035, TNK18037, TNK18055, TNK18056, TNK18057, TNK18058, TNK18059, TNK19018, TNK20002, TNK20005, TNK20015, TNK20016, TNK20037, TNK20280, TNK20281, TNK20282, TNK20335, TNK20360, TNK20563
TNK11023 | 2011-09-08 | RES (2013) Ltd 130 Collins Road Hamilton 3245 | RES (2013) LIMITED FAB0043 | AS 1692-2006, Category 4 | Capacity: 18,975 litres | Approved for: The storage and transfer of Urea 30%-40% solution having a hazard classification of 6.1D, 6.3B, 6.4A, E, 6.3A, 6.4A, 9.3C | RES (2013) Ltd 130 Collins Road Hamilton 3245 |  | N/A | FAB0043
TNK11024 | 9/29/2011 & 4/4/2012 & 4/03/2020 (Certificate CC02122) | Martin Engineering Ltd. 891 Tremaine Avenue Palmerston North | Martin Engineering (Palmerston North) Ltd. FAB0045 | Prior to 4/03/2020 AS1692: 1989 Cat.4 tank HSNOCOP 24-1 (March 2008) multi hazard rated (2 hour) tanks to UL 2085 :1997 As of 4/03/2020 (Certificate CC02122) AS1692 – 2006, Category 4 & Reduced Secondary Containment Safe Work Instrument 2017 (Impact Protected) | 5,000 litre double wall steel aboveground fuel storage tanks Safe Fill Volume: 5,000 litres | Prior to 4/03/2020 Diesel fuel Class 3.1D As of 4/03/2020 (Certificate CC02122) Flammable liquids having hazard classifications 3.1C or 3.1D | Martin Engineering (Palmerston North) Ltd. | As of 4/03/2020 (Certificate CC02122) Tank specific vent design required. Randall & Associates Wind & Seismic Design Compliance Certificate MS 59413. Allocate unique serial number for each tank and retain fabrication records. Approval is invalid following any changes to the design parameters and / or referenced Martin Engineering Design Drawings. | 2030-03-04 | FAB0045
TNK11025 | 2011-10-13 | RES (2013) Ltd 130 Collins Road Hamilton 3245 | RES (2013) LIMITED FAB0043 | AS 1692-2006, Category 4 | Capacity: 150,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B |  |  | N/A | FAB0043
FAB0046 | 2011-10-20 |  | Martin Engineering Ltd. 891 Tremaine Avenue Palmerston North | AS1692, Category 5 (ref TNK11012) | carbon steel AS 1594-HA300 in thickness range 4.5 to 9mm |  | Martin Engineering Ltd. 891 Tremaine Avenue Palmerston North Tel: 06 357 9052 |  | 2014-10-20 | Fabricator of: TNK 11012 11030, 11031.
TNK11026 | 2011-10-17 | RES (2013) Ltd 130 Collins Road Hamilton 3245 | RES (2013) LIMITED FAB0043 | AS 1692-2006, Category 4 | Capacity: 5,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B | RES (2013) Ltd 130 Collins Road Hamilton 3245 |  | N/A | FAB0043
TNK11027 | 2011-10-19 | Jardboranir HF - NZ Branch 283 Vaughan Road Rotorua 3010 PO Box 992, Rotorua 3040 |  | BS EN 12285 | Capacity: 30,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B | Jardboranir HF - NZ Branch 283 Vaughan Road Rotorua 3010 PO Box 992, Rotorua 3040 |  | N/A | Unsure of Fabricator
TNK11028 | 2011-10-19 | Jardboranir HF - NZ Branch 283 Vaughan Road Rotorua 3010 PO Box 992, Rotorua 3040 |  | BS EN 12285 | Capacity: 30,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B | Jardboranir HF - NZ Branch 283 Vaughan Road Rotorua 3010 PO Box 992, Rotorua 3040 |  | N/A | Unsure of Fabricator
TNK11029 | 2011-12-12 | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 |  | AS 1692-2006, Category 3 | Capacity: 21,500 litres Envirobulka EBD180 double-skinned above-ground | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 |  | N/A | Fabricated by Western Global UK (FAB0053)
TNK11030 | 2011-11-13 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0046 | AS1692 – 2006, Category 5 | 4,500 litre above ground open top sodium sulphide storage tank | Approved for: sodium sulphide | Martin Engineering Ltd. 891 Tremaine Avenue Palmerston North Tel: 06 357 9052 |  | 2016-11-13 | FAB0046
TNK11031 | 2011-11-20 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0046 | AS1692 – 2006, Category 5 | 4,500 litre above ground open top sodium sulphide storage tank | Approved for: sodium sulphide | Martin Engineering Ltd. 891 Tremaine Avenue Palmerston North Tel: 06 357 9052 |  | 2016-11-20 | FAB0046
TNK11032 | 2011-11-29 | RES (2013) Ltd 130 Collins Road Hamilton 3245 | RES (2013) LIMITED FAB0043 | AS1692-2006, Category 4 | Capacity 50,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B | RES (2013) Ltd 130 Collins Road Hamilton 3245 |  | N/A | FAB0043
TNK11033 | 2011-11-14 | Arista Group Limited PO Box 10125 Phillipstown Christchurch | Zhangjiagang Logitank Heavy Industry Co. Ltd No.3, Hai Xin North Road, Zhangjiagang City, 215600 FAB0052 | AS 1692-2006, Cat 3 (primary tank). AS 1940-2004 | Design Ref: LSK 1000 Kube tank, Manufacturer: LogiTank Pty Ltd. Facility: Double skin steel PUFF storage tank. Material: 5mm mild steel plate primary & 3mm secondary Capacity: 1250 litres gross. SFL 1,000 lts | Class 3.1D flammable liquids | Arista Group Limited PO Box 10125 Phillipstown Christchurch |  | 2016-11-13 | FAB0052
TNK11034 | 2011-11-14 | Arista Group Limited PO Box 10125 Phillipstown Christchurch | Zhangjiagang Logitank Heavy Industry Co. Ltd No.3, Hai Xin North Road, Zhangjiagang City, 215600 FAB0052 | AS 1692-2006, Cat 3 (primary tank). AS 1940-2004 | Design Ref: LSB-12 Manufacturer: LogiTank Pty Ltd. Facility: Double skin steel PUFF storage tank. Material: 6mm mild steel plate GR 250mPa primary & secondary Capacity: 11,700 litres gross. SFL 10,530 lts | Class 3.1D flammable liquids | Arista Group Limited PO Box 10125 Phillipstown Christchurch |  | 2016-11-13 | FAB0052
TNK11035 | 2011-11-14 | Arista Group Limited PO Box 10125 Phillipstown Christchurch | Zhangjiagang Logitank Heavy Industry Co. Ltd No.3, Hai Xin North Road, Zhangjiagang City, 215600 FAB0052 | AS 1692-2006, Cat 3 (primary tank). AS 1940-2004 | Design Ref: LSB-30 Manufacturer: LogiTank Pty Ltd. Facility: Double skin steel PUFF storage tank. Material: 6mm mild steel plate GR 250mPa primary & secondary Capacity: 30,500 litres gross. SFL 27,450 lts | Class 3.1D flammable liquids | Arista Group Limited PO Box 10125 Phillipstown Christchurch |  | 2016-11-13 | FAB0052
TNK11036 | 2011-11-14 | Arista Group Limited PO Box 10125 Phillipstown Christchurch | Zhangjiagang Logitank Heavy Industry Co. Ltd No.3, Hai Xin North Road, Zhangjiagang City, 215600 FAB0052 | AS 1692-2006, Cat 3 (primary tank). AS 1940-2004 | Design Ref: LSB-68 Manufacturer: LogiTank Pty Ltd. Facility: Double skin steel PUFF storage tank. Material: 6mm mild steel plate GR 250mPa primary & secondary Capacity: 68,000 litres gross. SFL 61,200 lts | Class 3.1D flammable liquids | Arista Group Limited PO Box 10125 Phillipstown Christchurch |  | 2016-11-13 | FAB0052
TNK11037 | 2011-11-14 | Arista Group Limited PO Box 10125 Phillipstown Christchurch | Zhangjiagang Logitank Heavy Industry Co. Ltd No.3, Hai Xin North Road, Zhangjiagang City, 215600 FAB0052 | AS 1692-2006, Cat 3 (primary tank). AS 1940-2004 | Design Ref: LSB-80 Manufacturer: LogiTank Pty Ltd. Facility: Double skin steel PUFF storage tank. Material: 6mm mild steel plate GR 250mPa primary & secondary Capacity: 81,500 litres gross. SFL 73,350 lts | Class 3.1D flammable liquids | Arista Group Limited PO Box 10125 Phillipstown Christchurch |  | 2016-11-13 | FAB0052
TNK11038 | 2011-11-14 | Arista Group Limited PO Box 10125 Phillipstown Christchurch | Zhangjiagang Logitank Heavy Industry Co. Ltd No.3, Hai Xin North Road, Zhangjiagang City, 215600 FAB0052 | AS 1692-2006, Cat 3 (primary tank). AS 1940-2004 | Design Ref: LSB-105 Manufacturer: LogiTank Pty Ltd. Facility: Double skin steel PUFF storage tank. Material: 6mm mild steel plate GR 250mPa primary & secondary Capacity: 99,500 litres gross. SFL 95,000 lts | Class 3.1D flammable liquids | Arista Group Limited PO Box 10125 Phillipstown Christchurch |  | 2016-11-13 | FAB0052
TNK12001 | 2012-01-26 | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 |  | AS1692-2006, Category 3 | Capacity: 29,400 litres Envirobulka EBD270 double-skinned above-ground | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 |  | N/A | Fabricated by Western Global UK (FAB0053)
TNK12002 | 2012-01-31 | Scott Sheetmetal Co. Cnr Railway and Ontario Streets Gore (03) 208 5381 |  | AS1692-2006, Category 1 | Capacity: 503 & 944 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B |  |  | N/A | FAB0025
TNK12003 | 2012-03-26 | Jardboranir HF - NZ Branch 283 Vaughan Road Rotorua 3010 PO Box 992, Rotorua 3040 |  | BS EN 12285 | Capacity: 30,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B. |  |  | N/A | Unsure of Fabricator
TNK12004 | 2012-03-15 | Advanced Fuel Tanks NZ Limited PO Box 41 029 Christchurch | Advanced Fuel Tanks NZ Limited 5 Tanya St, Bromley, Christchurch | AS1692:2006 Cat 3 | iT87 double wall mild steel diesel storage tank. Max safe fill capacity: 85,240 litres | Approved for: The storage of Class 3.1D flammable liquids | Advanced Fuel Tanks NZ Limited PO Box 41 029 Christchurch |  | 2022-03-14 | FAB0014
TNK12005 | 2012-04-04 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692-2006, Category 4 | Capacity: 6,500 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B |  |  | N/A | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
TNK12006 | 2012-04-04 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692-2006, Category 4 | Capacity: 13,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B |  |  | N/A | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
TNK12007 | 2012-04-04 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692-2006, Category 4 | Capacity: 20,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B |  |  | N/A | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
TNK12008 | 2012-04-04 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692-2006, Category 4 & HSNOCOP 24-1 | Capacity: 6,500 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B |  |  | N/A | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
TNK12009 | 2012-04-04 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692-2006, Category 4 & HSNOCOP 24-1 | Capacity: 13,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B |  |  | N/A | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
TNK12010 | 2012-04-04 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692-2006, Category 4 & HSNOCOP 24-1 | Capacity: 20,000 litres | Approved for: The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E,6.3B,6.7B,9.1B |  |  | N/A | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
FAB0047 | 4/04/2012 |  | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North | AS 1692-2006 | Capacity: Up to 60,000 litres | Approved for: The shop fabrication of steel tanks up to 60,000 litres capacity for Classes 3.1A, B, C or D hazardous substances for which TNK numbers have been registered with ERMA / EPA / WorkSafe New Zealand | TNK 12005, 12006, 12007, 12008, 12009, 12010, 13023, 13027, 13057, 13078, 16009, 16015, 16016, 17000, 18003, 18004, 18036, 20007. TAN 16025, 16026. | Retention of individual tank fabrication and testing records. | 2021-08-01 | Fabricator of: TNK 12005, 12006, 12007, 12008, 12009, 12010, 13023, 13027, 13057, 13078, 16009, 16015, 16016, 17000, 18003, 18004, 18036, 20007. Fabricators of Tankwagons: TAN 16025, 16026.
TNK12011 | 2012-05-07 | BVT Consulting Limited | NYMIC Engineering Ltd 9 Kilronan Place Wigram Christchurch FAB0023 | AS1692-2006 Category 4. | 3275 L Double Skin Tank | Approved for :The storage and transfer of automotive or low flashpoint diesel having a hazard classification of 3.1D or 3.1C | NYMIC Engineering Ltd |  | N/A | For 3.1D substances, the tank must be connected to a burner or generator. FAB0023
TNK12012 | 2012-05-22 | FUEL PRO 130 COLLINS ROAD HAMILTON | RES (2013) LIMITED FAB0043 | AS1692-2006 Category 3 | 11,000 L double-skin above-ground steel storage tank. | Approved for - the storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, and 9.1B | RES (2013) Ltd 130 Collins Road Hamilton 3245 |  | N/A | FAB0043
FAB0048 | 2012-07-02 |  | Taylors Manufacturing Ltd (t/a Taymac) 19 Taurus Place Bromley Christchurch | TNK12018 TNK12019 TNK13002 TNK13003 | see listings | Approved for: The shop fabrication of steel tanks for Class 3.1 D hazardous substances in accordance with AS 1692-2006 | Taylors Manufacturing Ltd (t/a Taymac) 19 Taurus Place Bromley Christchurch |  | 2/07/2015 for TNK12018 & TNK12019 22/1/2016 for TNK13002 & TNK13003 | Fabricator of: TNK12018 , TNK12019, TNK13002 & TNK13003
TNK12013 | 2012-05-14 | Wellman Associates Ltd | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 5 | 30,000 litre above ground insulated stainless steel storage tank, 2910mmID x 5.88m. High 5mm. 304L s/s shell, cone down floor 6mm 304L s/s and cone roof 5 mm 304L s/s. Operating volume 29,000L Tank serial number V278, Fonterra no. CH29 | Approved for: Product Resolve plus caustic soda, s.g. 1.49 gm/cm3 | ETECH NZ Ltd Palmerston North | Subject to the conditions specified on the Test Certificate 2012026 | 2017-05-14 | FAB0049
TNK12014 | 2012-05-14 | Wellman Associates Ltd | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 5 | 21,000 litre above ground 50mm air gap stainless steel storage tank, 2500mm ID x 6.204m. High 5mm. 304L s/s shell, cone down floor 6mm 304L s/s and cone roof 5 mm 304L s/s. Operating volume 20,000L Tank serial number V277, Fonterra no. CH28 | Approved for: 68% nitric acid, s.g. 1.4 gm/cm3 | ETECH NZ Ltd Palmerston North | Subject to the conditions specified on the Test Certificate 2012026 | 2017-05-14 | FAB0049
TNK12015 | 2012-05-14 | Wellman Associates Ltd | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 5 | 7,000 litre above ground clad stainless steel storage tank, 2000mm ID x 4.047m. High 5mm. 316L s/s shell, cone down floor 6mm 316L s/s and cone roof 5 mm 316L s/s. Operating volume 6,500L Tank serial number V274, Fonterra no. CH24 | Approved for: 5-25% acetic acid, s.g. 1.02 gm/cm3 | ETECH NZ Ltd Palmerston North | Subject to the conditions specified on the Test Certificate 2012026 | 2017-05-14 | FAB0049
TNK12016 | 2012-05-14 | Wellman Associates Ltd | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 5 | 21,000 litre above ground clad stainless steel storage tank, 2500mm ID x 6.204m. High 5mm. 316L s/s shell, cone down floor 6mm 316L s/s and cone roof 5 mm 316L s/s. Operating volume 20,000L Tank serial number V275, Fonterra no. CH25 | Approved for: 80% acetic acid, s.g. 1.04 gm/cm3 | ETECH NZ Ltd Palmerston North | Subject to the conditions specified on the Test Certificate 2012026 | 2017-05-14 | FAB0049
TNK12017 | 2012-05-14 | Wellman Associates Ltd | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 5 | 21,000 litre above ground clad stainless steel storage tank, 2500mm ID x 6.204m. High 5mm. 304L s/s shell, cone down floor 6mm 304L s/s and cone roof 5 mm 304L s/s. Operating volume 20,000L Tank serial number V276, Fonterra no. CH26 | Approved for: 25% aqueous ammonia, s.g. 1.00 gm/cm3 | ETECH NZ Ltd Palmerston North | Subject to the conditions specified on the Test Certificate 2012026 | 2017-05-14 | FAB0049
TNK12018 | 2012-07-04 | Taymac |  | AS1692-2006, under HSNOCOP24-1, 03-08 | 20,000 Litre above ground DC tank | Approved for: Storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B or 9.1B | Taylors Manufacturing Ltd (t/a Taymac) 19 Taurus Place Bromley Christchurch | Subject to the conditions specified on the Test Certificate 290 | N/A | TNK12018 is assigned to FAB0048 (dated 02-07-2012).
TNK12019 | 2012-07-05 | Taymac |  | AS1692-2006, under HSNOCOP24-1, 03-08 | 15000 Litre above ground double skin tank | Approved for: Storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B or 9.1B | Taylors Manufacturing Ltd (t/a Taymac) 19 Taurus Place Bromley Christchurch | Subject to the conditions specified on the Test Certificate 291 | N/A | TNK12019 is assigned to FAB0048 (dated 02-07-2012).
FAB0049 | 21/07/2012 22/01/2016 |  | ETECH NZ Ltd Palmerston North | AS 1692, Category 5 | see listings |  | ETECH NZ Ltd 130 Kaimanawa Street Palmerston North | Subject to the conditions specified on the Test Certificate 2016004 | 2019-01-21 | Fabricator of: TNK12013, TNK12014, TNK12015, TNK12016, TNK12017, TNK13006
TNK12020 | 2012-08-20 | Mainline Sheetmetals Ltd., Hamilton | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161 FAB0018 | AS 1692 - 2006 Category 2 | 2350 Litre single wall single compartment above ground diesel storage tank. Outer diameter 1.33m x 1.86m long x 3mm Gr250 mild steel shell and 4mm knuckled Gr 250 heads. | Approved for the storage of Class 3.1D flammable liquids. | Mainline Sheet Metals, Hamilton | Subject to the conditions specified on the Test Certificate 2012062 | 2017-08-20 | FAB0018
TNK12021 | 22/08/2012 27/07/2021 - Renewal | Mainline Sheetmetals Ltd., Hamilton | Mainline Sheetmetals Ltd, 209 Ellis St Hamilton PO Box 15161, Hamilton, 3240 FAB0018 | AS1692 - 2006 Category 2 | 1400 L - Double skin horizontal cylindrical above ground boiler stationary tank Capacity: 1428 litres Safe Fill Level: 1357 litres | Name: Diesel only Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Mainline Sheet Metals, Hamilton | 110% secondary containment achieved. 1400 litre double skin, single compartment aboveground diesel storage boiler tank. Outer diameter 1.276m., Inner diameter 1.233m x 1.248m long x 3mm Gr250 mild steel shell and ends inner and outer. All tanks are to be fabricated, inspected and tested for leakage before shipment from the factory as completely assembled vessels. Venting - Description: Extended 2” Vent, Drawing No.: CB-SW-0836, Sheet: 1, Date: 4/06/20, Drawn by: C Besley. Venting of the tanks is to be provided in accordance with AS 1692:2006 for category 2 tanks. It is Mainline Sheetmetals Ltd's responsibility to ensure the correct size vents are fitted. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe ﬁll height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks may be carried out under liquid and vapour tight connections. Doubler plates are to be fitted under all the fill / dip tubes in accordance with the requirements of AS 1692. Design Statement – Job No. 19-305 – In respect of: 1400L double skin boiler tank, Issued by: Stiles and Hooker Architects + Engineers, Roger Baker dated 7/05/2020 (AS/NZS 1170, AS/NZS 3404 & AS 1692): Anchor and foundation requirements for 1400L double skin boiler tank, with following parameters: Tank category 2, in accordance with AS 1692 Design wind speed = 56m/s (any NZ location) Design earthquake lateral force coefficient Cd(T) = 0.8g Hazard factor Z ≤ 0.45, importance level 2 and 25 years design life Minimum anchoring requirements: 1-M10 trubolt at each leg (T10085X) and 5mm thick footplate Minimum foundation requirements: 2m x 2m x 0.15m thick concrete slab, with SE72 mesh. Approved to supply a burner or engine (boiler). Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. | N/A | FAB0018
TNK12022 | 2012-08-26 | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 |  | AS1692-2006, Category 3 | 39500 Litre double skin above ground tank EBD370. | Approved for: Storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B or 9.1B | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 | Subject to the conditions specified on the Test Certificate TC311 |  | Fabricated by Western Global UK (FAB0053)
TNK12023 | 2012-10-24 | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS1692-2006, Category 4 | 30,000 L single skin above ground horizontal tank on foot mounts. | Approved for storage and transfer of Premium motor spirit with a hazard classification of 3.1A, 6.1E, 6.3B, 6.7B or 9.1B. | Petroleum Services (2001) Ltd | Subject to the conditions on the Test Certificate TC322 | N/A | FAB0083 (FAB0016 prior to 9/06/2019)
TNK12024 | 2012-11-26 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS1692 – 2006, Category 3 | 5670 litre single compartment above-ground double wall diesel generator base storage tank, 8360mm o/a length. X 1842mm. Wide x 595mm. High, 6mm Gr250 mild steel inner tank and double wall. | Approved for storage of Class 3.1D flammable liquids. | Martin Engineering | Subject to the conditions specified on the Test Certificate 2012077 | 2015-11-26 | FAB0045
TNK12025 | 2012-11-28 | Gilkison & Engineering Maintenance Ltd, Invercargill | FAB0040 | AS1692-2006, Category 4 | 2770 Litre above ground petrol tank. | Approved for storage and transfer of Premium motor spirit with a hazard classification of 3.1A, 6.1E, 6.3B, 6.7B or 9.1B. | Gilkison & Engineering Maintenance Ltd, Invercargill | Subject to the conditions on the Test Certificate TC332 |  | FAB0040
TNK13001 | 2013-01-11 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS1692 – 2006, Category 4 | 80000 Litre four compartment above-ground double wall storage tank. 2784mm outside diameter x 14225mm OAL x 6mm wrap plate. 11000L 'Ad Blue' tank 40000L Diesel tank 12000L Diesel Tank 15000L Kerosene tank. | Approved for storage of class 3.1C or D flammable liquids. | Martin Engineering | Subject to the conditions specified on the Test Certificate 2012076 | 2016-01-11 | FAB0045
TNK13002 | 2013-01-21 | Taymac |  | AS1692-2006, HSNOCOP24-1,03-08 | 10000L DC Above Ground Tank | Approved for storage and transfer of diesel with a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Taylors Manufacturing Ltd (t/a Taymac) 19 Taurus Place Bromley Christchurch | Subject to the conditions specified on the Test Certificate TC00401 |  | FAB0048
TNK13003 | 2013-01-21 | Taymac |  | AS1692-2006, HSNOCOP24-1,03-08 | 20000 PUF Tank | Approved for storage and transfer of diesel with a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Taylors Manufacturing Ltd (t/a Taymac) 19 Taurus Place Bromley Christchurch | Subject to the conditions specified on the Test Certificate TC00402 |  | FAB0048
FAB0050 | 2014-07-01 |  | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu 3840 | Prior to 13/07/2020: Design Standards: AS 1692-2006, HSNOCOP 24-1, HSNOCOP 6-V2.1 From 13/07/2020: Design Standard: AS 1692-2006 From 5/12/2024: Design Standards: AS 1692-2006, Reduced Secondary Containment Safe Work Instrument 2017, UL142, SwRI 95-01, SwRI 95-03 | Capacity: Up to 60,000 litres (maximum gross capacity) Prior to 27/06/2023: TAN13021, TAN13045, TAN16014, From 27/06/2023: TNK13021, TNK13022, TNK13077,TNK15026, TNK16003, TNK16004,TNK16012, TNK16018, TNK16023, TNK17010, TNK19000, TNK19001, TNK19002, TNK19003, TNK20038, TNK20083, TNK20093, TNK20106, TNK20168, TNK20173, TNK20174, TNK20175 From 5/12/2024: Shop fabrication of steel tanks up to 100,000 litres capacity for TNK13021, TNK13022, TNK13077, TNK15026, TNK16003, TNK16004, TNK16012, TNK16018, TNK16023, TNK17010, TNK19000, TNK19001, TNK19002, TNK19003, TNK20038, TNK20083, TNK20093, TNK20106, TNK20168, TNK20173, TNK20174, TNK20175, TNK20334, TNK20388 | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu 3840 | Subject to the conditions specified on Test Certificate TC00409/ TC00432 / TC00441 / TC00528 / TC00662 / TC01053 / TC01141 / TC01191, TC01205, TC01255, TC01257, TC01305, TC01433, CC01886, CC01887, CC01888, CC01889, CC02261, 6480-001, 100241-6644-09, 100241-6644-07, 100241-6644-08, 100241-7524-02. Approval apply only to designs for which TNK numbers have been registered tiwh ERMA/EPA/WorkSafe New Zealand. Allocation of unique individual tank serial number to be stamped on each individual tank and recorded. Retention of individual tank fabrication, testing records and QA records for each tank. | 2027-12-05 | Fabricator of: Prior to 27/06/2023: TAN13021, TAN13045, TAN16014 From 27/06/2023: TNK13021, TNK13022, TNK13077,TNK15026, TNK16003, TNK16004, TNK16012, TNK16018, TNK16023, TNK17010, TNK19000, TNK19001, TNK19002, TNK19003, TNK20038,TNK20083, TNK20093, TNK20106, TNK20168, TNK20173, TNK20174, TNK20175, TNK20334, TNK20388
TNK13004 | 2013-04-30 | NYMIC Engineering Ltd. |  | AS 1692-2006/ HSNOCOP 24-1, 3/08 FAB0023 | 20,000 Litre above ground double skin tank | Approved for storage and transfer of diesel with a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | NYMIC Engineering Ltd, Christchurch | Subject to the conditions specified on the Test Certificate TC00433 |  | FAB0023
TNK13005 | 2013-06-05 | RES (2013) Ltd 140 Collins Road Hamilton 3245 | RES (2013) LIMITED FAB0043 | AS 1692-2006/ HSNOCOP 24-1, 3/08 | 10,932 Litre above-ground double skin tank. | Approved for storage and transfer of AdBlue (Urea >26% solution) diesel exhaust fluid having a hazard classification of 6.1D, 6.3B, 6.4A, 9.3C. | RES (2013) Ltd 140 Collins Road Hamilton 3245 | Subject to the conditions specified on the Test Certificate TC00449. | N/A | FAB0043
TNK13006 | 2013-06-18 | Wellman Associates Ltd | ETECH NZ Ltd Palmerston North | AS1692-2006, Category 5 | 30,000 Litre above-ground insulated stainless steel storage tank, 2910mm ID x 6.255m high 5mm 304L s/s shell, cone down floor 6mm 304L s/s and cone roof 5mm 304L s/s Operating volume 29,000L Tank serial #V290, Fonterra no. MT34 | Approved for storage of Rezolve plus caustic soda, s.g. 1.53 gm/cm3 (50% caustic soda solution) | ETECH NZ Ltd Palmerston North | Subject to the conditions specified on the Test Certificate 2013045 | 2018-06-18 | FAB0049
TNK13007 | 2011-11-14 | Arista Group Limited PO Box 10125 Phillipstown Christchurch | Zhangjiagang Logitank Heavy Industry Co. Ltd No.3, Hai Xin North Road, Zhangjiagang City, 215600 FAB0052 | AS 1692 : 2006 Cat 3 (primary tank) AS 1940-2004 | 20,000 Litres gross SFL 18,000L double skin steel PUFF storage tank Material: 6mm mild steel plate GR 250mPa primary and secondary | Approved for Class 3.1D flammable liquids. | Arista Group Limited PO Box 10125 Phillipstown Christchurch | Subject to the conditions specified on the Test Certificate SCS D 26 | 2016-11-13 | FAB0052
TNK13008 | 2011-11-14 | Arista Group Limited PO Box 10125 Phillipstown Christchurch | Zhangjiagang Logitank Heavy Industry Co. Ltd No.3, Hai Xin North Road, Zhangjiagang City, 215600 FAB0052 | AS 1692 : 2006 Cat 3 (primary tank) AS 1940-2004 | 74,388 Litres gross SFL 70,688L double skin steel PUFF storage tank Material: 6mm mild steel plate GR 250mPa primary and secondary | Approved for Class 3.1D flammable liquids. | Arista Group Limited PO Box 10125 Phillipstown Christchurch | Subject to the conditions specified on the Test Certificate SCS D 27 | 2016-11-13 | FAB0052
TNK13009 | 2011-11-14 | Arista Group Limited PO Box 10125 Phillipstown Christchurch | Zhangjiagang Logitank Heavy Industry Co. Ltd No.3, Hai Xin North Road, Zhangjiagang City, 215600 FAB0052 | AS 1692 : 2006 Cat 3 (primary tank) AS 1940-2004 | 38,000 Litres gross SFL 34,200L double skin steel PUFF storage tank Material: 6mm mild steel plate GR 250mPa primary and secondary | Approved for Class 3.1D flammable liquids. | Arista Group Limited PO Box 10125 Phillipstown Christchurch | Subject to the conditions specified on the Test Certificate SCS D 28 | 2016-11-13 | FAB0052
TNK13010 | 26/07/2012 26/7/2015 | SWRI | Advanced Fuel Tanks N.Z. Ltd 5 Tanya St, Bromley, Christchurch | Supervault FL SWRI 93-01 AS1692 & UL142 | Cylindrical D1 1000 - 5600 litres D2 5800 - 17600 litres D3 5300 - 35600 litres D4 19000 - 55100 litres and up to 60,000 litres | Class 3.1A, B, C & D | SWRI |  | 2018-07-26 | FAB0014
TNK13011 | 2012-07-26 | Fuelchief Limited - DL | Prior to 29/01/2021: Advanced Fuel Tanks N.Z. Ltd 5 Tanya St, Bromley, Christchurch FAB0014/FAB0069 As of 29/01/2021: Fuelchief 5 Tanya Street PO Box 41 029 Bromley, Christchurch FAB0076 As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 FAB0069 or FAB0093 | UL 142 and SwRI 95-03 As of 17/02/2026: UL142, SwRI 95-03, SwRI 93-01, AS1692 and AS1940. | Prior to 29/01/2021: Cylindrical D1 1000 - 5600 litres D2 5800 - 17600 litres D3 5300 - 35600 litres D4 19000 - 55100 litres and up to 60,000 litres As of 29/01/2021 SuperVault 2,434L to 110,000L above ground double skin horizontal cylindrical stationary tank range | Prior to 17/02/2026: Class 3.1A, 3.1B, 3.1C or 3.1D As of 17/02/2026: 3.1A, 3.1B, 3.1C, 3.1D, 6.1A, 6.1B, 6.1C, 6.1D, 6.5A, 6.5B, 6.6A, 6.6B, 6.7A, 6.7B, 6.8A, 6.8B, 6.8C, 6.9A, 6.9B, 8.2A, 8.2B, 8.2C, 8.3A | Fuelchief Limited | Specific vent design required for each tank. O'Loughlan Taylor Spence Ltd design Certificate 3375/JSO. Babbage Consultants Ltd compliance letter 22/05/15. Allocate unique serial number for each tank and retain individual tank fabrication records. This approval expires following any change to the original design parameters and / or referenced Fuelchief Drawings. Tank range generic PS1: 5970- Fuelchief SV1-5 PS1, Draft 00, Rev 01, 13OCT21. Validation of additional tanks: 8913-CAN-0001, Additional SV Tanks, Rev00, 16Feb26. SuperVault MH Tank SwRI certificate: Fuelchief Ltd_SwRI 95-03 Certificate, Document No: 08177-03-02. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. Approved to supply an engine or burner. | 2036-02-17 | Prior to 29/01/2021: FAB0014/FAB0069 As of 29/01/2021: FAB0076 As of 19/03/2023 FAB0093 As of 11/04/2024 FAB0069 As of 02/04/2026: FAB0093
TNK13012 | 26/07/2012 26/7/2015 | 5 Tanya Street, Bromley, Christchurch, 8062 | Advanced Fuel Tanks N.Z. Ltd 5 Tanya St, Bromley, Christchurch | Supervault FL SWRI 93-01 AS1692 & UL142 | Rectangular 1000 - 7500 litres | Class 3.1A, B, C & D | SWRI |  | 2018-07-26 | FAB0014
TNK13013 | 26/07/2012 26/7/2015 8/10/2018 | Fuelchief Limited 5 Tanya Street, Bromley Christchurch (Formerly SWRI) | Fuelchief Limited 5 Tanya Street, Bromley Christchurch (Formerly Advanced Fuel Tanks N.Z. Ltd 5 Tanya St, Bromley, Christchurch) As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | Supervault MH SWRI 95-03 & UL142 | 773 to 7,732 litres rectangular tanks | Class 3.1A, 3.1B, 3.1C & 3.1D | Fuelchief Limited 5 Tanya Street, Bromley Christchurch (Formerly SWRI) | Tanks may supply a burner or generator. | 2028-10-07 | FAB0014/FAB0069/FAB0076 As of 19/03/2023 FAB0093 As of 11/04/2024 FAB0069 As of 02/04/2026 FAB0093
TNK13014 | 26/07/2012 26/7/2015 | SWRI | Advanced Fuel Tanks N.Z. Ltd 5 Tanya St, Bromley, Christchurch As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | Pyrotector Double Wall UL2085 AS1692 & UL142 | Cylindrical D1 1250 - 10500 litres D2 5600 - 24900 litres D3 8100 - 47800 litres D4 25200 - 56600 litres and up to 60,000 litres | Class 3.1A, B, C & D | SWRI |  | 2018-07-26 | FAB0014 As of 19/03/2023 FAB0093
TNK13015 | 26/07/2012 26/7/2015 14/12/2018 | Fuelchief Limited 5 Tanya Street, Bromley Christchurch (Formerly SWRI) | Fuelchief Limited 5 Tanya Street, Bromley Christchurch (Formerly Advanced Fuel Tanks N.Z. Ltd 5 Tanya St, Bromley, Christchurch) As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | Pyrotector Double Wall UL2085 AS1692 & UL142 2 hour fire rating in accordance with SwRI 97-04 | 1000 to 7500 litres rectangular Pyrotector tanks | Class 3.1A, B, C & D | Fuelchief Limited 5 Tanya Street, Bromley Christchurch (Formerly SWRI) | Specific venting capacity to be detemined per tank and product stored. | 2028-12-14 | FAB0014 (Expired 26/07/2018) FAB0076 (From 14/12/2018) As of 19/03/2023 FAB0093
TNK13016 | 14/04/2013 27/7/2015 | Advanced Fuel Tanks NZ Limited PO Box 41 029 Christchurch | Advanced Fuel Tanks NZ Limited 5 Tanya St, Bromley, Christchurch | Vanguard Double Skin AS1692: 2006 | Cylindrical VG2 5445 - 34800 litres VG3 7200 - 40200 litres VG4 28700 - 51700 litres and up to 60,000 litres | Class 3.1A, B, C & D | Advanced Fuel Tanks N.Z. Ltd |  | 2018-07-27 | FAB0014/FAB0069
TNK13017 | 14/04/2013 27/7/2015 - Renewal 17/06/2021 - Renewal | Prior to 17/06/2021: Advanced Fuel Tanks NZ Limited PO Box 41 029 Christchurch As of 17/06/2021: Fuelchief Limited PO Box, 41 029, Christchurch, 8247 5 Tanya Street, Bromley, Christchurch, | Prior to 17/06/2021: Advanced Fuel Tanks NZ Limited 5 Tanya St, Bromley, Christchurch FAB0014 Quindao Jinhuanghai Container Co Ltd c/- Fuelchief Ltd 5 Tanya Street Bromley, Christchurch FAB0069 As of 17/06/2021: Fuelchief Limited PO Box, 41 029, Christchurch, 8247 5 Tanya Street, Bromley, Christchurch, FAB0076 As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | Prior to 17/06/2021: Portaqube Double skin AS1692: 2006 As of 17/06/2021: AS 1692 & SWI Reduced Secondary Containment for Tanks | Prior to 17/06/2021: 1000 - 7500 litres tank As of 17/06/2021: Vanguard PortaQube 1,000 - 7,000 litres double skin above ground rectangular tank range designs Capacity: 1,000 to 7,000 litres | Prior to 17/06/2021: Class 3.1A, B, C & D As of 17/06/2021: Name: Diesel only Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Prior to 17/06/2021: Advanced Fuel Tanks NZ Limited PO Box 41 029 Christchurch As of 17/06/2021: Fuelchief Limited PO Box, 41 029, Christchurch, 8247 5 Tanya Street, Bromley, Christchurch, | Motovated Design & Analysis - Statement of Compliance - Seismic & Wind loads - 6245-1001, Vanguard Portaqube Tank Seismic & Wind Assessment, Rev00, 17Jun21 : - For an maximum Importance Level of 3, - For regions of New Zealand with a hazard factor of Z=0.42 (Upper Hutt) or less, - When anchored to a suitably designed foundation for at least the provided anchor loads, - When used to store diesel up to the safe fill level, Force per Anchor (min. 4 x per tank) Shear Tension VGR1000-2000L 10.9kN 19.6kN VGR3000-7000L 34.0kN 28.9kN Location of tanks stipulated by Health and Safety at Work (Hazardous Substances - Reduced Secondary Containment for Certain Above Ground Stationary Tanks) Safe Work Instrument 2017 This approval expires following any change to the referenced contents, design, duty, service, drawings or applicable standard | N/A | Prior to 17/06/2021: FAB0014/FAB0069 As of 17/06/2021: FAB0076 As of 19/03/2023 FAB0093 As of 11/04/2024 FAB0069 As of 02/04/2026: FAB0093
TNK13018 | 2010-08-19 | Service Engineers Ltd |  | AS 1692 - 2006, Category 5 | 4500L - 6000 L Single skin steel vertical cylindrical above-ground tanks for Firewater | Approved for storage and transfer of firewater with a hazard classification of 9.1B | Service Engineers Ltd | Subject to the conditions specified on the Test Certificate ST2028 | 2015-08-19 | FAB0011 - expired
TNK13019 | 2010-08-19 | Service Engineers Ltd |  | AS 1692 - 2006, Category 4 | 2500 L single skin steel horizontal cylindrical above-ground tank for recovered diesel | Approved for storage and transfer of diesel with a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Service Engineers Ltd | Subject to the conditions specified on the Test Certificate ST2029 | 2015-08-19 | FAB0011 - expired
TNK13020 | 2010-11-19 | Plastics Constructions Ltd 26 Fremlin Place Avondale Auckland |  | AS 2634 | 1500mm high x 1524mm diameter polypropylene above-ground tank for aluminium chloride | Approved for storage and transfer of aluminium chloride with a hazard classification of 6.1D, 8.1A, 8.2B, 8.3A, 9.1B & 9.3B | Plastics Construction Ltd | Subject to the conditions specified on the Test Certificate ST22258 | 2015-11-19 | FAB0035 - expired
TNK13021 | 2013-08-13 | 26 Fremlin Place |  | AS 1692-2006, Cat 3 / HSNOCOP 24-1,3/08 | 10,000 Litre double skin tank for diesel. | Approved for storage of diesel with a hazard classification of 3.1D and 3.1C only. | Fuel Storage Limited | Subject to the conditions of test certificate TC00518 | NA | FAB0050
TNK13022 | 2013-08-21 | Avondale |  | AS 1692-2006, Cat 3 / HSNOCOP 24-1,3/08 | 20,000 Litre double skin tank | Approved for storage of diesel with a hazard classification of 3.1D and 3.1C only. | Fuel Storage Limited | Subject to the conditions of test certificate TC00529 | NA | FAB0050
TNK13023 | 2013-09-05 | Auckland | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692-2006, Cat 4 / HSNOCOP 24-1,3/08 | 5,252 litre diesel double skin tank | Approved for storage of diesel with a hazard classification of 3.1D and 3.1C only. | Fuelcon Ltd | Subject to the conditions of test certificate TC00525 |  | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
TNK13024 | 2013-08-23 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS1692-2006, Cat 3 | 4,000 Litre Single compartment above ground double-walled diesel generator base storage tank 5000mm o/a length x 2200mm wide x 595mm high, 6mm Gr250 mild steel inner tank and double wall | Approved for storage of diesel with a hazard classification of 3.1D | Martin Engineering | Subject to the conditions of test certificate 2013079 | 2016-08-23 | FAB0045
TNK13025 | 2013-08-28 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS1692 – 2006, Category 4 HSNOCOP 24-1,3/08 constructed to UL2085 : 1997 | 70,000 Litre single compartment above ground Integral bunded diesel storage tank 2750mm dia. X 11.85m long x 6mm Gr250 mild steel shell, end and secondary containment. Multi hazard rated stationary tank - 2 hour constructed to UL2085: 1997 | Approved for storage of Class 3.1C or 3.1D Flammable liquids in accordance with HSNOCOP 24-1 March 2008 for use on a farm or isolated place or a bulk fuel storage and distribution site | Martin Engineering | Subject to the conditions of test certificate 2013090 | 2016-08-28 | FAB0045
TNK13026 | 2013-08-30 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS 1692 – 2006, Cat 3 | 25,000 Litre baffled single compartment aboveground double wall diesel storage tank 4690mm o/a length x 2291mm wide x 2608 mm high; 6mm Gr250 mild steel inner tank and double wall. | Approved for storage of Class 3.1D Flammable liquids | Martin Engineering | Subject to the conditions of test certificate 2013091 | 2016-08-30 | FAB0045
TNK13027 | 2013-09-09 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692-2006, Cat 4 / HSNOCOP 24-1,3/08 | Standard double skin tank design range 20,950 litres to 63,300 litres capacity | Approved for storage of diesel with a hazard classification of 3.1D and 3.1C only. | Fuelcon Ltd | Subject to the conditions of test certificate TC00539 |  | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
TNK13028 | 2013-08-08 | Armatec Environmental Ltd |  | AS 2634 | 8075l 2.0M DIA X 2.57M HI Vertical Cylindrical Fibre Reinforced Plastic Above-ground Tank for Sodium Hydroxide 30% | Approved for storage of Sodium Hydroxide 30% with a hazard classification of 6.1D,8.1A,8.2B,8.3A, 9.1D | Armatec Environmental Ltd for Stratford WTP | Subject to the conditions specified on the Test Certificate ST5447 | 2018-08-08 | FAB 0004 - Expired
TNK13029 | 2013-08-08 | Armatec Environmental Ltd |  | AS 2634 | 1898L 1.07m dia x 2.11m hi Vertical Cylindrical Fibre Reinforced Plastic above-Ground Tank for sodium Hydroxide 30%-50% | Approved for storage of Sodium Hydroxide 30%-50% with a hazard classification of 6.1D,8.1A,8.2B,8.3A, 9.1D | Armatec Environmental Ltd for Opunake WTP | Subject to the conditions specified on the Test Certificate ST5448 | 2018-08-08 | FAB 0004 - Expired
TNK13030 | 2012-09-05 | Armatec Environmental Ltd |  | AS 2634 & B S 4994 | 23,450L 2800mmNB x 4600mmH GRP Vertical cylindrical above-ground Tank for Sulphuric Acid 78% | Approved for storage of Sulphuric Acid 78% with a hazard classification of 6.1D, 6.1E, 6.7A, 6.9A, 8.1A,8.2B,8.3A, 9.1C, 9.1D | Armatec Environmental Ltd for Meadow Mushrooms Ltd | Subject to the conditions specified on the Test Certificate ST4174 | 2017-09-05 | FAB 0004 - Expired
TNK13031 | 2013-03-25 | Armatec Environmental Ltd |  | AS 2634 | 10,000L 2.41m dia x 2.71m hi Vertical Cylindrical Fibre Reinforced Plastic Above-ground Tank for Sodium Hypochlorite | Approved for storage of Sodium Hypochlorite with a hazard classification of 5.1.1B, 6.1E, 8.2C, 8.3A, 9.1A | Armatec Environmental Ltd for Marshall Projects Ltd & Taupo District Council WTP | Subject to the conditions specified on the Test Certificate ST4887 | 2018-03-24 | FAB 0004 - Expired
TNK13032 | 2013-03-25 | Armatec Environmental Ltd |  | AS 2634 | 12,750L 2.41m dia x 3.29m hi Vertical Cylindrical Fibre Reinforced Plastic Above-ground Tank for Sodium Hydroxide | Approved for storage of Sodium Hydroxide with a hazard classification of 6.1D,8.1A,8.2B,8.3A, 9.1D, 9.3C | Armatec Environmental Ltd for Marshall Projects Ltd & Taupo District Council WTP | Subject to the conditions specified on the Test Certificate ST5008 | 2018-03-24 | FAB 0004 - Expired
TNK13033 | 2013-03-25 | Armatec Environmental Ltd |  | AS 2634 | 60,000L 3.52m dia x 6.55m hi Vertical Cylindrical Fibre Reinforced Plastic Above-ground Tank for Mixed Effluent | Approved for storage of mixed effluent with a hazard classification of 6,8 & 9 | Armatec Environmental Ltd for Orica Chemnet, Mt Maunganui | Subject to the conditions specified on the Test Certificate ST5013 | 2018-03-24 | FAB 0004 - Expired
TNK13034 | 2013-01-07 | Plastics Constructions Ltd 26 Fremlin Place Avondale Auckland |  | HSNOCOP 56 | 2.43m hi x 2.4m id 11,000 Litre and 2.5m hi x 2.9m id 16,500 Litre Polyethylene Thermoplastic Above-ground Tanks for Soda Ash & Aluminium sulphate | Approved for storage of Soda Ash & Aluminium sulphate with a hazard classification of 6.1D, 6.1E, 6.3A, 6.4A, 8.1A, 9.1B, 9.3C | Plastics Constructions Ltd for Chemical Feed Solutions, Taumarunui | Subject to the conditions specified on the Test Certificate ST4610 | 2018-01-07 | FAB0035 - expired
TNK13035 | 2013-02-12 | Plastics Constructions Ltd 26 Fremlin Place Avondale Auckland |  | AS 2634 | 1.58m HI x 1m ID 1,100 Litre PVC-GRP above-ground tank for Sodium Hypochlorite | Approved for storage of Sodium Hypochlorite with a hazard classification of 8.2C, 8.3A, 9.1A | Plastics Constructions Ltd for Chemical Feed Solutions, Taumarunui | Subject to the conditions specified on the Test Certificate ST4703 | 2018-02-12 | FAB0035 - expired
TNK13036 | 2013-05-10 | Plastics Constructions Ltd 26 Fremlin Place Avondale Auckland |  | HSNOCOP 56 | 2900mm i.d. x 2500mm hi HDPE above-ground tank for Aluminium Sulphate | Approved for storage of Aluminium sulphate with a hazard classification of 6.1D, 6.1E, 6.3A, 6.4A, 8.1A, 9.1B, 9.3C | Plastics Constructions Ltd for Ngaruawahia Wastewater TP | Subject to the conditions specified on the Test Certificate ST5161 | 2018-05-09 | FAB0035 - expired
TNK13037 | 2013-04-08 | Direct Mechanical Services |  | AS 1692 | 1800L - 2500 L Double Skin Steel Rectangular Above-ground base Diesel Fuel Tanks for Generator Sets | Approved for storage of diesel with a hazard classification of 3.1D | Direct Mechanical Services | Subject to the conditions specified on the Test Certificate ST5047 | 2018-04-07 | Unsure of FAB number
TNK13038 | 2013-09-23 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS 1692-2006, Cat 4 / HSNOCOP 24-1,3/08 FAB0023 | 10,575L double skin tank | Approved for storage and transfer of automotive or low flashpoint diesel with a hazard classification of 3.1D or 3.1C | NYMIC Engineering, Christchurch | Subject to the conditions specified on the Test Certificate TC00546 | N/A | FAB0023
TNK13039 | 2013-09-23 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS 1692-2006, Cat 4 / HSNOCOP 24-1,3/08 FAB0023 | 28,513L double skin tank | Approved for storage and transfer of automotive or low flashpoint diesel with a hazard classification of 3.1D or 3.1C | NYMIC Engineering, Christchurch | Subject to the conditions specified on the Test Certificate TC00549 | N/A | FAB0023
TNK13040 | 2013-09-23 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS 1692-2006, Cat 4 / HSNOCOP 24-1,3/08 FAB0023 | 60,242L double skin tank | Approved for storage and transfer of automotive or low flashpoint diesel with a hazard classification of 3.1D or 3.1C | NYMIC Engineering, Christchurch | Subject to the conditions specified on the Test Certificate TC00551 | N/A | FAB0023
TNK13041 | 2013-08-20 | Service Engineers Ltd |  | API 650 | 1.906m i.d. x 1.9m hi 316 Stainless Steel Vertical Cylindrical 5000 L Above-ground Tank for sodium hydroxide > 5% aqueous solution | Approved for storage of sodium hydroxide > 5% aqueous solution with a hazard classification of 6.1D, 8.1A, 8.2B, 8.3A, 9.3B | Service Engineers Ltd for Eltham WTP | Subject to the conditions specified on the Test Certificate ST5488 | 2018-08-20 | FAB0011 - expired
TNK13042 | 2013-09-27 | Plastics Constructions Ltd 26 Fremlin Place Avondale Auckland |  | HSNOCOP 56 | 1500mm i.d. x 1900mm hi 3000L Above-ground tank for Hydrofluorosilicic Acid (HFA) | Approved for storage and transfer of Hydrofluorosilicic Acid (HFA) with a hazard classification of 6.1D, 8.1A, 8.2B, 8.3A | Plastics Constructions Ltd for Palmerston North WTP | Subject to the conditions specified on the Test Certificate ST5656 | 2018-09-27 | FAB0035 - expired
TNK13043 | 2013-10-25 | TP Engineering, Wiri, Auckland. |  | API650 Twelfth Edition, March 2013 | 68,200 litre aboveground mild steel grade 250 storage tank, 3800mm ID x 5850mm high 8mm bottom strake and 6mm second and upper strake. Flat floor 8mm mild steel grade 250 and 6mm mild steel grade 250 cone roof slope 15o | approved for filling with ACQ wood preservative UN No 2922 (s.g. 1.18 gm/cm3. ) to a maximum safe fill height of 5.427m. | TP Engineering | Subject to the conditions specified on the Test Certificate 2013118 |  | FAB0012 - expired
TNK13044 | 2013-12-08 | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692-2006, Cat. 4 / HSNOCOP 44 V1.1 | 2,500 to 6,000 L capacity 1450mm double skin underground fuel storage tank | Approved for storage of a single product with a hazard classification of 3.1A or 3.1B or 3.1C or 3.1D. | Petroleum Services (2001) Ltd | Subject to the conditions specified on the Test Certificate TC00574 | N/A | FAB0083 (FAB0016 prior to 9/06/2019)
TNK13045 | 2014-02-04 | Mercer Stainless Ltd Corbett Road, Bell Block, Taranaki |  | AS1692 -2006 Cat 5 | Vertical Cylindrical Aboveground 20,000 Litre single skin stainless steel tank | Sulphuric Acid Classes 6.1D,6.7A,6.9A, 8.1A,8.2B,8.3A,9.1D. | Mercer Stainless Ltd | Subject to the conditions specified on the Test Certificate 000001-STD1-14 | 2019-02-03 | Unsure of FAB number
TNK13046 | 2014-03-04 | LogiTank Pty Ltd | Zhangjiagang Logitank Heavy Industry Co. Ltd No.3, Hai Xin North Road, Zhangjiagang City, 215600 FAB0052 | AS 1692-2006 / HSNOCOP 24-1 | LogiTank Pty Ltd model LSK-10KL double skin above ground tank | Approved for storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petrotec Services Limited 12 Venture Place, Middleton, Christchurch, 8024 PO Box 10125, Philipstown, Christchurch, 8145 | Subject to the conditions specified on the Test Certificate TC00601 | N/A | FAB0052
TNK13047 | 2014-02-27 | Plastics Constructions Ltd 26 Fremlin Place Avondale Auckland | Plastics Constructions Ltd SCF3717REN | HSNOCOP 56 | 2900mm i.d. x 2500mm hi 16,500L HDPE Above-ground Tank for Polyaluminium Chloride (PACL) | Approved for storage of Polyaluminium Chloride (PACL) with a hazard classification of 6.1D, 6.3A, 6.4A | Rangitikei District Council - Taihape Water Treatment plant | Subject to the conditions specified on the Test Certificate ST6266 | 2019-02-27 | FAB0035 - expired
TNK13048 | 2014-02-28 | Plastics Constructions Ltd 26 Fremlin Place Avondale Auckland | Plastics Constructions Ltd SCF3717REN | HSNOCOP 56 & AS 2634 | 2500mm i.d. x 2040mm hi 11,000L Dual Laminate Above-ground Tanks (2) for Polyaluminium Chloride (PACL) | Approved for storage of Polyaluminium Chloride (PACL) with a hazard classification of 6.1D, 6.3A, 6.4A | South Taranaki District Council - Waimate West Water Treatment plant | Subject to the conditions specified on the Test Certificate ST6267 | 2019-02-28 | FAB0035 - expired
TNK13049 | 2014-02-28 | Plastics Constructions Ltd 26 Fremlin Place Avondale Auckland | Plastics Constructions Ltd SCF3717REN | HSNOCOP 56 & AS 2634 | 2500mm i.d. x 2650mm hi 14,300L Dual Laminate Above-ground Tank for Sodium Hydroxide 25-50% | Approved for storage of Sodium Hydroxide 25-50% with a hazard classification of 6.1D, 8.1A, 8.2B, 8.3A, 9.1D | South Taranaki District Council - Waimate West Water Treatment plant | Subject to the conditions specified on the Test Certificate ST6268 | 2019-02-28 | FAB0035 - expired
TNK13050 | 2014-01-29 | Garth Galloway | Galloway International Ltd. | HSNOCOP 61 FAB0051 | 5,000 Litres Above Ground Vertical Cylindrical Tank diameter 1830mm dia, 2335mm high, MDPE, rotationally moulded, fixed roof | Hazardous Substances Oxidising Agents and Aqueous solutions of 5.1.1A, 5.1.1B, 5.1.1C (subject to Special Conditions) Hazardous Substances Toxic and Aqueous solutions of 6.1A, 6.1B, 6.1C, 6.1D, 6.1E, 6.3A, 6.3B, 6.4A, 6.5A, 6.5B (subject to special conditions) Hazardous Substances Corrosives and Aqueous solutions of 8.1A, 8.2A, 8.2B, 8.2C, 8.3A General Ecotoxic Hazardous Substances and Aqueous Solutions of 9.1A, 9.1B, 9.1C, 9.1D, 9.2A, 9.2B, 9.2C, 9.2D, 9.3A, 9.3B, 9.3C, 9.4A, 9.4B, 9.4C (subject to special conditions) | Galloway International Ltd. | Subject to the conditions specified on the Test Certificate 100111-ADM14003 |  | FAB0051
TNK13051 | 2014-01-29 | Garth Galloway | Galloway International Ltd. | HSNOCOP 61 FAB0051 | 10,000 Litres Above Ground Vertical Cylindrical Tank diameter 2180mm dia, 2995mm high, MDPE, rotationally moulded, fixed roof | Hazardous Substances Oxidising Agents and Aqueous solutions of 5.1.1A, 5.1.1B, 5.1.1C (subject to Special Conditions) Hazardous Substances Toxic and Aqueous solutions of 6.1A, 6.1B, 6.1C, 6.1D, 6.1E, 6.3A, 6.3B, 6.4A, 6.5A, 6.5B (subject to special conditions) Hazardous Substances Corrosives and Aqueous solutions of 8.1A, 8.2A, 8.2B, 8.2C, 8.3A General Ecotoxic Hazardous Substances and Aqueous Solutions of 9.1A, 9.1B, 9.1C, 9.1D, 9.2A, 9.2B, 9.2C, 9.2D, 9.3A, 9.3B, 9.3C, 9.4A, 9.4B, 9.4C (subject to special conditions) | Galloway International Ltd. | Subject to the conditions specified on the Test Certificate 100111-ADM14004 |  | FAB0051
TNK13052 | 2014-01-29 | Garth Galloway | Galloway International Ltd. | HSNOCOP 61 FAB0051 | 16,000 Litres Above Ground Stationary Tank Vertical Cylindrical Tank diameter 3555mm dia, 2010mm high, MDPE, rotationally moulded, fixed roof | Hazardous Substances Oxidising Agents and Aqueous solutions of 5.1.1A, 5.1.1B, 5.1.1C (subject to Special Conditions) Hazardous Substances Toxic and Aqueous solutions of 6.1A, 6.1B, 6.1C, 6.1D, 6.1E, 6.3A, 6.3B, 6.4A, 6.5A, 6.5B (subject to special conditions) Hazardous Substances Corrosives and Aqueous solutions of 8.1A, 8.2A, 8.2B, 8.2C, 8.3A General Ecotoxic Hazardous Substances and Aqueous Solutions of 9.1A, 9.1B, 9.1C, 9.1D, 9.2A, 9.2B, 9.2C, 9.2D, 9.3A, 9.3B, 9.3C, 9.4A, 9.4B, 9.4C (subject to special conditions) | Galloway International Ltd. | Subject to the conditions specified on the Test Certificate 100111-ADM14005 |  | FAB0051
TNK13053 | 2014-01-29 | Garth Galloway | Galloway International Ltd. | HSNOCOP 61 FAB0051 | 25,000 Litres Above Ground Stationary Tank Vertical Cylindrical Tank diameter 3555mm dia, 2900mm high, MDPE, rotationally moulded, fixed roof | Hazardous Substances Oxidising Agents and Aqueous solutions of 5.1.1A, 5.1.1B, 5.1.1C (subject to Special Conditions) Hazardous Substances Toxic and Aqueous solutions of 6.1A, 6.1B, 6.1C, 6.1D, 6.1E, 6.3A, 6.3B, 6.4A, 6.5A, 6.5B (subject to special conditions) Hazardous Substances Corrosives and Aqueous solutions of 8.1A, 8.2A, 8.2B, 8.2C, 8.3A General Ecotoxic Hazardous Substances and Aqueous Solutions of 9.1A, 9.1B, 9.1C, 9.1D, 9.2A, 9.2B, 9.2C, 9.2D, 9.3A, 9.3B, 9.3C, 9.4A, 9.4B, 9.4C (subject to special conditions) | Galloway International Ltd. | Subject to the conditions specified on the Test Certificate 100111-ADM14006 |  | FAB0051
TNK13054 | 2014-03-26 | Plastics Constructions Ltd 26 Fremlin Place Avondale Auckland | Plastics Constructions Ltd SCF3717REN | HSNOCOP 56 & EN12573 | 13,750L 2300 mm i.d. x 3200 mm hi Single Skin HDPE Above-ground Tank for Polyamuminium Chloride (PACL) | Classifications: 6.1D, 6.3A, 6.4A | Plastics Constructions Ltd. | Subject to the conditions specified on the Test Certificate ST6351 | 2019-03-25 | FAB0035 - expired
TNK13055 | 2014-03-14 | Plastics Constructions Ltd 26 Fremlin Place Avondale Auckland | Plastics Constructions Ltd SCF3717REN | HSNOCOP 56 & EN12573 | 16,500L 2608 mm i.d. x 3200 mm hi Single Skin HDPE Above-ground Tank for Aluminium Sulphate | Classifications: 6.1D, 6.1E, 6.3A, 6.4A, 8.1A, 9.1B, 9.3C | Plastics Constructions Ltd. | Subject to the conditions specified on the Test Certificate ST6323 | 2019-03-13 | FAB0035 - expired
FAB0051 | 2014-04-01 | Garth Galloway | Galloway International Ltd. | AS/NZS 4766:2006 / HSNOCOP 61 | Up to 25,000 litres | Non flammable hazardous substances with class 5, 6, 8 & 9 classifications only | Galloway International Ltd. | Subject to the conditions specified on the Test Certificate TC00611 | 2017-03-31 | Fabricator of: TNK13050, TNK13051, TNK13052, TNK13053, TNK13060, TNK13061
TNK13056 | 2014-04-24 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS1692-2006, Category 3 / HSNOCOP 24-1, 3/08 FAB0023 | 5,308L Double Skin Tank | Storage and transfer of diesel Hazard Classification 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | NYMIC Engineering Ltd. | Subject to the conditions specified on the Test Certificate TC00617 | N/A | FAB0023
TNK13057 | 2014-05-08 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS1692, Category 4 FAB0047 | 5,529L Above Ground Bund Tanks | Storage and transfer of petrol Hazard Classification 3.1A, 6.1E, 6.3B, 6.7B, 9.1B | Fuelcon Limited, Palmerston North | Subject to the conditions specified on the Test Certificate TC00624 | N/A | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
TNK13058 | 2014-04-30 | Advanced Fuel Tanks NZ Limited PO Box 41 029 Christchurch | Advanced Fuel Tanks NZ Limited 5 Tanya St, Bromley, Christchurch FAB0014 | AS1692 – 2006, Category 3 | 15,000 litre single compartment aboveground Integral bunded diesel storage tank, 2.8 m. oal x 2.784 m. high x 2.438 m wide x 6 mm. Gr250 mild steel shell, end and secondary containment. AS1692 – 2006 Cat. 3 tank. | Storage of Class 3.1D flammable liquids | Advanced Fuel Tanks, Christchurch | Subject to the conditions specified on the Test Certificate 2013087 | 2019-04-29 | FAB0014
TNK13059 | 2014-05-08 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. | AS1692 – 2006, Category 4 FAB0045 | 5,000 litre single compartment aboveground Oil thinnings storage tank, 1.34 m. ID x 2.89 m. OAL x 6 mm. Gr250 mild steel shell and ends. | Storage of Class 3.1A-D flammable liquids | Martin Engineering (Palmerston North) Ltd. | Subject to the conditions specified on the Test Certificate 2014039 | 2019-05-07 | FAB0045
TNK13060 | 2014-05-07 | Garth Galloway | Galloway International Ltd. | HSNOCOP 61 FAB0051 | 3000 Litres Horizontal Cylindrical Tank Diameter 1400 mm x 2455 mm LOA, MDPE, rotationally moulded, turret, UNDERGROUND SERVICE | Hazardous Substances Oxidising Agents and Aqueous solutions of 5.1.1A, 5.1.1B, 5.1.1C Hazardous Substances Toxic and Aqueous solutions of 6.1A, 6.1B, 6.1C, 6.1D, 6.1E, 6.3A, 6.3B, 6.4A, 6.5A, 6.5B Hazardous Substances Corrosives and Aqueous solutions of 8.1A, 8.2A, 8.2B, 8.2C, 8.3A (subject to Special Conditions) General Ecotoxic Hazardous Substances and Aqueous Solutions of 9.1A, 9.1B, 9.1C, 9.1D, 9.2A, 9.2B, 9.2C, 9.2D, 9.3A, 9.3B, 9.3C, 9.4A, 9.4B, 9.4C (subject to special conditions) | Galloway International Ltd. | Subject to the conditions specified on the Test Certificate 100111-ADM14027 |  | FAB0051
TNK13061 | 2014-05-07 | Garth Galloway | Galloway International Ltd. | HSNOCOP 61 FAB0051 | 1900 Litres Horizontal Cylindrical Tank Diameter 1400 mm x 1420 mm LOA, MDPE, rotationally moulded, turret, UNDERGROUND SERVICE | Hazardous Substances Oxidising Agents and Aqueous solutions of 5.1.1A, 5.1.1B, 5.1.1C (subject to special conditions) Hazardous Substances Toxic and Aqueous solutions of 6.1A, 6.1B, 6.1C, 6.1D, 6.1E, 6.3A, 6.3B, 6.4A, 6.5A, 6.5B (subject to special conditions) Hazardous Substances Corrosives and Aqueous solutions of 8.1A, 8.2A, 8.2B, 8.2C, 8.3A (subject to Special Conditions) General Ecotoxic Hazardous Substances and Aqueous Solutions of 9.1A, 9.1B, 9.1C, 9.1D, 9.2A, 9.2B, 9.2C, 9.2D, 9.3A, 9.3B, 9.3C, 9.4A, 9.4B, 9.4C (subject to special conditions) | Galloway International Ltd. | Subject to the conditions specified on the Test Certificate 100111-ADM14026 |  | FAB0051
TNK13062 | 2014-04-24 | PK Engineering (Nelson) Ltd. | PK Engineering (Nelson) Ltd. | AS1692 – 2006, Category 3. FAB0027 | 100,000 litre single compartment baffled aboveground double wall internally stiffened diesel storage tank, 12 m long x 2.95 m wide x 2.95 m high. | Storage of Class 3.1D flammable liquids to a maximum safe fill height of 2.818 m. (ullage 4.7%) in accordance with Table 3.1 of HSNOCOP March 2008 for use on a bulk fuel storage and distribution site Design specification: AS1692 – 2006, Category 3. | PK Engineering (Nelson) Ltd. | Subject to the conditions specified on the Test Certificate 2014036 | 2019-04-23 | FAB0027
TNK13063 | 16/05/2014 14/07/2021 - Renewed | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS1692 – 2006, Category 2 | 795 L - Double skinned horizontal cylindrical above ground stationary tank Capacity: 820 litres Safe Fill Level: 795 litres | Name: Diesel only Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Martin Engineering (Palmerston North) Ltd. | 795 litre double wall single compartment aboveground diesel storage tank, Outer diameter 0.973m., Inner diameter 0.951m. Internal length 1154mm. Outside length 1220mm. Safe fill height 0.887mm. Inner and outer shells and ends 3 mm Gr 250 mild steel. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks is to be carried out under liquid and vapour tight connections. Statement of Design compliance: Wind and Seismic assessment has been carried out by Randall & Associates Certificate Number MS 43790.3 dated 27/03/2014: Tanks are to be installed in Regions A (1-7), B and C as per AS/NZS 1170.2 with a maximum wind speed of 80m/s and subsoil Class A, B, C and D in New Zealand as per NZS 1170.5. No changes are to be made to the manufacturers ratings. Mounting of structure to be periodically checked for security. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. Approved to supply a burner or engine. | N/A | FAB0045
TNK13064 | 16/05/2014 14/07/2021 - Renewed | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS1692 – 2006, Category 2 | 1000 L - Double skinned horizontal cylindrical above ground stationary tank Capacity: 1033 litre Safe Fill Level: 1000 litres | Name: Diesel only Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Martin Engineering (Palmerston North) Ltd. | 1000 litre double wall single compartment aboveground diesel storage tank, Outer diameter 0.973m., Inner diameter 0.951m. Internal length 1454mm. Outside length 1520mm. Safe fill height 0.883mm. Inner and outer shells and ends 3mm Gr 250 mild steel. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50 mm diameter vent is to terminate not less than 150 mm above the tank top. Filling and discharge of the tanks is to be carried out under liquid and vapour tight connections. Statement of Design compliance: Wind and Seismic assessment has been carried out by Randall & Associates Certificate Number MS 43790.3 dated 27/03/2014: Tanks are to be installed in Regions A (1-7), B and C as per AS/NZS 1170.2 with a maximum wind speed of 80m/s and subsoil Class A, B, C and D in New Zealand as per NZS 1170.5. No changes are to be made to the manufacturers ratings. Mounting of structure to be periodically checked for security. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. Approved to supply a burner or engine. | N/A | FAB0045
TNK13065 | 16/05/2014 14/07/2021 - Renewed | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS1692 – 2006, Category 2 | 1190 L - Double skinned horizontal cylindrical above ground stationary tank Capacity: 1232 litres Safe Fill Level: 1190 litres | Name: Diesel only Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Martin Engineering (Palmerston North) Ltd. | 1190 litre double wall single compartment aboveground diesel storage tank, Outer diameter 0.973m., Inner diameter 0.951m. Internal length 1734mm. Outside length 1800mm. Safe fill height 0.858mm. Inner and outer shells and ends 3mm Gr 250 mild steel. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks is to be carried out under liquid and vapour tight connections. Statement of Design compliance: Wind and Seismic assessment has been carried out by Randall & Associates Certificate Number MS 43790.3 dated 27/03/2014: Tanks are to be installed in Regions A (1-7), B and C as per AS/NZS 1170.2 with a maximum wind speed of 80m/s and subsoil Class A, B, C and D in New Zealand as per NZS 1170.5. No changes are to be made to the manufacturers ratings. Mounting of structure to be periodically checked for security. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. Approved to supply a burner or engine. | N/A | FAB0045
TNK13066 | 16/05/2014 14/07/2021 - Renewed | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS1692 – 2006, Category 2 | 2100 L - Double skinned horizontal cylindrical above ground stationary tank Capacity: 2175 litres Safe Fill Level: 2100 litres | Name: Diesel only Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Martin Engineering (Palmerston North) Ltd. | 2,050 litre double wall single compartment aboveground diesel storage tank, Outer diameter 1.402m., Inner diameter 1.380m. Internal length 1454mm. Outside length 1520mm. Safe fill height 1,233mm. Inner and outer shells and ends 3mm Gr 250 mild steel. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks is to be carried out under liquid and vapour tight connections. Statement of Design compliance: Wind and Seismic assessment has been carried out by Randall & Associates Certificate Number MS 43790.1 dated 27/03/2014: Tanks are to be installed in Regions A (1-7), B and C as per AS/NZS 1170.2 with a maximum wind speed of 80m/s and subsoil Class A, B, C and D in New Zealand as per NZS 1170.5. No changes are to be made to the manufacturers ratings. Mounting of structure to be periodically checked for security. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. Approved to supply a burner or engine. | N/A | FAB0045
TNK13067 | 16/05/2014 14/07/2021 - Renewed | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS1692 – 2006, Category 2 | 2500 L - Double skinned horizontal cylindrical above ground stationary tank Capacity: 2594 litres Safe Fill Level: 2500 litres | Name: Diesel only Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Martin Engineering (Palmerston North) Ltd. | 2,500 litre double wall single compartment aboveground diesel storage tank, Outer diameter 1.402m., Inner diameter 1.380m. Internal length 1734mm. Outside length 1800mm. Safe fill height 1,273mm. Inner and outer shells and ends 3mm Gr 250 mild steel. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks is to be carried out under liquid and vapour tight connections. Statement of Design compliance: Wind and Seismic assessment has been carried out by Randall & Associates Certificate Number MS 43790.1 dated 27/03/2014: Tanks are to be installed in Regions A (1-7), B and C as per AS/NZS 1170.2 with a maximum wind speed of 80m/s and subsoil Class A, B, C and D in New Zealand as per NZS 1170.5. No changes are to be made to the manufacturers ratings. Mounting of structure to be periodically checked for security. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. Approved to supply a burner or engine. | N/A | FAB0045
FAB0052 | 2014-05-29 | LogiTank Pty Ltd | Prior to 12/12/2023 Zhangjiagang Logitank Heavy Industry Co. Ltd As of 12/12/2023 Zhangjiagang Fuel Equipment Systems Company. Ltd Trading as FES 3 Hai Xin North Road, Nanfeng Town, Zhangjiagang City, Jiangsu Province P.R. China, 215600 | AS 1692 - 2006, Category 3 | Capacity: Up to 110,000 L Manufacture of approved tank designs: TNK11033, TNK11034, TNK11035, TNK11036, TNK11037, TNK11038, TNK13007, TNK13008, TNK13009, TNK13046, TNK15022, TNK16014, TNK16026, TNK16027, TNK18012, TNK20039, TNK20041, TNK20042, TNK20043, TNK20044, TNK20045, TNK20046, TNK20047, TNK20048, TNK20049, TNK20463 | Storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petrotec Services Limited 12 Venture Place, Middleton, Christchurch, 8024 PO Box 10125, Philipstown, Christchurch, 8145 | Fabrication, inspection and testing in accordance with the specified tank design code, approved tank design drawings, approved for construction drawings and approved internal QA procedures. Allocation of individual tank serial numbers. Retention of individual tank QA records. | 2026-12-12 | Fabricator of: TNK11033, TNK11034, TNK11035, TNK11036, TNK11037, TNK11038, TNK13007, TNK13008, TNK13009, TNK13046, TNK15022, TNK16014, TNK16026, TNK16027, TNK18012, TNK20039, TNK20041, TNK20042, TNK20043, TNK20044, TNK20045, TNK20046, TNK20047, TNK20048, TNK20049, TNK20463
FAB0053 | 2014-07-02 |  | Western Global UK | AS 1692 - 2006, Category 3 / HSNOCOP 24-1 | Capacity: up to 60,000 litres Reference: TAN09062, TAN09065, TAN10018, TAN11043, TAN10019, TAN11042, TAN09063, TAN09066, TAN09064, TAN09067, TAN15085 TNK10023, TNK10024, TNK11004, TNK11005, TNK11007, TNK11029, TNK12001, TNK12022, TNK15024, TNK15025, TNK15027, TNK16005, TNK16006. | Storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Civilquip 8-10 Chesterfield St, Greymouth | Subject to the conditions specified on the Test Certificate TC00647 | 2017-07-02 | Fabricator of: TNK10023, TNK10024, TNK11004, TNK11005, TNK11007, TNK11029, TNK12001, TNK12022, TNK15024, TNK15025, TNK15027, TNK16005, TNK16006. Fabricator of Tankwagons: TAN09062, TAN09065, TAN10018, TAN11043, TAN10019, TAN11042, TAN09063, TAN09066, TAN09064, TAN09067, TAN15085.
TNK13068 | 16/05/2014 14/07/2021 - Renewed | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS1692 – 2006, Category 2 | 1150 L - Double skinned horizontal cylindrical above ground stationary tank Capacity: 1188 litres Safe Fill Level: 1150 litres | Name: Diesel only Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Martin Engineering (Palmerston North) Ltd. | 1,150 litre double wall single compartment aboveground diesel storage tank, Outer diameter 1.167m., Inner diameter 1.145m. Internal length 1154mm. Outside length 1220mm. Safe fill height 0.887mm. Inner and outer shells and ends 3mm Gr 250 mild steel. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks is to be carried out under liquid and vapour tight connections. Statement of Design compliance: Wind and Seismic assessment has been carried out by Randall & Associates Certificate Number MS 43790.2 dated 27/03/2014: Tanks are to be installed in Regions A (1-7), B and C as per AS/NZS 1170.2 with a maximum wind speed of 80m/s and subsoil Class A, B, C and D in New Zealand as per NZS 1170.5. No changes are to be made to the manufacturers ratings. Mounting of structure to be periodically checked for security. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. Approved to supply a burner or engine. | N/A | FAB0045
TNK13069 | 16/05/2014 14/07/2021 - Renewed | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS1692 – 2006, Category 2 | 1450 L - Double skinned horizontal cylindrical above ground stationary tank Capacity: 1497 litres Safe Fill Level: 1450 litres | Name: Diesel only Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Martin Engineering (Palmerston North) Ltd. | 1,400 litre double wall single compartment aboveground diesel storage tank, Outer diameter 1.167m., Inner diameter 1.145m. Internal length 1454mm. Outside length 1520mm. Safe fill height 0.883mm. Inner and outer shells and ends 3mm Gr 250 mild steel. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks is to be carried out under liquid and vapour tight connections. Statement of Design compliance: Wind and Seismic assessment has been carried out by Randall & Associates Certificate Number MS 43790.2 dated 27/03/2014: Tanks are to be installed in Regions A (1-7), B and C as per AS/NZS 1170.2 with a maximum wind speed of 80m/s and subsoil Class A, B, C and D in New Zealand as per NZS 1170.5. No changes are to be made to the manufacturers ratings. Mounting of structure to be periodically checked for security. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. Approved to supply a burner or engine. | N/A | FAB0045
TNK13070 | 16/05/2014 14/07/2021 - Renewed | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS1692 – 2006, Category 2 | 1700 L - Double skinned horizontal cylindrical above ground stationary tank Capacity: 1785 litres Safe Fill Level: 1700 litres | Name: Diesel only Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Martin Engineering (Palmerston North) Ltd. | 1,700 litre double wall single compartment aboveground diesel storage tank, Outer diameter 1.167m., Inner diameter 1.145m. Internal length 1734mm. Outside length 1800mm. Safe fill height 0.858mm. Inner and outer shells and ends 3mm Gr 250 mild steel. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 2, test pressure in Kpa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks is to be carried out under liquid and vapour tight connections Statement of Design compliance: Wind and Seismic assessment has been carried out by Randall & Associates Certificate Number MS 43790.2 dated 27/03/2014: Tanks are to be installed in Regions A (1-7), B and C as per AS/NZS 1170.2 with a maximum wind speed of 80m/s and subsoil Class A, B, C and D in New Zealand as per NZS 1170.5. No changes are to be made to the manufacturers ratings. Mounting of structure to be periodically checked for security. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. Approved to supply a burner or engine. | N/A | FAB0045
TNK13071 | 16/05/2014 14/07/2021 - Renewed | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS1692 – 2006, Category 4 | 2972 L - Double skinned horizontal cylindrical above ground stationary tank Capacity: 3064 litres Safe Fill Level: 2972 litres | Name: Diesel only Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Martin Engineering (Palmerston North) Ltd. | 2,950 litre double wall single compartment aboveground diesel storage tank, Outer diameter 1.522m., Inner diameter 1.500m. Internal length 1734mm. Outside length 1800mm. Safe fill height 1,383mm. Inner and outer shells and ends 3mm Gr 250 mild steel. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 4, test pressure in Kpa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks is to be carried out under liquid and vapour tight connections. Statement of Design compliance: Wind and Seismic assessment has been carried out by Randall & Associates Certificate Number MS 43790 dated 27/03/2014: Tanks are to be installed in Regions A (1-7), B and C as per AS/NZS 1170.2 with a maximum wind speed of 80m/s and subsoil Class A, B, C and D in New Zealand as per NZS 1170.5. No changes are to be made to the manufacturers ratings. Mounting of structure to be periodically checked for security. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. Approved to supply a burner or engine. | N/A | FAB0045
TNK13072 | 16/05/2014 14/07/2021 - Renewed | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS1692 – 2006, Category 4 | 4000 L - Double skinned horizontal cylindrical above ground stationary tank Capacity: 4125 litres Safe Fill Level: 4000 litres | Name: Diesel only Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Martin Engineering (Palmerston North) Ltd. | 4,000 litre double wall single compartment aboveground diesel storage tank, Outer diameter 1.522m., Inner diameter 1.500m. Internal length 2334mm. Outside length 2400mm. Safe fill height 1,397mm. Inner and outer shells and ends 3mm Gr 250 mild steel. The TNK register number is to be marked on the tank nameplate in addition to the Manufacturers serial number, date of manufacture / pressure test, AS1692-2006 category 4, test pressure in Kpa and safe fill height in mm. All other markings to comply with the Hazardous Substances Regulations. The 50mm diameter vent is to terminate not less than 150mm above the tank top. Filling and discharge of the tanks is to be carried out under liquid and vapour tight connections. Statement of Design compliance: Wind and Seismic assessment has been carried out by Randall & Associates Certificate Number MS 43790 dated 27/03/2014: Tanks are to be installed in Regions A (1-7), B and C as per AS/NZS 1170.2 with a maximum wind speed of 80m/s and subsoil Class A, B, C and D in New Zealand as per NZS 1170.5. No changes are to be made to the manufacturers ratings. Mounting of structure to be periodically checked for security. Re-certification required following any change to the referenced contents, design, duty, service, drawings or applicable standards. Approved to supply a burner or engine. | N/A | FAB0045
TNK13073 | 2014-05-19 | Service Engineers Ltd | Service Engineers Ltd | AS1692 Category 4 Approved fabricator No. FAB0011 | 17,000L Single skin steel horizontal cylindrical above-ground tank for firefighting chemicals (Group Standard 2006, HSR002573) | Classifications 6.9B | Methanex Omata Site, New Plymouth | Subject to the conditions specified on the Test Certificate ST6590 | 2019-05-19 | FAB0011 - expired
TNK13074 | 2014-07-09 | Cranrock Oilfield Services Limited | Cranrock Oilfield Services Limited | AS 1692-2006, Category 5 FAB0054 | Capacity: 63,646 litres | Storage and transfer of Crude or Condensate having a Hazard Classification of 3.1A, 6.1E, 6.3B, 6.7B, 9.1 | Cranrock Oilfield Services Limited | Subject to the conditions specified on the Test Certificate TC00650 |  | FAB0054
FAB0054 | 2014-07-09 | Cranrock Oilfield Services Limited | Cranrock Oilfield Services Limited | AS 1692-2006, Category 5 TNK13074 | Capacity: 63,646 litres | Storage and transfer of Crude or Condensate having a Hazard Classification of 3.1A, 6.1E, 6.3B, 6.7B, 9.1 | Cranrock Oilfield Services Limited | Subject to the conditions specified on the Test Certificate TC00660 | 2017-07-09 | Fabricator of: TNK13074
TNK13075 | 2014-08-19 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS 1692 - 2006, Category 4 FAB0023 | 9,690 Litre Single Skin Tank | The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | NYMIC Engineering Ltd | Subject to the conditions specified on the Test Certificate TC00683. The Test Certificate becomes invalid following any change to the approved drawing. | N/A | FAB0023
TNK13076 | 2014-10-13 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS 1692-2006, Cat 3 / HSNOCOP 24-2, 7/14 FAB0023 | 44,114 litre double Skin Tank | The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | NYMIC Engineering Ltd | Subject to the conditions specified on the Test Certificate TC00741. The Test Certificate becomes invalid following any change to the approved drawing. | N/A | FAB0023
TNK13077 | 2014-10-29 | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu 3840 |  | AS 1692-2006, Cat. 3 / HSNOCOP 24-1, 3/08 FAB0050 | 3,106 litre double skin tank to supply a burner or generator. | The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuel Storage Limited | Subject to the conditions specified on the Test Certificate TC00747. Tank to supply a burner or generator. The Test Certificate becomes invalid following any change to the approved drawings. | NA | FAB0050
TNK13078 | 2014-12-02 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692 - 2006, Category 4 | 3,493 litre single skin tank for petrol (3.1A) | The storage and transfer of petrol having a hazard classification of 3.1A, 6.1E, 6.3B, 6.7B, 9.1B | Fuelcon Limited, Palmerston North | Subject to the conditions specified on the Test Certificate TC00790 The Test Certificate becomes invalid following any change to the approved Fuelcon design and drawing. | Unless surrendered or revoked, Test Certificate TC00790 remains valid for the service life of the tank. | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
TNK13079 | 2014-12-15 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | Prior to 31 July 2019: AS1692 – 2006, Category 4 As of 31 July 2019: AS1692 – 2006, Category 4 & Reduced Secondary Containment Safe Work Instrument 2017 (Impact Protected) | 60,000 litre double skin fuel tank | Prior to 31 July 2019: The storage of Class 3.1D flammable liquids As of 31 July 2019: Flammable liquids having hazard classifications of 3.1A, 3.1B, 3.1C or 3.1D | Martin Engineering (Palmerston North) Ltd. | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. Impact & projectile tested in accordance with UL2085, Clauses 20 & 21. Tank specific vent design required. Randall & Associates Wind & Seismic Design Compliance Certificate MS 45498. Allocation of unique serial number for each tank and retention of fabrication & testing records. | 2024-07-31 | FAB0045
TNK13080 | 2014-12-15 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | Prior to 5 August 2019: AS1692 – 2006, Category 4 As of 5 August 2019: AS1692 – 2006, Category 4 & Reduced Secondary Containment Safe Work Instrument 2017 (Impact Protected) | 70,000 litre double skin single compartment aboveground tank | Prior to 5 August 2019: The storage of Class 3.1D flammable liquids As of 5 August 2019: Flammable liquids having hazard classifications of 3.1A, 3.1B, 3.1C or 3.1D | Martin Engineering (Palmerston North) Ltd. | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. Impact & projectile tested in accordance with UL2085, Clauses 20 & 21. Tank specific vent design required. Randall & Associates Wind & Seismic Design Compliance Certificate MS 45498. Allocation of unique serial number for each tank and retention of fabrication & testing records. | 2024-08-05 | FAB0045
TNK13081 | 2014-12-15 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | Prior to 5 August 2019: AS1692 – 2006, Category 4 As of 5 August 2019: AS1692 – 2006, Category 4 & Reduced Secondary Containment Safe Work Instrument 2017 (Impact Protected) | 80,000 litre double skin single compartment aboveground tank | Prior to 5 August 2019: The storage of Class 3.1D flammable liquids As of 5 August 2019: Flammable liquids having hazard classifications of 3.1A, 3.1B, 3.1C or 3.1D | Martin Engineering (Palmerston North) Ltd. | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. Impact & projectile tested in accordance with UL2085, Clauses 20 & 21. Tank specific vent design required. Randall & Associates Wind & Seismic Design Compliance Certificate MS 45498. Allocation of unique serial number for each tank and retention of fabrication & testing records. | 2024-08-05 | FAB0045
TNK13082 | 2014-12-15 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | Prior to 5 August 2019: AS1692 – 2006, Category 4 As of 5 August 2019: AS1692 – 2006, Category 4 & Reduced Secondary Containment Safe Work Instrument 2017 (Impact Protected) | 94,000 litre double skin single compartment aboveground tank | Prior to 5 August 2019: The storage of Class 3.1D flammable liquids As of 5 August 2019: Flammable liquids having hazard classifications of 3.1A, 3.1B, 3.1C or 3.1D | Martin Engineering (Palmerston North) Ltd. | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. Impact & projectile tested in accordance with UL2085, Clauses 20 & 21. Tank specific vent design required. Randall & Associates Wind & Seismic Design Compliance Certificate MS 45498. Allocation of unique serial number for each tank and retention of fabrication & testing records. | 2024-08-05 | FAB0045
TNK13083 | 2014-12-15 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | Prior to 5 August 2019: AS1692 – 2006, Category 4 As of 5 August 2019: AS1692 – 2006, Category 4 & Reduced Secondary Containment Safe Work Instrument 2017 (Impact Protected) | 100,000 litre double skin single compartment aboveground tank | Prior to 5 August 2019: The storage of Class 3.1D flammable liquids As of 5 August 2019: Flammable liquids having hazard classifications of 3.1A, 3.1B, 3.1C or 3.1D | Martin Engineering (Palmerston North) Ltd. | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. Impact & projectile tested in accordance with UL2085, Clauses 20 & 21. Tank specific vent design required. Randall & Associates Wind & Seismic Design Compliance Certificate MS 45498. Allocation of unique serial number for each tank and retention of fabrication & testing records. | 2024-08-05 | FAB0045
TNK13084 | 2014-12-15 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | Prior to 5 August 2019: AS1692 – 2006, Category 4 As of 5 August 2019: AS1692 – 2006, Category 4 & Reduced Secondary Containment Safe Work Instrument 2017 (Impact Protected) | 107,500 litre double skin single compartment aboveground tank. | Prior to 5 August 2019: The storage of Class 3.1D flammable liquids As of 5 August 2019: Flammable liquids having hazard classifications of 3.1A, 3.1B, 3.1C or 3.1D | Martin Engineering (Palmerston North) Ltd. | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. Impact & projectile tested in accordance with UL2085, Clauses 20 & 21. Tank specific vent design required. Randall & Associates Wind & Seismic Design Compliance Certificate MS 45498. Allocation of unique serial number for each tank and retention of fabrication & testing records. | 2024-08-01 | FAB0045
FAB0055 | 2015-07-07 | Superior Stainless 4 Mustang Drive Bell Block New Plymouth | Superior Stainless 4 Mustang Drive Bell Block New Plymouth |  | Type: Transportable container Capacity: Up to 1,500 L UN Model Regulations Tank Code 31A | Classes 3.1A to 3.1D hazardous substances | Superior Stainless Limited | In addition to the conditions specified on Test Certificate TC00822, the following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the fabricator for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2018-07-06 | Fabricator of Tankwagons: TAN15048
TNK13085 | 2015-02-16 | TransTank, Western Global (Australia) | TransTank, Western Global (Australia) |  | 30,208 L SFL Horizontal above ground tank with integral secondary containment TRANSTANK P31 | Diesel UN30802; 3.1D Design specification: AS 1692 | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley Christchurch 8062 | Subject to the conditions specified on the Test Certificate 100111-ADM15023A | 2018-02-15
FAB0056 | 2015-02-12 | All Purpose Engineering Ltd. | All Purpose Engineering Ltd. | TAN12023 TAN13061 TAN14003 TAN14108 TAN17129 | TAN12023 - double wall steel 1360 litre diesel trailer tank TAN13061 - double wall steel 1360 litre diesel trailer tank TAN14003 - double wall steel 1360 litre diesel trailer tank TAN14108 - double wall aluminium 1950 litre avgas trailer tank TAN17129 - 1360 litre single compartment diesel trailer tank | TAN12023 Transportation of class 3.1D flammable liquids TAN13061 The transportation of class 3.1D flammable liquids TAN14003 Flammable Liquids Tankwagon Code Appendix B TAN14108 Transportation of Class 3.1 C Jet A1 TAN17129 Transportation of class 3.1D flammable liquids | All Purpose Engineering Ltd. | In addition to the conditions specified on Test Certificate 2014129 Rev A, the following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the fabricator for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2018-02-12 | Fabricator of Tankwagons: TAN12023, TAN13061, TAN14003, TAN14108, TAN17129
TNK13086 | 2015-02-20 | PK Engineering (Nelson) Ltd. | PK Engineering (Nelson) Ltd. | AS1692 – 2006, Class 3. | 40,000 litre double wall single compartment aboveground diesel storage tank, Height 2,810 mm, Width 2,950 mm, Inside length 6,288 mm. Safe fill height 2,284 mm. (From tank floor). Inner and outer shells and ends 6 mm Gr 250 mild steel. | The storage of Class 3.1D flammable liquids | PK Engineering (Nelson) Ltd. | Subject to the conditions specified on the Test Certificate 2014089 | This design approval is valid for a period of 5 years | FAB0027
TNK13087 | 2015-02-20 | PK Engineering (Nelson) Ltd. | PK Engineering (Nelson) Ltd. | AS1692 – 2006, Class 3. | 50,000 litre double wall single compartment aboveground diesel storage tank, Height 2,810 mm, Width 2,950 mm, Inside length 7,788 mm. Safe fill height 2,305 mm. (From tank floor). Inner and outer shells and ends 6 mm Gr 250 mild steel. | The storage of Class 3.1D flammable liquids | PK Engineering (Nelson) Ltd. | Subject to the conditions specified on the Test Certificate 2014089 | This design approval is valid for a period of 5 years | FAB0027
TNK13088 | 2015-02-20 | PK Engineering (Nelson) Ltd. | PK Engineering (Nelson) Ltd. | AS1692 – 2006, Class 3. | 60,000 litre double wall single compartment aboveground diesel storage tank, Height 2,810 mm, Width 2,950 mm, Inside length 9,488 mm. Safe fill height 2,270 mm. (From tank floor). Inner and outer shells and ends 6 mm Gr 250 mild steel. | The storage of Class 3.1D flammable liquids | PK Engineering (Nelson) Ltd. | Subject to the conditions specified on the Test Certificate 2014089 | This design approval is valid for a period of 5 years | FAB0027
TNK13089 | 2015-02-20 | PK Engineering (Nelson) Ltd. | PK Engineering (Nelson) Ltd. | AS1692 – 2006, Class 3. | 70,000 litre double wall single compartment aboveground diesel storage tank, Height 3,390 mm, Width 3,100 mm, Inside length 8,538 mm. Safe fill height 2,791 mm. (From tank floor). Inner and outer shells and ends 6 mm Gr 250 mild steel. | The storage of Class 3.1D flammable liquids | PK Engineering (Nelson) Ltd. | Subject to the conditions specified on the Test Certificate 2014089 | This design approval is valid for a period of 5 years | FAB0027
TNK13090 | 2015-02-20 | PK Engineering (Nelson) Ltd. | PK Engineering (Nelson) Ltd. | AS1692 – 2006, Class 3. | 80,000 litre double wall single compartment aboveground diesel storage tank, Height 3,390 mm, Width 3,100 mm, Inside length 9,738 mm. Safe fill height 2,800 mm. (From tank floor). Inner and outer shells and ends 6 mm Gr 250 mild steel. | The storage of Class 3.1D flammable liquids | PK Engineering (Nelson) Ltd. | Subject to the conditions specified on the Test Certificate 2014089 | This design approval is valid for a period of 5 years | FAB0027
TNK13091 | 2015-02-20 | PK Engineering (Nelson) Ltd. | PK Engineering (Nelson) Ltd. | AS1692 – 2006, Class 3. | 90,000 litre double wall single compartment aboveground diesel storage tank, Height 3,390 mm, Width 3,100 mm, Inside length 10,988 mm. Safe fill height 2,790 mm. (From tank floor). Inner and outer shells and ends 6 mm Gr 250 mild steel. | The storage of Class 3.1D flammable liquids | PK Engineering (Nelson) Ltd. | Subject to the conditions specified on the Test Certificate 2014089 | This design approval is valid for a period of 5 years | FAB0027
TNK13092 | 2015-03-13 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. | AS1692 – 2006, Category 4. | 2,000 litre double wall single compartment underground diesel storage tank, Outer diameter 1.374 m., Inner diameter 1.335 m. Internal length 1488 mm. Outside length 1602 mm. Safe fill height 1,224 mm. Inner and outer shells and ends 6 mm Gr 250 mild steel. | The storage of Class 3.1D flammable liquids | Martin Engineering (Palmerston North) Ltd. | Subject to the conditions specified on the Test Certificate 2015028 | This design approval is valid for a period of 5 years
TNK13093 | 2015-04-16 | Polymaster Industrial (Australia) Ltd. | Polymaster Industrial (Australia) Ltd. | FAB0062 Design specification: HSNOCOP 61 | 1,500 litre rotationally moulded PE storage tank contained within secondary containment bund. Aboveground chemical storage tank, 1,703 mm overall height, 1106 mm wide, 1106 mm deep. PE moulded sides 10 mm thick at bottom knuckle radius tapering on linear basis to 6 mm at top of sides. Base thickness 10 mm, top thickness 6 mm. Material : Qenos LL711UV. | Classes 5, 6, 8 and 9 substances | Polymaster Industrial (Australia) Ltd. | Subject to the conditions specified on the Test Certificate 2014079 | This design approval is valid for a period of 5 years | FAB0062
TNK15001 | 2014-09-22 | Fuelchief Limited 5 Tanya Street Bromley, Christchurch 8062 (formally Advanced Fuel Tanks NZ Limited prior to 27 May 2019) | Fuelchief Limited 5 Tanya Street Bromley, Christchurch 8062 FAB0076 (FAB0014/FAB0069 by Advanced Fuel Tanks NZ Limited prior to 27 May 2019) As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | Prior to 22 September 2017: AS1692 – 2006 As of 17 December 2019: AS1692 – 2006, Category 4 & Reduced Secondary Containment Safe Work Instrument 2017 (Impact Protected) | Vanguard Portaqube rectangular above ground tanks 10,370 L and 12,371 L Safe Fill Level: 10,000 litres and 12,000 litres | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B Octone booster having a hazardous classification of 3.1D, 6.1C, 6.9B, 9.1A, 9.3B | Fuelchief Limited 5 Tanya Street Bromley, Christchurch 8062 | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | 2029-12-17 | FAB0076 (Fuelchief Limited) (FAB0014/FAB0069 by Advanced Fuel Tanks NZ Limited prior to 27 May 2019) As of 19/03/2023 FAB0093 As of 11/04/2024 FAB0069 As of 02/04/2026: FAB0093
TNK15002 | 2013-12-19 | Carterpillar (NI) Ltd. 370 Doagh Road, Newtown Abbey, Monkstown, Belfast, United Kingdom | Carterpillar (NI) Ltd. 370 Doagh Road, Newtown Abbey, Monkstown, Belfast, United Kingdom | FAB0057 Design specification: BS 799-5:2010 & HSNOCOP 60 | 850 L single skin steel, rectangular above-ground generator base tank | Classes 3.1D, 6.3B, 6.7B and 9.1B substances | Carterpillar (NI) Ltd. 370 Doagh Road, Newtown Abbey, Monkstown, Belfast, United Kingdom | Subject to the conditions specified on the Test Certificate ST6111 | This design approval is valid for a period of 5 years | FAB0057
FAB0057 | 2015-05-20 |  | Carterpillar (NI) Ltd. 370 Doagh Road, Newtown Abbey, Monkstown, Belfast, United Kingdom | Design specification: BS 799-5:2010 & HSNOCOP 60 | 850 L single skin steel, rectangular above-ground generator base tank Reference: TNK15002 | Classes 3.1D, 6.3B, 6.7B and 9.1B substances |  | Subject to the conditions specified on the Test Certificate SCF8068 | 2018-05-19 | Fabricator of: TNK15002
TNK15003 | 2015-07-10 | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | FAB0016 AS 1692 - 2006, Category 4 | 4,900 L horizontal, above ground single skin tank design for petrol (3.1A) | Approved for storage and transfer of petrol having a hazard classification of 3.1A, 6.1E, 6.3B, 6.7B, 9.1B | Petroleum Services (2001) Ltd | Subject to the conditions specified on the Test Certificate TC00885 | N/A | FAB0083 (FAB0016 prior to 9/06/2019)
TNK15004 | 2015-08-03 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 17/10/2023: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 06 326 8826 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | FAB0047 Design Specification: AS 1692-2006 | Capacity: 13,553 litres Tank serial number: Name Plate Tank Design: AS 1692 - 2006, Category 4 Manufacture Year: Name Plate | The storage and transfer of petrol having a hazard classification of 3.1A, 6.1E, 6.3B, 6.7B, 9.1B | Fuelcon Limited 84B Armstrong Street P O Box 9031 Palmerston North Ph 06 326 8826 | Subject to the conditions specified on the Test Certificate TC00899 | N/A | Prior to 17/10/2023: FAB0047 As of 17/10/2023: FAB0096
TNK15005 | 2015-07-20 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | FAB0023 AS 1692-2006, Cat 3 / HSNOCOP 24-2, 7/14 | 11,100 litre double skin tank design for diesel (3.1D) only | The storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | NYMIC Engineering Ltd | Subject to the conditions specified on the Test Certificate TC00895 | N/A | FAB0023
TNK15006 | 2015-07-21 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | FAB0023 AS 1692-2006, Category 4 | 32,572 litre single skin above ground horizontal tank design. | Approved for storage and transfer of flammable liquids having hazard classifications of 3.1A, 3.1B, 3.1C, 3.1D, 6.1E, 6.3B, 6.7B, 6.8B, 9.1B, 9.1C | NYMIC Engineering Ltd. | Subject to the conditions specified on the Test Certificate TC00897 | N/A | FAB0023
FAB0058 | 2015-08-13 | BVT Consulting | Hubei Heli Special Automobile Manufacture Co Ltd. | AS 1692 and HSNOCOP 24. | 5,000, 10,000 & 30,000 litre double skin tanks Reference: TNK13056, TNK13038 & TNK13039 (China) | Diesel 3.1D only | PP Warner Ltd, 189 Waterloo Road, Hornby, Christchurch | In addition to the conditions specified on Test Certificate TC00920, the following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2018-08-12 | Fabricator of: TNK13056, TNK13038 & TNK13039 (China) | 126/83
FAB0059 | 2015-08-13 | BVT Consulting | Qingdao Xinguangzheng Group | AS 1692 and HSNOCOP 24. | 5,000, 10,000 & 30,000 litre double skin tanks Reference: TNK13056, TNK13038 & TNK13039 (China) | Diesel 3.1D only | PP Warner Ltd, 189 Waterloo Road, Hornby, Christchurch | In addition to the conditions specified on Test Certificate TC00921, the following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2018-08-12 | Fabricator of: TNK13056, TNK13038, TNK13039
TNK15007 | 2015-07-04 | Stainless Engineering Co Ltd. | NA | Design specification: AS 1692 | 2,000 L above ground stationary tank. S/N 9174-A Vertical Cylindrical tank 316 SS. 1644 mm diameter by 1220 mm high. | Storage of Classes 6.1C, 6.5A, 6.5B, 6.9B, 8.1A, 8.2B, 8.3A, 9.1A,9.3C substances | Contact Energy Oruani Road Te Mihi Power Station Waikarei | Subject to the conditions specified on the Test Certificate 100111-ADM15129
TNK15008 | 2015-07-04 | Stainless Engineering Co Ltd. | NA | Design specification: AS 1692 | 2,000 L above ground stationary tank. S/N 9174-B Vertical Cylindrical tank 316 SS. 1644 mm diameter by 1220 mm high. | Storage of Classes 6.1C, 6.5A, 6.5B, 6.9B, 8.1A, 8.2B, 8.3A, 9.1A,9.3C substances | Contact Energy Oruani Road Te Mihi Power Station Waikarei | Subject to the conditions specified on the Test Certificate 100111-ADM15130
TNK15009 | 2015-08-13 | Advanced Fuel Tanks NZ Limited PO Box 41 029 Christchurch | Advanced Fuel Tanks NZ Limited 5 Tanya St, Bromley, Christchurch | Supervault MH, SWRI 95-03, AS1692 & UL142 | 75,000 litre single compartment aboveground multi hazard rated storage tank. | Storage of classes 3.1A-D flammable liquids | Advanced Fuel Tanks NZ Limited, Christchurch | Subject to the conditions specified on the Test Certificate 2015095 | This design approval is valid for a period of 3 years
FAB0060 | 20/10/2015 20/10/2021 - Renewal |  | Acme Engineering Limited PO Box 38 064, Wellington Mail Centre, Wellington, 5045 11-29 Hutt Road, Petone, Lower Hutt, 5012 | TNK 15010, 17017, 17018 | Capacity: Up to 110,000 litres Design Specification: AS1692, API650, API620, BS EN 14015 Manufacture Year: Nameplate | Class 3.1 hazardous substances |  | Fabrication, inspection and testing in accordance with the speciﬁed tank design and fabrication code, approved tank design drawings and approved for construction drawings. Allocation of individual tank serial numbers. Retention of individual tank QA records. In addition to the conditions specified on Compliance Certificate 6407-0002, the following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the fabricator for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2024-10-20 | Fabricator of: TNK15010, 17017, 17018
TNK15010 | 2015-10-20 | Acme Engineering Limited | Acme Engineering Limited FAB0060 | API650 | Capacity: 62,915 litres Tank Serial Number: 584 to 587 incl. Tank Design Code: API650 Tank ID: Name Plate Manufacture Year: Name Plate | Storage and transfer of Crude or Condensate oil having a Hazard Classification of 3.1A, 6.1E, 6.3B, 6.7B, 9.1 | Acme Engineering Limited | This approval becomes invalid following any change to the referenced design drawings, duty or service conditions. | NA | FAB0060
FAB0061 | 2015-10-12 |  | Visa S.p.a. Via I Maggio, 55 Fontanelle (TV) Italia |  | Capacity: Up to 2,500 litres Design Specification: AS1692 - 2006, Category 3 Refer to individual TNK numbers: TNK15011, TNK15012, TNK15013, TNK15014, TNK15015, TNK15016, TNK15017, TNK18027, TNK18028, TNK20345, TNK20455, TNK20456, TNK20457 | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Quality Power Limited, PO Box 851, Dunedin, 9054 | Allocation of unique individual tank serial number to be stamped on each individual tank and recorded. Retention of individual tank fabrication, testing records and QA records for each tank. In addition to the conditions specified on Certificate TC00948 and 100241-7074-0003, the following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the coompliance certifier who issued the certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2026-03-22 | Fabricator of: TNK15011, TNK15012, TNK15013, TNK15014, TNK15015, TNK15016, TNK15017, TNK18027, TNK18028, TNK20345, TNK20455, TNK20456, TNK20457
TNK15011 | 2015-10-12 | Visa S.p.a. ADDRESS: Via I Maggio, 55 Fontanelle (TV) Italia | Visa S.p.a. Via I Maggio, 55 Fontanelle (TV) Italia FAB0061 | Design Specification: AS 1692 - 2006, Category 3 | Tank Serial Number: Name Plate Tank ID: 241081057/058 Make: Visa Capacity: 500 litres Tank Design Code: AS 1692 - 2006, Category 3 Manufacture Year: Name Plate Tank ID: 241081057/058 | Storage of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B supplying a generator engine | Quality Power Limited, Dunedin | Subject to the conditions specified on the Test Certificate TC00932 | NA | Approval becomes invalid following any change to the referenced design drawing, duty or service conditions. FAB0061
TNK15012 | 2015-10-12 | Visa S.p.a. ADDRESS: Via I Maggio, 55 Fontanelle (TV) Italia | Visa S.p.a. Via I Maggio, 55 Fontanelle (TV) Italia FAB0061 | Design Specification: AS 1692 - 2006, Category 3 | Tank Serial Number: Name Plate Tank ID: 241010225/226 Make: Visa Capacity: 600 litres Tank Design Code: AS 1692 - 2006, Category 3 Manufacture Year: Name Plate Tank ID: 241010225/226 | Storage of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B supplying a generator engine | Quality Power Limited, Dunedin | Subject to the conditions specified on the Test Certificate TC00936 | NA | Approval becomes invalid following any change to the referenced design drawing, duty or service conditions. FAB0061
TNK15013 | 2015-10-12 | Visa S.p.a. ADDRESS: Via I Maggio, 55 Fontanelle (TV) Italia | Visa S.p.a. Via I Maggio, 55 Fontanelle (TV) Italia FAB0061 | Design Specification: AS 1692 - 2006, Category 3 | Tank Serial Number: Name Plate Tank ID: 241010176/177 Make: Visa Capacity: 600 litres Tank Design Code: AS 1692 - 2006, Category 3 Manufacture Year: Name Plate | Storage of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B supplying a generator engine | Quality Power Limited, Dunedin | Subject to the conditions specified on the Test Certificate TC00938 | NA | Approval becomes invalid following any change to the referenced design drawing, duty or service conditions. FAB0061
TNK15014 | 2015-10-12 | Visa S.p.a. ADDRESS: Via I Maggio, 55 Fontanelle (TV) Italia | Visa S.p.a. Via I Maggio, 55 Fontanelle (TV) Italia FAB0061 | Design Specification: AS 1692 - 2006, Category 3 | Tank Serial Number: Name Plate Tank ID: 241081086/087 Make: Visa Capacity: 800 litres Tank Design Code: AS 1692 - 2006, Category 3 Manufacture Year: Name Plate | Storage of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B supplying a generator engine | Quality Power Limited, Dunedin | Subject to the conditions specified on the Test Certificate TC00940 | NA | Approval becomes invalid following any change to the referenced design drawing, duty or service conditions. FAB0061
TNK15015 | 2015-10-12 | Visa S.p.a. ADDRESS: Via I Maggio, 55 Fontanelle (TV) Italia | Visa S.p.a. Via I Maggio, 55 Fontanelle (TV) Italia FAB0061 | Design Specification: AS 1692 - 2006, Category 3 | Tank Serial Number: Name Plate Tank ID: 241081063/064 Make: Visa Capacity: 800 litres Tank Design Code: AS 1692 - 2006, Category 3 Manufacture Year: Name Plate | Storage of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B supplying a generator engine | Quality Power Limited, Dunedin | Subject to the conditions specified on the Test Certificate TC00942 | NA | Approval becomes invalid following any change to the referenced design drawing, duty or service conditions. FAB0061
TNK15016 | 2015-10-12 | Visa S.p.a. ADDRESS: Via I Maggio, 55 Fontanelle (TV) Italia | Visa S.p.a. Via I Maggio, 55 Fontanelle (TV) Italia FAB0061 | Design Specification: AS 1692 - 2006, Category 3 | Tank Serial Number: Name Plate Tank ID: 241081098/099 Make: Visa Capacity: 800 litres Tank Design Code: AS 1692 - 2006, Category 3 Manufacture Year: Name Plate | Storage of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B supplying a generator engine | Quality Power Limited, Dunedin | Subject to the conditions specified on the Test Certificate TC00944 | NA | Approval becomes invalid following any change to the referenced design drawing, duty or service conditions. FAB0061
TNK15017 | 2015-10-12 | Visa S.p.a. ADDRESS: Via I Maggio, 55 Fontanelle (TV) Italia | Visa S.p.a. Via I Maggio, 55 Fontanelle (TV) Italia FAB0061 | Design Specification: AS 1692 - 2006, Category 3 | Tank Serial Number: Name Plate Tank ID: 241081076/077 Make: Visa Capacity: 950 litres Tank Design Code: AS 1692 - 2006, Category 3 Manufacture Year: Name Plate | Storage of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B supplying a generator engine | Quality Power Limited, Dunedin | Subject to the conditions specified on the Test Certificate TC00946 | NA | Approval becomes invalid following any change to the referenced design drawing, duty or service conditions. FAB0061
TNK15018 | 2015-08-06 | Transtank | NA | Design specification: AS 1692 | 67,120 L horizontal tank with Integral Secondary Containment TRANSTANK P69, S/N 740330-9 | Diesel UN3082 3.1D | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley Christchurch 8062 | Subject to the conditions specified on the Test Certificate 100111-15162A
FAB0062 | 2015-09-13 | Polymaster Industrial (Australia) Ltd. | Polymaster Industrial (Australia) Ltd. | TNK13093 | 1,500 litre rotationally moulded PE storage tank Material: Quenos LL711UV colour natural 7032 | Classes 5, 6, 8 and 9 substances |  | The following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the fabricator for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2018-09-12
TNK15019 | 2015-10-05 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS 1692-2006, Cat 3 / HSNOCOP 24-2, 7/14 FAB0023 | 20,000 L double skin above ground horizontal tank | Storage and transfer of diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | NYMIC Engineering Ltd. | Subject to the conditions specified on the Test Certificate TC00994. This approval becomes invalid following any change to the approved drawing. | N/A | FAB0023
TNK15020 | 2015-10-05 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS 1692-2006, Cat 3 / HSNOCOP 24-2, 7/14 FAB0023 | 30,000 L double skin above ground horizontal tank | Storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | NYMIC Engineering Ltd. | Subject to the conditions specified on the Test Certificate TC00995. This approval becomes invalid following any change to the approved drawing. | N/A | FAB0023
TNK15021 | 2015-12-03 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS 1692-2006, Cat 3 / HSNOCOP 24-2, 7/14 FAB0023 | 41,700 L double skin above ground horizontal tank | Storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | NYMIC Engineering Ltd. | Subject to the conditions specified on the Test Certificate TC01021. This approval becomes invalid following any change to the approved drawing. | N/A | FAB0023
TNK15022 | 2016-03-30 | Petrotec Services Limited 12 Venture Place, Middleton, Christchurch, 8024 PO Box 10125, Philipstown, Christchurch, 8145 | Zhangjiagang Logitank Heavy Industry Co. Ltd No.3, Hai Xin North Road, Zhangjiagang City, 215600 FAB0052 | AS 1692-2006, Cat 3 / HSNOCOP 24-2, 7/14 | Above ground double skin rectangular horizontal twin tank Tank Serial Number: Name Plate Make: LogiTank Pty Ltd Model: LSBD-68-00 Capacity: 56,604 L (diesel tank) / 7,268 L (exhaust fluid) Tank Design Code: AS 1692-2006, Cat 3 / HSNOCOP 24-2, 7/14 Manufacture Year: Name Plate | DEF (diesel exhaust fluid) ONLY in the 7,000 L compartment - hazard classification of 6.3A, 6.4A, 9.3C and diesel ONLY in the 56,000L compartment - hazard classification 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Petrotec Services Limited 12 Venture Place, Middleton, Christchurch, 8024 PO Box 10125, Philipstown, Christchurch, 8145 | Subject to the conditions specified on the Test Certificate TC01094. This approval becomes invalid following any change to the approved drawing. | N/A | FAB0052
TNK15023 | 2016-08-24 | Civilquip Limited 54 Tasman Street Greymouth 7805 | Prior to 11/04/2024: Western Global UK FAB0053, FAB0064 As of 11/04/2024: Quindao Jinhuanghai Container Co Ltd Qingdao, Dajinjia, Jimo, P.R. China, 2662299 c/- Fuelchief Ltd 5 Tanya Street Bromley, Christchurch Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS 1692 - 2006 | DC25 - Above ground Type 3 double skinned integral rectangular mild steel tank Safe Fill Level: 2,375 litres | Diesel, 3.1D only | Civilquip Limited 54 Tasman Street Greymouth 7805 | Subject to Test Certificate 100111-00016142 Tank to supply a burner or generator for the purpose of certification. | NA | FAB0053/FAB0064/FAB0069
TNK15024 | 2015-11-12 | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 | Western Global UK/ Przedsiebiorstwo Wielobranzowe, SKALA sp.j. | FAB0053 AS 1692 - 2006, Category 3 / HSNOCOP 24-1 | DC50 - Above ground integral rectangular steel tank. Nominal Volume: 5,000 L Safety Fill Level: 4,700 L | Diesel, 3.1D only | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 | Subject to the conditions specified on the Test Certificate 100111 - ADM15235A | NA | FAB0053/FAB0064/FAB0069
TNK15025 | 2015-11-12 | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 | Western Global UK/ Przedsiebiorstwo Wielobranzowe, SKALA sp.j. | FAB0053 AS 1692 - 2006, Category 3 / HSNOCOP 24-1 | DC100 - Above ground integral rectangular steel tank. Capacity: 10,000 L | Diesel, 3.1D only | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 | Subject to the conditions specified on the Test Certificate 100111 - ADM15234 | NA | FAB0053/FAB0064/FAB0069
TNK15026 | 2015-12-17 | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu 3840 | Fuel Storage Limited | AS 1692: 2006 FAB0050 | Description: 43,500 litres double skin above ground rectangular stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: Refer to Details of Certification for drawings Name of Designer: Fuel Storage Limited Capacity: 43,500 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | FUEL STORAGE LIMITED 700 Bond Road, Te Awamutu 3800 | Approved Drawings: - 1508694-01, Sheets 1-3, 40,000 Litre Rectangular Tank – General Assembly, Rev A, Drawn: L. Ferguson, Date: 18.09.15. - 1508694-02, Sheets 1 & 3, 40,000 Litre Rectangular Tank – Detail, Rev A, Drawn: T. Mead, Date: 25.09.15. - 1508694-03, Sheets 1-3, 40kL DS Tank – Design Updates, Rev A, Drawn: BAZ, Date 25/06/2025. Approved For: The storage and transfer of diesel only, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved to supply an engine or burner. When supplying burner or engine systems supply to have an anti-siphon device installed immediately adjacent to the tank. References: Design Statement: 1508694, Issued by: Joe Bain, Issued to: Fuel Storage Ltd, In respect of: 40,000 Litre Double-skinned Above Ground Fuel StorageTank, Date: 30/09/15. Allocate unique serial number for each tank and retain individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, design code, test pressure in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced drawings or applicable standards. | 2035-08-14 | FAB0050
TNK15027 | 2015-12-04 | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 | Western Global UK/ Przedsiebiorstwo Wielobranzowe, SKALA sp.j. | FAB0053 AS 1692 - 2006, Category 3 / HSNOCOP 24-1 | DCD100 - Above ground mild steel rectangular tank. Capacity: 10,000 L | Diesel, 3.1D only | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 | Subject to the conditions specified on the Test Certificate 100111 -ADM15244 | NA | FAB0053/FAB0064 As of 11/04/2024 FAB0069
TNK16001 | 2015-12-21 | Maskell Productions Ltd. and APD Ltd. 24 Bowden Road Mt Wellington Auckland | Maskell Productions Ltd. 24-26 Bowden Road Mt Wellington Auckland | FAB0063 | 6000 L GRP single wall above ground tank with HDPE liner Design specification: BS 4994 & AS 2634 | Sodium Hypochlorite having a hazard classification of 5.1.1B, 6.1E, 8.2C, 8.3A, 9.1A, 9.1D | Maskell Productions Ltd. and APD Ltd. 24 Bowden Road Mt Wellington Auckland | Subject to the conditions specified on the Test Certificate ST9178 | 2020-12-20 | FAB0063
FAB0063 | 21/12/2015 |  | Maskell Productions Ltd. 24-26 Bowden Road Mt Wellington Auckland | TNK16001 | 6000 L Fibreglass above ground tanks with HDPE liner | Sodium Hypochlorite having a hazard classification of 5.1.1B, 6.1E, 8.2C, 8.3A, 9.1A, 9.1D |  | In addition to the conditions specified on Test Certificate SCF9177, the following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the fabricator for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2018-12-20 | Fabricator of: TNK16001
TNK16002 | 2016-01-28 | Tecsas S.r.l. 26022 Castelverde, via E Fermi 9, Italy | Tecsas S.r.l. 26022 Castelverde, via E Fermi 9, Italy | AS 1692 | Serbatoio 15-127-1LP, 960 litre generator service tank stainless steel 235, | class 3.1D diesel | Powergen Box 14254 Tauranga |  | NA
TNK16003 | 2016-10-15 | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu 3840 | AS 1692 - 2006, Category 3 FAB0050 | 4,788 litre above ground storage tank to supply a burner or generator. | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu 3840 | Subject to the conditions specified on the Test Certificate TC01205. Tank to supply a burner or generator. This approval becomes invalid following any change to the approved drawing. | N/A | FAB0050
TNK16004 | 2016-10-26 | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu 3840 | AS 1692 - 2006, Category 3 FAB0050 | 1,965 litre double skin tank to supply a burner or generator. | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu 3840 | Subject to the conditions specified on the Test Certificate TC01255. Tank to supply a burner or generator. This approval becomes invalid following any change to the approved drawing. | N/A | FAB0050
TNK16005 | 2016-02-08 | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 | Western Global UK/ Przedsiebiorstwo Wielobranzowe, SKALA sp.j. | FAB0053 AS 1692 - 2006, Category 3 / HSNOCOP 24-1 | DCD200 - Above ground mild steel rectangular tank. Capacity: 20,000 L | Diesel, 3.1D only | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 | Subject to the conditions specified on the Test Certificate 100111 -ADM16007 | NA | FAB0053/FAB0064/FAB0069
TNK16006 | 2016-02-08 | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 | Western Global UK/ Przedsiebiorstwo Wielobranzowe, SKALA sp.j. | FAB0053 AS 1692 - 2006, Category 3 / HSNOCOP 24-1 | DCD150 - Above ground mild steel rectangular tank. Capacity: 15,000 L | Diesel, 3.1D only | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 | Subject to the conditions specified on the Test Certificate 100111 -ADM16010 | NA | FAB0053/FAB0064/FAB0069
TNK16007 | 2016-02-20 | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 | Western Global UK/ Przedsiebiorstwo Wielobranzowe, SKALA sp.j. | FAB0053 AS 1692 - 2006, Category 3 / HSNOCOP 24-1 | DCD450 - Above ground mild steel rectangular tank. Capacity: 45,000 L | Diesel, 3.1D only | Fuelchief Limited (formally Civilquip prior to 30 June 2017) 5 Tanya Street Bromley, Christchurch 8062 | Subject to the conditions specified on the Test Certificate 100111 -ADM16011 | NA | FAB0053/FAB0064/FAB0069
TNK16008 | 2016-03-04 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS 1692-2006 / HSNOCOP 24-1, 3/08 FAB0023 | 5,555 litre double skin above ground cylindrical horizontal tank | Storage and transfer of diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | NYMIC Engineering Ltd. | Subject to the conditions specified on the Test Certificate TC01083. This approval becomes invalid following any change to the approved drawing. | N/A | FAB0023
TNK16009 | 2016-07-19 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692-2006, Category 4 FAB0047 | 20,248 litre single skin petrol storage tank | Petrol having a hazard classification of 3.1A, 6.1E, 6.3B, 6.7B, 9.1B | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Subject to the conditions specified on the Test Certificate TC01198. This approval becomes invalid following any change to the approved drawing. | N/A | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
FAB0064 | 2016-04-01 |  | Przedsiebiorstwo Wielobranzowe, SKALA sp.j. Maloszyce 12/2 84-302 Lebork Production Department Brusy 89-632 Brusy Ul.Polna 3 NIP: PL 8411602615 | AS 1692 - 2006, Cat 3 / HSNOCOP 24-2, 7/14 | Capacity: Up to 60,000 litres Reference: TNK10024, 15024, 15025, 15027, 16005, 16006, 16007 | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Civilquip 8-10 Chesterfield St, Greymouth | Subject to the conditions specified on the Test Certificate TC01100. In addition to the conditions specified on Test Certificate TC01100, the following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2019-03-31 | Fabricator of: TNK10024, 15024, 15025, 15027, 16005, 16006, 16007
FAB0065 | 2016-02-26 |  | Maskell Productions Ltd. 24-26 Bowden Road Mt Wellington Auckland | TNK16010 | 40,000 L FRP above-ground process container. Cone-based precipitation tanks. | Expended Chromium Tanning Liquor - Hazardous classification 8.2B |  | In addition to the conditions specified on Test Certificate SCF9503, the following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the fabricator for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2019-02-25 | Fabricator of: TNK16010
TNK16010 | 2016-02-22 | Maskell Productions Ltd. 24-26 Bowden Road Mt Wellington Auckland |  | FAB0065 | 40,000 L FRP above-ground process container. Cone-based precipitation tank. 3500 mm i.d x 3805 mm hi above 2255 mm skirt. | Expended Chromium Tanning Liquor - Hazardous classification 8.2B | Maskell Productions Ltd. 24-26 Bowden Road Mt Wellington Auckland
TNK16011 | 2016-05-05 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd 9 Kilronan Place Wigram Christchurch FAB0023 | AS 1692-2006 / HSNOCOP 24-1, 3/08 FAB0023 | 3,817 litre horizontal cylindrical double skin tank | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | NYMIC Engineering Ltd. | Subject to the conditions specified on the Test Certificate TC01134. Cylindrical double skin tank to supply a burner or generator. This approval becomes invalid following any change to the approved drawing. | N/A | FAB0023
TNK16012 | 2016-06-02 | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu Ph 0800 623 255 | Fuel Storage Limited | AS 1692-2006, Cat. 3 FAB0050 | Up to 02/04/2026: 900 litre double skin diesel storage tank to supply a burner or generator From 02/04/2026: Description: 990 Litres above ground, double skinned, rectangular stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: FSL-DS950-01, Rev: A, Sheets: 1 to 6, Date: 01/04/2026, Drawn by: Baz Burtt Name of Designer: Fuel Storage Limited Capacity: 990 Litres Maximum Safe Fill: 950 litres Compartments: 1 | Up to 02/04/2026: Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B From 02/04/2026: Name: Diesel Class(es): 3.1D, 6.7B Name: Low Flash Diesel Class(es): 3.1C, 6.7B | FUEL STORAGE LIMITED 700 Bond Road, Te Awamutu, 3800 | Subject to the conditions specified on the Test Certificate TC01141. This approval becomes invalid following any change to the approved drawing. Approved For: The storage and transfer of Diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B or Low Flash Diesel having a hazard classification of 3.1C, 6.1E, 6.3B, 6.7B, 9.1B. Approved to supply an engine or burner. References: Compliant with AS 1692:2006, Category 3. 16040551 - Fuel Storage - 950L HSNO Paperwork Rev D. 8879-CAN-0001, 950L Double Skin Tank Equivalence, Rev01, 01Apr26. Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank name plate in addition to the manufacturers serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. QA inspection and documentation to be completed before installation of the tank/s. Must not be installed in non-fire resistant construction - Installation location stipulated in clause 17.63 of Heath and Safety at Work (Hazardous Substances) Regulations 2017. The following clauses from the Heath and Safety at Work (Hazardous Substances) Regulations 2017, are requirements to be met on installation for this stationary tank supplying an engine (generator): 17.6 (2), 17.25, 17.27, Part 17 Subpart 3, 11-13, 17.75, 17.78, 17.79, 17.80 & 17.81. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced Fuel Storage Limited drawings or applicable standards. | 2036-04-02 | FAB0050
TNK16013 | 2016-08-16 |  | NYMIC Engineering Ltd. | AS 1692-2006, Cat. 4 / HSNOCOP 24 V2.0, July 2014 FAB0023 |  | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | NYMIC Engineering Ltd. | Subject to the conditions specified on the Test Certificate TC01140. This approval becomes invalid following any change to the approved drawings. | N/A | FAB0023
TNK16014 | 2016-06-16 | Petrotec Services Limited 12 Venture Place, Middleton, Christchurch, 8024 PO Box 10125, Philipstown, Christchurch, 8145 | Zhangjiagang Logitank Heavy Industry Co. Ltd No.3, Hai Xin North Road, Zhangjiagang City, 215600 FAB0052 | AS 1692-2006, Cat 3 / HSNOCOP 24-2, 7/14 | Above ground double skin rectangular horizontal twin tank Tank Serial Number: Name Plate Make: LogiTank Pty Ltd Model: LSBD-68-00 Capacity: 58,070 L (diesel tank) / 7,220 L (exhaust fluid) Tank Design Code: AS 1692-2006, Cat 3 / HSNOCOP 24-2, 7/14 Manufacture Year: Name Plate | DEF (diesel exhaust fluid) ONLY in the 7,000 L compartment - hazard classification of 6.3A, 6.4A, 9.3C and diesel ONLY in the 56,000L compartment - hazard classification 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Petrotec Services Limited 12 Venture Place, Middleton, Christchurch, 8024 PO Box 10125, Philipstown, Christchurch, 8145 | Subject to the conditions specified on Test Certificate TC01176. This approval becomes invalid following any change to the approved drawing. | N/A | FAB0052
TNK16015 | 2016-06-28 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692-2006, Cat. 4 / HSNOCOP 24 V2.0, July 2014 FAB0047 | 5,550 litre (outer volume) double skin tank | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Subject to the conditions specified on the Test Certificate TC01182. This approval becomes invalid following any change to the approved drawings, design service conditions or duty. | N/A | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
TNK16016 | 2016-06-20 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692-2006, Cat. 4 / HSNOCOP 24 V2.0, July 2014 FAB0047 | 13,972 litre (outer volume) double skin tank | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Subject to the conditions specified on the Test Certificate TC01178. This approval becomes invalid following any change to the approved drawings, design service conditions or duty. | N/A | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
TNK16017 | 2016-05-27 | Fuelchief Limited 5 Tanya Street Bromley, Christchurch 8062 (formally Advanced Fuel Tanks NZ Limited prior to 27 May 2019) | Fuelchief Limited 5 Tanya Street Bromley, Christchurch 8062 FAB0076 (FAB0014 by Advanced Fuel Tanks NZ Limited prior to 27 May 2019) As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS1692 - 2006 Category 4 | PXS 5,156 litre above ground single skin steel tank Safe Fill Level: 5,000 Litres | Flammable liquids having hazard classifications of 3.1A, 3.1B, 3.1C or 3.1D | Fuelchief Limited 5 Tanya Street Bromley, Christchurch 8062 | This approval becomes invalid following any change to the referenced drawings, duty or service conditions. | 2024-07-31 | FAB0076 FAB0014 (prior to 27 May 2019) As of 19/03/2023 FAB0093
TNK16018 | 2016-07-15 | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu Ph 0800 623 255 | Fuel Storage Limited | AS 1692 - 2006, Category 3 FAB0050 | 1,816 litre above ground diesel storage tank to supply a burner or generator. | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuel Storage Limited | Subject to the conditions specified on the Test Certificate TC01191. Tank to supply a burner or generator. This approval becomes invalid following any change to the approved drawings. | N/A | FAB0050
TNK16019 | 2016-11-24 | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692-2006, Cat. 4 / HSNOCOP 44 V1.1 FAB0016 | Underground steel tanks with integral HDPE secondary containment. Single, double or triple compartments with a gross volume ranging from 27,952 L to 70,717 L. | Class 3.1A, 3.1B, 3.1C, 3.1D hazardous substances | Petroleum Services (2001) Ltd | Subject to the conditions specified on the Test Certificate TC01304. This approval becomes invalid following any change to the referenced Petroleum Services Ltd drawings (2750mm OD DS 1 to 7 incl. B, Revision 17-06-16). | N/A | FAB0083 (FAB0016 prior to 9/06/2019)
TNK16020 | 2016-08-19 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS 1692 – 2006, Category 4 FAB0045 | Horizontal cylindrical double skin above ground tanks: 55,500 L, 62,000 L, 74,000 L, 86,500 L, 93,500 L, 99,500 L | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Martin Engineering (Palmerston North) Ltd. | Subject to the conditions specified on the Test Certificate TC01214. This approval becomes invalid following any change to the referenced Martin Engineering Ltd drawings (TNK55K-100KDS 1 to 8 incl. A, Revision 19-08-16). | N/A | FAB0045
TNK16022 | 2016-11-21 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS 1692-2006 FAB0023 | 130,000 L cylindrical single skin above ground horizontal fuel storage tank with three compartments. | Storage of class 3.1A flammable liquids | NYMIC Engineering Ltd. | Subject to the conditions specified on the Test Certificate TC01292. This approval becomes invalid following any change to the design and / or referenced drawings. | NA | FAB0023
TNK16023 | 2016-11-25 | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu 3840 | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu 3840 | AS 1692:2006 FAB0050 | Description: 31,755 litres double skin above ground rectangular stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: Refer to Details of Certification for drawings Name of Designer: Fuel Storage Limited Capacity: 31,755 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | FUEL STORAGE LIMITED 700 Bond Road PO Box 108 Te Awamutu 3840 | Approved Drawings: - 16101577-01, Sheets 1-3, 30,000 Litre Rectangular Tank – General Assembly, Rev A, Drawn: S. Bamford, Date: 19.10.16. - 16101577-02, Sheets 1-2, 30,000 Litre Rectangular Tank – Detail, Rev A, Drawn: S. Bamford, Date: 19.10.16. - 16101577-03, Sheets 1-3, 30kL DS Tank – Design Updates, Rev A, Drawn: BAZ, Date 25/06/2025. Approved For: The storage and transfer of diesel only, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved to supply an engine or burner. When supplying burner or engine systems supply to have an anti-siphon device installed immediately adjacent to the tank. References: Design Statement: 16101577, Issued by: Matt Bishop, Issued to: Fuel Storage Ltd, In respect of: 30,000 Litre Double-skinned Above Ground Fuel Storage Tank, Date: 21/10/16. Allocate unique serial number for each tank and retain individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, design code,test pressure in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced drawings or applicable standards. | 2035-08-14 | FAB0050
TNK16026 | 2017-01-19 | Petrotec Services Limited 12 Venture Place, Middleton, Christchurch, 8024 PO Box 10125, Philipstown, Christchurch, 8145 | Zhangjiagang Logitank Heavy Industry Co. Ltd No.3, Hai Xin North Road, Zhangjiagang City, 215600 FAB0052 | AS 1692-2006 / HSNOCOP 24-1, 3/08 / HSNOCOP 6-V2.1 | 11,700 L above ground double skin rectangular horizontal tank. | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petrotec Services Limited 12 Venture Place, Middleton, Christchurch, 8024 PO Box 10125, Philipstown, Christchurch, 8145 | Subject to the conditions specified on Test Certificate TC01342. This approval becomes invalid following any change to the design duty or service conditions or approved drawings. | N/A | FAB0052
TNK16027 | 2017-02-09 | Petrotec Services Limited 12 Venture Place, Middleton, Christchurch, 8024 PO Box 10125, Philipstown, Christchurch, 8145 | Zhangjiagang Logitank Heavy Industry Co. Ltd No.3, Hai Xin North Road, Zhangjiagang City, 215600 FAB0052 | AS 1692-2006 / HSNOCOP 24-1, 3/08 / HSNOCOP 6-V2.1 | 30,500 L above ground double skin rectangular horizontal tank. | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petrotec Services Limited 12 Venture Place, Middleton, Christchurch, 8024 PO Box 10125, Philipstown, Christchurch, 8145 | Subject to the conditions specified on Test Certificate TC01343. This approval becomes invalid following any change to the design duty or service conditions or approved drawings. | N/A | FAB0052
TNK17000 | 2017-02-01 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692-2006 / HSNOCOP 24, V2.0 July 2014 FAB0047 | 20,000 to 60,000 litres double skin storage tanks | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North | Subject to the conditions specified on the Test Certificate TC01353. This approval becomes invalid following any change to the referenced Fuelcon drawings. | NA | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
TNK17001 | 2017-03-17 | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692-2006, Cat. 4 / HSNOCOP 24-1, 3/08 | 16,615 L double skin cylindrical above ground tank | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Subject to the conditions specified on the Test Certificate TC01373. This approval becomes invalid following any change to the design parameters and referenced drawings. Approved to supply a burner or engine. | NA | FAB0083 (FAB0016 prior to 9/06/2019)
TNK17002 | 2017-03-17 | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692-2006, Cat. 4 / HSNOCOP 24-1, 3/08 As of 1 August 2019: AS1692 – 2006, Category 4 & Reduced Secondary Containment Safe Work Instrument 2017 (Impact Protected) | 29,477 L double skin cylindrical above ground tank | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Subject to the conditions specified on the Test Certificate TC01371. This approval becomes invalid following any change to the design parameters and referenced drawings. Approved to supply a burner or engine. Amended on 1 August 2019 as per compliance certificate 191547 | 2029-07-31 | FAB0083 (FAB0016 prior to 9/06/2019)
TNK17003 | 2017-05-05 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS 1692-2006 FAB0023 | 80,300 L rectangular single skin above ground storage tank | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | NYMIC Engineering Ltd. | This approval becomes invalid following any change to the BVT design, service conditions and/or referenced drawings. | NA | FAB0023
TNK17005 | 2017-06-16 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS 1692 - 2006, Category 4 FAB0023 | 5,000L cylindrical, horizontal, single skin tank | Class 3.1A, 3.1B, 3.1C or 3.1D hazardous substances and Avgas 100 having a Hazard Classification of 3.1A, 6.1E, 6.3B, 6.7B, 6.8A, 9.1B | NYMIC Engineering Ltd. | This approval becomes invalid following any change to the BVT Consulting design and/or referenced drawings. | N/A | FAB0023
TNK17006 | 2017-06-16 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS 1692 - 2006, Category 4 FAB0023 | 10,000L cylindrical, horizontal, single skin tank | Class 3.1A, 3.1B, 3.1C or 3.1D hazardous substances and Avgas 100 having a Hazard Classification of 3.1A, 6.1E, 6.3B, 6.7B, 6.8A, 9.1B | NYMIC Engineering Ltd. | This approval becomes invalid following any change to the BVT Consulting design and/or referenced drawings. | N/A | FAB0023
TNK17007 | 2017-06-16 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS 1692 - 2006, Category 4 FAB0023 | 20,000L cylindrical, horizontal, single skin tank | Class 3.1A, 3.1B, 3.1C or 3.1D hazardous substances and Avgas 100 having a Hazard Classification of 3.1A, 6.1E, 6.3B, 6.7B, 6.8A, 9.1B | NYMIC Engineering Ltd. | This approval becomes invalid following any change to the BVT Consulting design and/or referenced drawings. | N/A | FAB0023
TNK17008 | 2017-08-15 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS 1692 – 2006, Category 3 FAB0045 | 21,678 litre horizontal above ground tank | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Martin Engineering (Palmerston North) Ltd. | Subject to the conditions specified on the Test Certificate TC01431. This approval becomes invalid following any change to the referenced drawings and producer statement. | N/A | FAB0045
TNK17009 | 2017-06-26 | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Prior to 9/06/2019 Petroleum Services Ltd 15 Manchester Place, Hamilton & 21 Midhurst St, Palmerston North FAB0016 As of 19/12/2019 Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692-2006, Cat. 4 / HSNOCOP 24-1, 3/08 | 2,300 L rectangular above ground tank | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petroleum Services (2001) Limited 15 Manchester Place Te Rapa Hamilton | Subject to the conditions specified on the Test Certificate TC01435. This approval becomes invalid following any change to the design parameters and referenced drawings. Approved to supply a burner or engine. | N/A | FAB0083 (FAB0016 prior to 9/06/2019)
FAB0069 | 2017-05-17 |  | Quindao Jinhuanghai Container Co Ltd Qingdao, Dajinjia, Jimo, P.R. China, 2662299 c/- Fuelchief Ltd 5 Tanya Street Bromley, Christchurch Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | Prior to 11/04/2024: Design Standard: AS1692-2006 As of 11/04/2024: Design Standards: AS1692-2006, AS1940:2017 | Capacity: Steel tanks up to 68,000 litres Reference: TNK13011, TNK13013, TNK13016, TNK13017, TNK15001, TNK15023, TNK15024, TNK15025, TNK15027, TNK16005, TNK16006, TNK16007, TNK18026, TNK19023, TNK20023, TNK20095, TNK20096, TNK20084 | As of 21/12/2020: Class 3.1D Prior to 21/12/2020: Class 3.1A, B, C or D hazardous substances | Quindao Jinhuanghai Container Co Ltd Qingdao, Dajinjia, Jimo, P.R. China, 2662299 c/- Fuelchief Ltd 5 Tanya Street Bromley, Christchurch Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the compliance certifier who issued the certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2027-04-11 | Fabricator of: TNK13011, TNK13013, TNK13016, TNK13017, TNK15001, TNK15023, TNK15024, TNK15025, TNK15027, TNK16005, TNK16006, TNK16007, TNK18026, TNK19023, TNK20023, TNK20095, TNK20096, TNK20084
TNK17010 | 2017-07-10 | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu FAB0050 | AS 1692-2006 - Category 3 | 2,450 litre raised above ground rectangular single skin tank | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu | Subject to the conditions specified on the Test Certificate TC01433. This approval becomes invalid following any change to the design parameters and referenced drawings. Approved to supply a burner or engine. | N/A | FAB0050
TNK17011 | 2017-05-15 | Advanced Fuel Tanks NZ Limited PO Box 41 029 Christchurch | Advanced Fuel Tanks NZ Limited 5 Tanya St, Bromley, Christchurch FAB0014 | AS1692 - 2006 Category 4 | 5,105 L single wall mild steel bulk storage tank Safe fill Level: 4,951 L. Tank outside diameter: 1.9 m. OAL: 1.84 m. Safe fill height: 1.785 m. Shell: 6 mm M/S. Ends: 6 mm M/S. | Storage of Class 3.1C-D flammable liquids (motor spirit additive or diesel) with a maximum SG of 1.0. | Advanced Fuel Tanks NZ Limited, Christchurch | The design is approved subject to the conditions specified on Test Certificate 2017035 2 inch Protectorseal PV vent model 8542H. Set point 0.32 kPa pressure. Set point -0.32 kPa vacuum. 9 inch emergency vent Liquip model EH230 3,836 CMH. Maximum pump in rate 150 LPM. Maximum pump out rate 7.5 LPM. | 2022-05-14 | FAB0014
TNK17012 | 2017-05-15 | Advanced Fuel Tanks NZ Limited PO Box 41 029 Christchurch | Advanced Fuel Tanks NZ Limited 5 Tanya St, Bromley, Christchurch FAB0014 | AS1692 - 2006 Category 4 | 20,000 L single wall mild steel bulk storage tank Safe fill Level: 19,351 L. Tank outside diameter: 2.4 m. OAL: 4.5 m. Safe fill height: 2.27 m. Shell: 6 mm M/S. Ends: 8 mm M/S. | Storage of Class 3.1A flammable liquids with a maximum SG of 1.0. | Advanced Fuel Tanks NZ Limited, Christchurch | The design is approved subject to the conditions specified on Test Certificate 2017035 2 inch Protectorseal PV vent model 8542H. Set point 0.32 kPa pressure. Set point -0.32 kPa vacuum. 9 inch emergency vent Liquip model EH230 3,836 CMH. Maximum pump in rate 300 LPM. Maximum pump out rate 150 LPM. | 2022-05-14 | FAB0014
FAB0070 | 2017-04-21 |  | Panus Assembly Co Limited 27/1 Moo 3 Koodngong Panusnikom Chonburi Thailand | AS1692 - 2006 Category 3 | Petro Cube 450 L, 1,100 L, 2,000 L, 3,000 L, 4,500 L, 6,300 L double skin steel self-bunded baffled above-ground diesel fuel tanks Petro Store 2,500 L, 5,500 L, 11,000 L double skin steel above-ground diesel fuel tanks Petro Tank PT12PB - 10,632 L and PT30PB - 28,974 L double skin steel above-ground diesel fuel tanks Reference: TNK17013, TNK17014, TNK17015, TNK18005, TNK18019, 18029 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petro Industrial Pty Limited Factory 2 - 106 Potassium Street PO Box 407 Narangba, Queensland 4504, Australia | The design is approved subject to the conditions specified on Test Certificate SFC11610. In addition to the conditions specified on Test Certificate SFC11610, the following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2020-04-20 | Fabricator of: TNK17013, TNK17014, TNK17015, TNK18005, TNK18019, 18029
TNK17013 | 2017-04-21 | Petro Industrial Pty Limited Factory 2 - 106 Potassium Street PO Box 407 Narangba, Queensland 4504, Australia | Panus Assembly Co Limited 27/1 Moo 3 Koodngong Panusnikom Chonburi Thailand FAB0070 | AS1692 - 2006 Category 3 | Petro Cube 450 L, 1,100 L, 2,000 L, 3,000 L, 4500 L, 6300 L double skin steel self-bunded baffled above-ground diesel fuel tanks | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petro Industrial Pty Limited Factory 2 - 106 Potassium Street PO Box 407 Narangba, Queensland 4504, Australia | The design is approved subject to the conditions specified on Test Certificate ST11611. 450 L above-ground diesel fuel tank to supply a burner or generator. | 2022-04-20 | FAB0070
TNK17014 | 2017-04-21 | Petro Industrial Pty Limited Factory 2 - 106 Potassium Street PO Box 407 Narangba, Queensland 4504, Australia | Panus Assembly Co Limited 27/1 Moo 3 Koodngong Panusnikom Chonburi Thailand FAB0070 | AS1692 - 2006 Category 3 | Petro Tank PT12PB - 10,632 L and PT30PB - 28,974 L double skin steel above-ground diesel fuel tanks | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petro Industrial Pty Limited Factory 2 - 106 Potassium Street PO Box 407 Narangba, Queensland 4504, Australia | The design is approved subject to the conditions specified on Test Certificate ST11612. | 2022-04-20 | FAB0070
TNK17015 | 2017-04-21 | Petro Industrial Pty Limited Factory 2 - 106 Potassium Street PO Box 407 Narangba, Queensland 4504, Australia | Panus Assembly Co Limited 27/1 Moo 3 Koodngong Panusnikom Chonburi Thailand FAB0070 | AS1692 - 2006 Category 3 | Petro Store 2,500 L, 5,500 L, 11,000 L double skin steel above-ground diesel fuel tanks | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petro Industrial Pty Limited Factory 2 - 106 Potassium Street PO Box 407 Narangba, Queensland 4504, Australia | The design is approved subject to the conditions specified on Test Certificate ST11613. | 2022-04-20 | FAB0070
TNK17016 | 2017-08-29 | NYMIC Engineering Ltd. | NYMIC Engineering Ltd. | AS 1692-2006, Category 3 & HSNCOP24-1 FAB0023 | 59,400 L double skin above ground horizontal fuel storage tank | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | NYMIC Engineering Ltd. | The design is approved subject to the conditions specified on Test Certificate TC01487. This approval becomes invalid following any change to the BVT Consulting design, service conditions and/or referenced drawings. | N/A | FAB0023
TNK17017 | 2017-08-23 | Acme Engineering Limited | Acme Engineering Limited FAB0060 | BS EN 14015 - 2004 | 49,990 L cylindrical above ground tank | Turpentine having a Hazard Classification of 3.1C, 6.1E, 6.4A. | Acme Engineering Limited | The design is approved subject to the conditions specified on Test Certificate TC01497. This approval becomes invalid following any change to the Acme Engineering Design and referenced drawings. Minor nozzle changes may apply to individual tanks. | N/A | FAB0060
TNK17018 | 2017-08-23 | Acme Engineering Limited | Acme Engineering Limited FAB0060 | BS EN 14015: 2004 | 72,348 L cylindrical above ground tank | Turpentine having a Hazard Classification of 3.1C, 6.3A, 6.4A, 6.8B, 6.9A, 9.1A, 9.1B | Acme Engineering Limited | The design is approved subject to the conditions specified on Test Certificate TC01498. This approval becomes invalid following any change to the Acme Engineering Design and referenced drawings. Minor nozzle changes may apply to individual tanks. | N/A | FAB0060
FAB0071 | 2017-08-25 |  | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Design Standards: AS 1692-2006 & API 650 | Capacity: Refer to invidual registered TNK designs Prior to 16/02/2024 refer to individual TNK numbers: TNK17019, 17020, 17026, 17027, 17028, 17029, 17030, 18017, 18018, 18030, 18031, 18032, 18033, 18034, 19011, 19012, 19013, 19020, 19021, 19022, 19024 From 16/02/2024 refer to individual TNK numbers: TNK17019, TNK17020, TNK17027, TNK17028, TNK17029, TNK17030, TNK18030, TNK18031, TNK18032, TNK18033, TNK18034, TNK19011, TNK19012, TNK19013, TNK19020, TNK19021, TNK19022, TNK19024, TNK20055, TNK20073, TNK20078, TNK20079, TNK20107, TNK20108. | Flammable, oxidising, toxic, eco-toxic or corrosive substances | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Design certificates for TNK17026, TNK18017, TNK18018 expired. To be renewed before being associated with FAB0071. WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the compliance certifier who issued the certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2027-02-16 | Fabricator of: TNK17019, TNK17020, TNK17027, TNK17028, TNK17029, TNK17030, TNK18030, TNK18031, TNK18032, TNK18033, TNK18034, TNK19011, TNK19012, TNK19013, TNK19020, TNK19021, TNK19022, TNK19024, TNK20055, TNK20073, TNK20078, TNK20079, TNK20107, TNK20108.
TNK17019 | 2017-08-25 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton FAB0071 | AS 1692-2006, Category 5 | 21,108 litre above ground stationary container tank | Sodium hydroxide, > 5% aqueous solution, having a Hazard Classification of 6.1D, 6.1E, 8.1A, 8.2B, 8.3A, 9.1D | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | N/A | FAB0071
TNK17020 | 2017-08-25 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton FAB0071 | AS 1692-2006, Category 5 | 21,108 litre above ground stationary container tank | 10% to 60% Nitric Acid solution having a hazard classification of 6.1D, 6.9B, 8.1A, 8.2B, 8.3A | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | N/A | FAB0071
FAB0072 | 2017-11-30 |  | Mercer Stainless Limited New Plymouth Branch Corbett Road Bell Block New Plymouth 4341 | AS1692, BS EN 14015, API650 & API620 | Up to 250,000 litres | Flammable, oxidising, toxic, eco-toxic or corrosive liquids | Mercer Stainless Limited New Plymouth Branch Corbett Road Bell Block New Plymouth 4341 | Fabrication, inspection and testing in accordance with the specified tank design code, approved tank design drawings and approved for construction drawings. Allocation of individual tank serial numbers. Retention of individual tank QA records. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2020-11-29 | Fabricator of: TNK18024, TNK18025, TNK20021
TNK17021 | 2017-09-08 | Fuelchief Limited 5 Tanya Street PO Box 41 029 Bromley Christchurch | Advanced Fuel Tanks N.Z. Ltd 5 Tanya St, Bromley, Christchurch FAB0014 As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS 1692-2006 | 35,000 litre double skin horizontal tank | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuelchief Limited 5 Tanya Street PO Box 41 029 Bromley Christchurch | This approval becomes invalid following any change to the referenced drawings, duty or service conditions. Approved to supply a burner or generator. | N/A | FAB0014 As of 19/03/2023 FAB0093
TNK17022 | 2017-09-11 | Greentank Limited 16 Donald Street Dunedin | Greentank Limited FAB0001 and FAB0019 | Design specification: UL 1316 - 1996 | 64,294 Litres double-wall fibreglass underground fuel storage tank. | Flammable liquids having hazard classifications of 3.1A, 3.1B, 3.1C or 3.1D | Greentank Ltd | The design is approved subject to the conditions specified on Test Certificate TC01548. This approval becomes invalid following any change to the referenced drawings, duty or service conditions. | N/A | FAB0001 (Expired 22/06/2007) FAB0019 (Expired 19/02/2012)
TNK17023 | 2015-11-29 | PK Engineering (Nelson) Ltd. | Brightwater Engineering Ltd., 7 Spencer Place, Brightwater 7022, Nelson. FAB0073 | AS1692 – 2006, Category 3 | 59,500 litres single compartment baffled aboveground double wall internally stiffened diesel storage tank. Internal length: 9.488 m Internal width: 2.778 m Height: 2.81 m. Manufacture: inner and outer shells from 6 mm Gr250 mild steel. Safe fill height 2195 mm.(58,000 litre). 15,500 litre single compartment baffled aboveground double wall internally stiffened Adblue/Goclear storage tank. Internal length: 2.400 m Internal width: 2.690 m Height: 2.610 m Manufacture: inner tank 4 mm 316L stainless steel, outer tank 6 mm Gr250 mild steel. Maximum safe fill: 15,000 litres. | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | PK Engineering (Nelson) Ltd. | The design is approved subject to the conditions specified on Test Certificate 2015105 The vent is to terminate not less than 150 mm. above the tank top and is to be higher than the fill point of the tank. All venting requirements for atmospheric tank are to be comply with API2000 for the maximum fill rates and discharge rates applicable for the installation. | 2020-11-28 | FAB0073
FAB0073 | 2017-09-28 |  | Brightwater Engineering Ltd., 7 Spencer Place, Brightwater 7022, Nelson. | AS1692 – 2006, Category 3 | 58,000 litre diesel / 15,000 litre AdBlue, Go clear additive PUFF tank. | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Brightwater Engineering Ltd., 7 Spencer Place, Brightwater 7022, Nelson. | The following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2020-09-27
TNK17024 | 2017-10-27 | Fuelchief Limited 5 Tanya Street PO Box 41029 Bromley Christchurch | Advanced Fuel Tanks N.Z. Ltd 5 Tanya St, Bromley, Christchurch FAB0014 As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS 1692-2006, Category 3 tank design | 2,000 L single skin above ground rectangular diesel fuel storage tank | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuelchief Limited 5 Tanya Street PO Box 41029 Bromley Christchurch | The design is approved subject to the conditions specified on Test Certificate TC01568. This approval becomes invalid following any change to the referenced drawings, duty or service conditions. Approved to supply a burner or engine. | N/A | FAB0014 As of 19/03/2023 FAB0093
TNK17026 | 2018-05-14 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton FAB0071 | AS 1692-2006, Category 5 | 11,000 L cylindrical above ground tank. Safe fill level: 10,092 Litres Serial number: 21392-Tank 15-A01 Tank ID: Tank 15 Equipment number: 19502183TK10 Manufacture: 2017 | Sulphuric Acid (98%) having a hazard classification of 6.1D, 6.1E, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A, 9.1C, 9.1D | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | 2023-05-13 | FAB0071
TNK17027 | 2018-01-15 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton FAB0071 | AS 1692-2006, Category 5 | 41,615 L vertical above ground tank Safe fill level: 40,000 litres | 1-10% Phosphorous / Citric Acid CIP solution having a hazard classification of 6.1E, 6.3A, 6.4A, 8.1A, 9.1D | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | N/A | FAB0071
TNK17028 | 2018-01-15 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton FAB0071 | AS 1692-2006, Category 5 | 14,250 L vertical above ground tank Safe fill level: 12,335 litres | Dilute Nitric acid CIP solution (approximately 1.5%) having a hazard classification of 6.1E, 6.9B, 8.1A, 8.2C, 8.3A | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | N/A | FAB0071
TNK17029 | 2018-01-15 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton FAB0071 | AS 1692-2006, Category 5 | 18,160 L vertical above ground tank Safe fill level: 15,474 litres | 0.5% caustic having hazard classifications of 6.1E, 6.3A, 6.4A OR 0.5% nitric acid CIP solution having hazard classification of 6.1E, 6.9B, 8.1A, 8.2C, 8.3A | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | N/A | FAB0071
TNK17030 | 2018-01-15 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton FAB0071 | AS 1692-2006, Category 5 | 18,060 L vertical above ground tank Safe fill level: 15,470 litres | 0.5% caustic OR 0.5% nitric acid CIP solution having hazard classifications of 6.1E, 6.3A, 6.4A OR 6.1E, 6.9B, 8.1A, 8.2C, 8.3A respectively | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | N/A | FAB0071
TNK18000 | 2018-01-24 | Direct Mechanical Services Limited 26 Hobill Avenue Wiri, Auckland 2104 |  | AS 1692 - 2006, Category 3 | 876 - 1,222 Litres above ground tanks 1000 to 1220 mm in length to to supply emergency fire pumps. | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Direct Mechanical Services Limited 26 Hobill Avenue Wiri, Auckland 2104 | Approved to supply an engine driving an emergency fire pump. | N/A
TNK18001 | 2018-01-23 | IT Power Services Limited 13a Piermark Drive Rosedale Auckland | Mainline Sheetmetals Limited 209 Ellis Street Frankton Hamilton FAB0018 (until 18/10/2019) | AS 1692 - 2006, Category 3 | 1,000 litre generator base tank | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | IT Power Services Limited 13a Piermark Drive Rosedale Auckland | Approved to supply an engine. | N/A | FAB0018 (until 18/10/2019)
TNK18002 | 2018-01-23 | IT Power Services Limited 13a Piermark Drive Rosedale Auckland | Mainline Sheetmetals Limited 209 Ellis Street Frankton Hamilton FAB0018 (until 18/10/2019) | AS 1692 - 2006, Category 3 | 2,000 litre generator base tank | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | IT Power Services Limited 13a Piermark Drive Rosedale Auckland | Approved to supply an engine. | N/A | FAB0018 (until 18/10/2019)
TNK18003 | 2018-01-30 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692:2006 Cat 4 | 3,490 litre double skin diesel tank. Tanks may supply burners or generators. | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 |  | N/A | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
TNK18004 | 2018-01-30 | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692:2006 Cat 4 | 4,870 litre double skin diesel tank. Tanks may supply burners or generators. | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North Ph 0800 383 5266 |  | N/A | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
TNK18005 | 2018-04-24 | Petro Industrial Pty Limited Factory 2 - 106 Potassium Street Narangba, Queensland 4504, Australia | Panus Assembly Co Limited 27/1 Moo 3 Koodngong Panusnikom Chonburi Thailand FAB0070 | AS 1692 - 2006, Category 3 | 65,200 L above ground double skin rectangular tank. Safe fill level: 62,300 L. | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petro Industrial Pty Limited Factory 2 - 106 Potassium Street Narangba, Queensland 4504, Australia | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | 2023-04-23 | FAB0070
TNK18011 | 2018-04-06 | Eneraque NZ Limited 211 Roscommon Rd, Wiri, Auckland 2104 | Elcos s.r.l. S.S.234 km 58.250 26023 Grumello Cremonese (CR) Italia FAB0074 | AS 1692-2006, Category 3 | 995 litre diesel generator base tank | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Eneraque NZ Limited 211 Roscommon Rd, Wiri, Auckland 2104 | Approved to supply an engine. | 2023-04-06 | FAB0074
FAB0074 | 2018-04-06 |  | Elcos s.r.l. S.S.234 km 58.250 26023 Grumello Cremonese (CR) Italia | AS 1692-2006, Category 3 | 995 litre diesel generator base tank fabricator | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B |  | Fabrication, inspection and testing in accordance with the specified tank design code, approved tank design drawings and approved for construction drawings. Allocation of individual tank serial numbers. Retention of individual tank QA records. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2021-04-06 | Fabricator of: TNK18011
TNK18012 | 2018-08-23 | Petrotec Services Limited 12 Venture Place, Middleton, Christchurch, 8024 PO Box 10125, Philipstown, Christchurch, 8145 | Zhangjiagang Logitank Heavy Industry Co. Ltd No.3, Hai Xin North Road, Zhangjiagang City, 215600 FAB0052 | AS 1692-2006, Category 3 | 24,550 L above ground double skin rectangular horizontal tank for diesel and 4,300 L for diesel exhaust fluid. Diesel Safe Fill Level: 23,320 Litres DEF Safe Fill Level: 4,085 Litres | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B and AdBlue (Urea >26% solution) diesel exhaust fluid having a hazard classification of 6.3B, 6.4A, 9.3C | Petrotec Services Limited 12 Venture Place, Middleton, Christchurch, 8024 PO Box 10125, Philipstown, Christchurch, 8145 | Not be used for Transport. Lift empty only. Individual serial numbers for each tank. Retention of individual tank fabrication and testing records. | 2023-08-22 | FAB0052
TNK18013 | 2018-04-16 | Fuelchief Limited 5 Tanya Street, Bromley Christchurch | As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS 1692 - 2006, Category 4 | 6,000 litre single skin above ground horizontal cylindrical foam storage tank. Safe Fill Level: 5,853 litres | Aqueous Film-Forming Foam Concentrates (AFFF) having a hazard classification of 6.1B | Fuelchief Limited 5 Tanya Street PO Box 41029 Bromley Christchurch |  | 2023-04-15 | Not to be associated with FAB0014 issued to Advanced Fuel Tanks N.Z. Ltd. As of 19/03/2023 FAB0093
TNK18014 | 2018-04-16 | NYMIC Engineering Limited | NYMIC Engineering Ltd FAB0023 | AS 1692 - 2006, Category 4 | 20,680 Litres Double Skin Tank Safe Fill Level: 20,000 litres | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | NYMIC Engineering Limited | This approval becomes invalid following any change to the BVT Consulting design, service conditions and/or referenced drawings. | 2023-04-15 | FAB0023
TNK18015 | 2018-04-16 | NYMIC Engineering Limited | NYMIC Engineering Ltd FAB0023 | AS 1692 - 2006, Category 4 | 30,900 Litres Double Skin Tank Safe Fill Level: 30,000 litres | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | NYMIC Engineering Limited | This approval becomes invalid following any change to the BVT Consulting design, service conditions and/or referenced drawings. | 2023-04-15 | FAB0023
TNK18016 | 2018-04-20 | Fuelchief Limited 5 Tanya Street PO Box 41 029 Bromley, Christchurch | As of 02/04/2026: FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS 1692-2006, Category 3 | 1,000 L rectangular tank. Safe fill level: 887 L | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuelchief Limited 5 Tanya Street PO Box 41 029 Bromley, Christchurch | To be fitted with 50mm free to air vent. To be fitted with calibrated dip stick. | 2023-04-19 | As of 02/04/2026: FAB0093
TNK18017 | 2018-08-31 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Longveld Limited, 153-157 Ellis Street, Hamilton FAB0071 | AS 1692-2006, Category 5 | 16,388 L above ground cylindrical storage tank Safe Fill Level: 15,100 Litres | Nitric Acid 0.5 to 10% solution having a hazard classification of 6.1E, 6.9B, 8.1A, 8.2C, 8.3A. | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | 2023-08-30 | FAB0071
TNK18018 | 2018-08-31 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Longveld Limited, 153-157 Ellis Street, Hamilton FAB0071 | AS 1692-2006, Category 5 | 16,388 L above ground cylindrical storage tank Safe Fill Level: 15,100 Litres | 5% caustic CIP solution having hazard classifications of 6.1E, 8.1A, 8.2C, 8.3A. | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | 2023-08-30 | FAB0071
TNK18019 | 2018-05-23 | Petro Industrial Pty Limited Factory 2 - 106 Potassium Street PO Box 407 Narangba, Queensland 4504, Australia | Panus Assembly Co Limited 27/1 Moo 3 Koodngong Panusnikom Chonburi Thailand FAB0070 | AS1692 - 2006 Category 3 | Above ground double wall storage tank CUBE4995. Safe fill level: 4,700 L | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petro Industrial Pty Limited Factory 2 - 106 Potassium Street PO Box 407 Narangba, Queensland 4504, Australia | Must meet wind and seismic requirements specified un Austica Pty Ltd review to AS/NZS 1170.2 and AS/NZS 1170.5 dated 7 April 2018 Rev 0. Must be connected to a burner or fuel burning installation for compliance with regulatory requirements. | 2023-05-23 | FAB0070
TNK18020 | 2018-06-22 | Crusader Engineering Limited |  | Design Specification: API Standard 650 | Description: 22,000 litre Sarmic Oxcel storage tank Tank Type: Above Ground Stationary Tank Safe Fill Capacity: 20,000 litres Compartments: 1 Tank ID 2.8 m. Strake height 3.6 m Safe fill height 3.258 m (20,000 litres) Overflow height 3.34 m. Tank shell 8 mm. Tank roof 6 mm. Tank floor 10 mm. Corrosion allowance 1.0 mm. Joint efficiency 0.7 (no radiography) | Name: Sarmic Oxcel C Class(es): 6.1A, 6.1B, 6.1C, 6.5B, 6.6A, 8.1A, 8.2B, 8.3A | Crusader Engineering Limited | Seismic design to AS/NZS 1170.5:2014. 22m3 CCA tank design report (revision0) dated 16/3/2018. Tank location Kerikeri. Return period factor R 1.0 (50 year life, importance level 2). Hazard factor Z 0.13. Structural performance factor Sp 1.0 Wind assessment to AS/NZS 1170.2 Tank design API650 and FEA stress and displacement assessment tank design report (revision0) dated 16/3/2018 Appendix C. Zero nett overturning moment, seismic base shear 155kN. Mounting restraint by 6 number M20 x 210 mm galvenised 8.8 threaded rod with min 100mm embedment in slab. Tank venting to API2000. Max inflow rate 250 litres/minute. Max pump out rate 60 litres/minute. Sarmic Oxcel C... UN No. 2994 Hazchem code 2XE. SG 1.8 @ 20 deg C. Avoid contact with aluminium, zinc or galvanised iron | 2021-06-22
TNK18021 | 2018-07-19 | CT Engineering Services Ltd. |  | Design Specification: API Standard 650 | Description: CCA 10,600 litre storage tank 2.2m ID x 3m high Tank Type: Above Ground Stationary Tank Safe Fill Capacity: 10,600 litres Compartments: 1 | Name: CCA sg 2.0 Class(es): 6.1A Name: Tanalith C Oxide Class(es): 6.1B, 6.5A, 6.5B, 6.6A, 8.1A, 8.2B, 8.3A | CT Engineering Services Ltd. | Tank serial number T163HP1695. Product stored Lonza Tanalith C Oxide. Max SG 2.0. Seismic design to NZS 1170-5. CMK Engineering Pty Ltd design report C17066-T163HP1695 Rev 1. Z factor 0.33. Soil class C (shallow soil). Near fault factor 1. Site location Hautapu Pine Products Ltd, SH1, Taihape. No wind assessment to NZS 1170-2 required as tank stored in building. Design specification API 650 12th edition : 2013 including Addendum 1 & 2. Joint efficiency 0.7 (no radiography). Overfill protection 200mm down from top strake fitted with E-stop level switch system. Seismic slosh wave height 200mm above safe fill height. Max / min design temperature -10 to 50 deg C. Corrosion allowance 2mm. Tank roof 6mm m/s 250 Gr. Self supporting roof 10 degree slope. Tank strakes 6mm m/s 250 Gr. Tank floor 8mm m/s 250 Gr. Tank anchors 3 number M30 Gr 4.6 bolts at 120 degree spacing. Tank venting assessed to API2000 for 80mm id goose neck free vent.. Max pump in rate 1020 litres/minute. Max pump out rate 1020 litres/minute. | 2023-07-19
TNK18022 | 2018-07-20 | CT Engineering Services Ltd. |  | Design Specification: API Standard 650 | Description: 46,800 litre dilute CCA 1-6% storage tank Tank Type: Above Ground Stationary Tank Safe Fill Capacity: 46,800 litres Compartments: 1 | Name: Lonza dilute CCA 1-6% Class(es): 6.1D, 6.5A, 6.5B, 6.6A, 8.3A | CT Engineering Services Ltd. | Tank serial number T164HP1695. Product stored Lonza dilute CCA 1-6%. Max SG 1.1. Seismic design to NZS 1170-5. CMK Engineering Pty Ltd design report C17066-T164HP1695 Rev 1. Z factor 0.33. Soil class C (shallow soil). Near fault factor 1. Site location Hautapu Pine Products Ltd, SH1, Taihape. No wind assessment to NZS 1170-2 required as tank stored in building. Design specification API 650 12th edition : 2013 including Addendum 1 & 2. Joint efficiency 0.7 (no radiography). Overfill protection 200mm down from top strake fitted with E-stop level switch system. Seismic slosh wave height 250mm above safe fill height. Max / min design temperature -10 to 50 deg C. Corrosion allowance 2mm. Tank roof 8mm m/s 250 Gr. Self supporting roof 10 degree slope. Tank strakes 8mm m/s 250 Gr. Tank floor 10mm m/s 250 Gr. Tank anchors 6 number M30 Gr 4.6 bolts at 60 degree spacing. Tank venting assessed to API2000 for two 100mm NB goose neck free vents. Max pump in rate 8,100 litres/minute. Max pump out rate 8,100 litres/minute. | 2023-07-20
TNK18023 | 2018-09-15 | CT Engineering Services Ltd. |  | Design Specification: API Standard 650 | Description: 12,600 L storage tank 2.4m ID x 3 m high Tank Type: Above Ground Stationary Tank Capacity: 12,600 litres Compartments: 1 | Name: Koppers Sure Bor N Class(es): 6.5A, 6.5B | CT Engineering Services Ltd. | Tank serial number T165CH1731. Product stored Koppers Sure Bor N. Hazchem code 3Z. UN number 3082. SG 1.35 @ 20 deg C. Design SG 2.0. Seismic design to NZS 1170.5. CMK Engineering Pty Ltd design report C18052B-T165CH1731 Rev 0. Z factor (Kawerau) 0.29. Sub soil class D. Near fault 1.0 Site location Carter Holt Harvey, Kawerau. No wind assessment to NZS 1170.2 requires as tank stored inside building. Design specification API650 12th edition : 2013 inc Addendum 1 & 2. Joint efficiency 0.7 (no radiography). Corrosion allowance 2 mm. Seismic anchoring required 6 number equi spaced 25 mm shank diameter bolts. Hydrostatic pressure test and pneumatic pressure test of all tank compensating plates carried out 11 September 2018. Safe fill height 2.8 m. Overfill protection 200 mm down from top curb angle, fitted with E-stop level switch system. Slosh wave height 220 mm. | 2023-09-15
TNK18024 | 2018-06-15 | Mercer Stainless Limited 53 Lunns Road, Middleton Christchurch 8024. | Mercer Stainless Limited 53 Lunns Road, Middleton Christchurch 8024. FAB0077 | AS 1692 - 2006, Category 5 | 31,550 litre cylindrical vertical above ground tank Equipment Number: 5103TK02 Manufacture Year: 2018 Safe fill level: 30,000 L | 50% sodium hydroxide solution having a hazard classification of 6.1D, 6.1E, 8.1A, 8.2B, 8.3A, 9.1D | Mercer Stainless Limited New Plymouth Branch Corbett Road Bell Block New Plymouth 4341 |  | NA | FAB0077
TNK18025 | 2018-06-15 | Mercer Stainless Limited New Plymouth Branch Corbett Road Bell Block New Plymouth 4341 | Mercer Stainless Limited New Plymouth Branch Corbett Road Bell Block New Plymouth 4341 FAB0072 | AS 1692 - 2006, Category 4 | 6,386 litre cylindrical horizontal above ground tank Safe fill level: 6,000 L | Class 6.9B fire fighting foam concentrate. | Mercer Stainless Limited New Plymouth Branch Corbett Road Bell Block New Plymouth 4341 |  | NA | FAB0072
FAB0075 | 2018-07-10 |  | Oilcon 2018 Limited 14 Hewlett Street Whangarei 0110 | AS 1692-2006, Categories 1 to 5 incl. | Up to 50,000 litre tanks | Class 3 substances | Oilcon 2018 Limited | Fabrication, inspection and testing in accordance with the specified tank design code, approved tank design drawings and approved for construction drawings. Allocation of individual tank serial numbers. Retention of individual tank QA records. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2021-07-09 | Fabricator of: TNK0807, TNK0808 | 494/97, 512/97, 548/98, 549/98, 718/99
TNK18026 | 2018-05-15 | Fuelchief Limited 5 Tanya Street PO Box 41 029 Bromley, Christchurch | Quindao Jinhuanghai Container Co Ltd FAB0069 | AS 1692-2006 | Tank Type: Above Ground Stationary Tank Description: FT55 Containerised Rectangular Integral Secondary Contained Safe Fill Capacity: 54,000 litres | Name: Diesel UN1202/3082 Class(es):3.1D | Fuelchief Limited 5 Tanya Street PO Box 41 029 Bromley, Christchurch |  | 2028-05-14 | FAB0069
FAB0076 | 6/07/2018 30/06/2021 - Renewal |  | Fuelchief 5 Tanya Street PO Box 41 029 Bromley, Christchurch | AS1692 / UL142 / UL2085 | Tanks up to 110,000 litres Licensed by Southwest Research Institute (SwRI) to manufacture tanks tested in accordance with SwRI 93-01, 95-03, 97-04 Testing Procedures. Reference: TNK12004, 13011, 13013, 13014, 13015, 13017, 13058, 15001, 15024, 16017, 17011, 17012, 17021, 20019, 20020, 20023. 20032, 20084, 20208 | Refer to individual TNK registry allocation |  | Fabrication, inspection and testing in accordance with the specified tank design code, approved tank design drawings and approved for construction drawings. Allocation of individual tank serial numbers. Retention of individual tank QA records. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2024-06-30 | Fabricator of: TNK 12004, 13011, 13013, 13014, 13015, 13017, 13058, 15001, 15024, 16017, 17011, 17012, 17021, 20019, 20020, 20023, 20032, 20084
TNK18027 | 2018-07-30 | Visa S.p.a. Via I Maggio, 55 Fontanelle (TV) Italia | Visa S.p.a. Via I Maggio, 55 Fontanelle (TV) Italia FAB0061 | AS 1692 - 2006, Category 3 | 1,800 litre rectangular tank supplying a generator Make: Visa Equipment number: 241081100/101 | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Quality Power Limited 212 Crawford Street Dunedin South | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | 2028-07-29 | FAB0061
TNK18028 | 2018-07-30 | Visa S.p.a. Via I Maggio, 55 Fontanelle (TV) Italia | Visa S.p.a. Via I Maggio, 55 Fontanelle (TV) Italia FAB0061 | AS 1692 - 2006, Category 3 | 2,500 litre rectangular tank supplying a generator Make: Visa Equipment number: 241081067/068 | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Quality Power Limited 212 Crawford Street Dunedin South | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | 2028-07-29 | FAB0061
TNK18029 | 2018-08-02 | Panus Assembly Co Limited 27/1 Moo 3 Koodngong Panusnikom Chonburi Thailand | Panus Assembly Co Limited 27/1 Moo 3 Koodngong Panusnikom Chonburi Thailand FAB0070 | AS 1692 - 2006, Cat. 3 & R.S.C. SWI 13/11/17 | 16,000 litre above ground, double skin, horizontal tank. Safe fill level: 15,200 Litres | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petro Industrial Pty Limited Factory 2 - 106 Potassium Street PO Box 407 Narangba, Queensland 4504, Australia | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | 2023-08-01 | FAB0070
TNK18030 | 2018-07-20 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton FAB0071 | AS 1692-2006, Category 5 | 30,000 L above ground tank Safe fill level: 27,600 litres Tank serial number: 20949-TANK 13-A01 Equipment number: Q1TK0400 Manufacture year: 2017 | 10% CIP nitric acid solution having a hazard classification of 6.1E, 6.9B, 8.1A, 8.2C, 8.3A | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | N/A | FAB0071
TNK18031 | 2018-07-20 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton FAB0071 | AS 1692-2006, Category 5 | 30,000 L above ground tank Safe fill level: 27,600 litres Tank serial number: 20949-TANK 14-A01 Equipment number: Q1TK0300 Manufacture year: 2017 | CIP caustic solution up to 2% concentration having a hazard classification of 6.1E, 6.3A, 6.4A | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | N/A | FAB0071
TNK18032 | 2018-07-20 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton FAB0071 | AS 1692-2006, Category 5 | 30,000 L above ground tank Safe fill level: 27,600 litres Tank serial number: 20949-TANK 16-A01 Equipment number: Q2TK0400 Manufacture year: 2017 | 10% CIP nitric acid solution having a hazard classification of 6.1E, 6.9B, 8.1A, 8.2C, 8.3A | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | N/A | FAB0071
TNK18033 | 2018-07-20 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton FAB0071 | AS 1692-2006, Category 5 | 30,000 L above ground tank Safe fill level: 27,600 litres Tank serial number: 20949-TANK 17-A01 Equipment number: Q2TK0300 Manufacture year: 2017 | CIP caustic solution up to 2% concentration having a hazard classification of 6.1E, 6.3A, 6.4A | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | N/A | FAB0071
TNK18034 | 2018-07-20 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton FAB0071 | AS 1692-2006, Category 5 | 30,000 L above ground tank Safe fill level: 27,600 litres Tank serial number: 20949-TANK 18-A01 Equipment number: Q2TK0200 Manufacture year: 2017 | CIP caustic solution up to 2% concentration having a hazard classification of 6.1E, 6.3A, 6.4A. | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | N/A | FAB0071
TNK18035 | 2018-08-20 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS 1692 – 2006, Category 3 FAB0045 | 999 L tank connected to a generator Safe fill level: 949 litres | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Martin Engineering (Palmerston North) Ltd. |  | 2028-08-19 | FAB0045
TNK18036 | 2018-08-16 | Fuelcon Limited 84B Armstrong Street P O Box 9031 Palmerston North | Prior to 22/04/2021: Fuelcon Limited 84B Armstrong Street PO Box 9031 Palmerston North FAB0047 As of 22/04/2021: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692 - 2006, Category 4 | 2,517 litre single skin tank | Petrol having a hazard classification of 3.1A, 6.1E, 6.3B, 6.7B, 9.1B | Fuelcon Limited 84B Armstrong Street P O Box 9031 Palmerston North | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | 2028-08-15 | Prior to 22/04/2021: FAB0047 As of 22/04/2021: FAB0085 As of 17/10/2023: FAB0096
TNK18037 | 2018-08-28 | Martin Engineering (Palmerston North) Ltd. | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS 1692 – 2006, Category 3 FAB0045 | Double skin tanks Nominal tank sizes: 2,000 L, 2,500 L, 3,000 L & 3,500 L respectively. Maximum Safe Fill Volumes: 2,080 L, 2,598 L, 3,050 L & 3,500 L respectively. | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Martin Engineering (Palmerston North) Ltd. | Tank approved to supply a burner or engine. The capacity of the secondary tank exceeds 110% of the gross volume of the primary tank for the ranges specified | 2028-08-27 | FAB0045
FAB0077 | 2018-08-30 |  | Mercer Stainless Limited 53 Lunns Road, Middleton Christchurch 8024 and 5 Tanya Street, Bromley, Christchurch 8062 (as of 17/03/2022) | AS1692, BS EN 14015, API650 & API620 | Up to 100,000 litre tanks Reference: TNK18024, TNK18044, TNK18053, TNK18054, TNK20080, TNK20086, TNK20151, TNK20308, TNK20309, TNK20310, TNK20393, TNK20394, TNK20395 | Refer to individual TNK registry allocation | Mercer Stainless Limited 53 Lunns Road, Middleton Christchurch 8024 and 5 Tanya Street, Bromley, Christchurch 8062 (as of 17/03/2022) | Fabrication, inspection and testing in accordance with the specified tank design code, approved tank design drawings and approved for construction drawings. Allocation of individual tank serial numbers. Retention of individual tank QA records. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the compliance certifier who issued the compliance certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2024-06-30 | Fabricator of: TNK18024, TNK18044, TNK18053, TNK18054, TNK20080, TNK20086, TNK20151, TNK20308, TNK20309, TNK20310, TNK20393, TNK20394, TNK20395
TNK18038 | 2018-09-15 | CT Engineering Services Ltd. |  | Design Specification: API Standard 650 | Description: 12,600 L storage tank 2.4 m ID x 3 m high Tank Type: Above Ground Stationary Tank Capacity: 12,600 litres Compartments: 1 | Name: Koppers Sure Bor N Class(es): 6.5A, 6.5B | CT Engineering Services Ltd. | Tank serial number T166CH1731. Product stored Koppers Sure Bor N. Hazchem code 3Z. UN number 3082. SG 1.35 @ 20 deg C. Design SG 2.0. Seismic design to NZS 1170.5. CMK Engineering Pty Ltd design report C18052-T166CH1731 Rev 0. Z factor (Kawerau) 0.29. Sub soil class D. Near fault 1.0 Site location Carter Holt Harvey, Kawerau. No wind assessment to NZS 1170.2 requires as tank stored inside building. Design specification API650 12th edition : 2013 inc Addendum 1 & 2. Joint efficiency 0.7 (no radiography). Corrosion allowance 2 mm. Seismic anchoring required 6 number equi spaced 25 mm shank diameter bolts. Hydrostatic pressure test and pneumatic pressure test of all tank compensating plates carried out 11 September 2018. Safe fill height 2.8 m. Overfill protection 200 mm down from top curb angle, fitted with E-stop level switch system. Slosh wave height 220 mm. | 2023-09-15
TNK18039 | 2019-06-03 | CT Engineering Services Ltd. |  | Design Specification: API Standard 650 | Description: 42,750 L storage tank 3.6m ID x 4.4m high Tank serial No T167NS1688 Tank Type: Above Ground Stationary Tank Capacity: 42,750 litres Compartments: 1 | Name: Koppers SureBor 10.5% solution Class(es): 6.5A, 6.5B | CT Engineering Services Ltd. | Tank serial number T167NS1688. Product stored Koppers Sure Bor N dilute 10.5 % solution. Hazchem code 3Z. UN number 3082. Max design SG 1.1 Seismic design to NZS 1770-5. CMK Engineering Pty Ltd design report C19009-T167NS1688. No wind assessment to NZS 1170-2 as the tank is stored indoors. Z factor Ruakaka 0.13. Sub soil class D. Near fault 1.0. Site location Northsawn Ltd, Ruakaka, NZ. Tank design specification API650 12th edition:2013 inc Addendum 1 & 2. Joint efficiency 0.7 no radiography. Shell 8 mm m/s. Floor 10 mm m/s. Roof 8 mm m/s 10 degree pitch self supporting. Venting to API2000, 2 number 100 mm gooseneck vent pipes. Max pump in rate nd pump out rate 8,100 litres per minute. | 2024-06-03
TNK18040 | 2019-06-05 | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland |  | ASME RTP-1:2011 | 7,500 litres (Safe fill level) above ground stationary tank Seismic design: NZS 1170.5 Wind loadings: do not cover design Design pressure: atmospheric Venting: API2000 for max pump in rate 42 cubic metres / hr, max pump out - rate 0.72 cubic metres / hr. Top vent DN80 ANSI 150 connection Material: FRP (D411 VE resin / BPO cure) | Name: Sodium hypochlorite < 16% (Reflux S800) Class(es): 8.2A, 8.3A | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland | Site location: Fonterra, 520 Awakeri Road, Edgecumbe. | 2024-06-05
TNK18041 | 2019-06-06 | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland |  | ASME RPT-1:2011 | 18,880 litres (Safe fill level) above ground stationary tank Tank serial number: MT416 Wind and Seismic design: NZS1170.2 and 1170.5 Design pressure: atmospheric Venting: API2000 for max pump in rate 42 cubic metres / hr, max pump out rate 0.72 cubic metres / hr. Top vent DN150. Material: GRP, resin H922 colour Moonstone | Name: Hydrofluorosilicic acid 25% Class(es): 8.1A, 8.2A, 8.2B, 8.2C, 8.3A | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland | Site location: Ballance Agri Nutrients, Tauranga. | 2024-06-06
TNK18042 | 2019-06-10 | Robin King Engineers Ltd. |  | Design Specification: API Standard 650 | Description: 60,000 litre resin tank OD 4.31m x 5m high x 4 strakes 5 mm. Tank Type: Above Ground Stationary Tank Capacity: 60,000 litres Compartments: 1 | Name: Sylvic M5531 bulk Class(es): 6.1A | Contract Mechanical Services Limited | 60,000 litre 304L grade stainless steel resin tank to API650 Annex S. Design temperature 40 deg C. 1.3 degree fall of floor. Joint efficience 0.7 (no radiography). Safe fill height 4.2m. High level alarm 4.35m. High high level alarm 4.5m. Overflow 4.65m. Roof pitch 10 degrees. Top curb angle 50 x 50 x 6mm. Design life 50 years. Location Hexion, 165 Totara Street, Mt Maunganui. Wind and seismic design to NZS1170-2 and 1170.5 Robin King Engineers Ltd report 14 September 2018. Seismic zone 0.2. Probability of exceedence 1/100. Maximum specific gravity 1.2. Sp=1.0 Site subsoil class D. Tank design pressure 1.0 kPa. Design vacuum 0.25 KPa. Venting to API2000. Maximum fill rate 530.6 litres / minute. Maximum pump out rate 166.7litres / minute. 100 mm gooseneck natural vent fitted with birdmesh. Anchoring: 6 anchors required M24 with 160 mm embeddment Epcon C6. Minimum concrete thickness at anchors 185 mm, minimum edge distance 100 mm | 2024-06-10
TNK18043 | 2019-06-13 | CT Engineering Services Ltd. |  | API Standard 650 | Description: 15,550 L tanalith oxide storage tank 3.0m dia x 2.4m high Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Capacity: 15,550 litres Compartments: 1 | Name: Lonza Tanalith C Oxide Class(es): 6.1A, 6.1B, 6.1C, 8.1A | CT Engineering Services Ltd. | Tank serial number T168LO1740. Product stored Tanalith C Oxide. Hazchem code 2X. UN number 2922. CA 2.0 mm. Max SG 2.0. Seismic design to NZS1170-5. Seismic design by CMK Engineering Pty Ltd design report C19021-T168LO1740 Rev 0. Z factor Tokoroa 0.21. Sub soil class D. Near fault 1.0. Site location 2988 Old Taupo Rd, Tokoroa. No wind assesment to NZS1170-2 as tank is stored inside building. Design specification API 650 12th edition:2013. Joint efficiency 0.7 (no radiography). Venting to API 2000. Max pump in and pump out rates 800L/min. Hydrostatic test 12/6/19. | 2024-06-13
TNK18044 | 2018-10-01 | Mercer Stainless Limited 53 Lunns Road Middleton, Christchurch 8024 | Mercer Stainless Limited 53 Lunns Road Middleton, Christchurch 8024 FAB0077 | AS 1692 - 2006, Category 4 | 5,445 litre cylindrical horizontal above ground tank Safe fill level: 5,000 litres | Class 6.9B fire fighting foam concentrate. | Mercer Stainless Limited 53 Lunns Road Middleton, Christchurch 8024 | This approval becomes invalid following any change to referenced drawings, change of service or change of duty. | 2028-09-30 | FAB0077
TNK18045 | 2015-07-15 | Pre 31/03/2022 PK Engineering (Nelson) Ltd. As of 31/03/2022 NPD LIMITED PO Box 3412, Richmond, Nelson 13 McPherson Street, Richmond, 7020 | Pre 31/03/2022 FAB0078 (PK Engineering (Nelson) Ltd.) As of 31/03/2022 FAB0023 (Nymic Engineering Ltd. for NPD Ltd.) As of 27/03/2023 A W TRINDER LIMITED PO Box 3143, Richmond, 7050 2 Poutama Street, Richmond, 7020 FAB0092 | AS1692 – 2006, Category 3 | Pre 31/03/2022 5,000 L above ground steel stationary container with integral secondary containment Material: 4 mm mild steel inner and outer shell As of 31/03/2022 Description: 5,000 Litres Double Skinned Rectangular Above Ground Stationary Tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: NPD - AM Capacity: 5,155 Litres Maximum Safe Fill Level: 4,700 Litres Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Pre 31/03/2022 PK Engineering (Nelson) Ltd. As of 31/03/2022 NPD LIMITED PO Box 3412, Richmond, Nelson 13 McPherson Street, Richmond, 7020 | As of 31/03/2022 Design Certificate - Certificate No.: 06206. Issued by: Lance Kennedy Hope, Issued to: Nelson Petroleum Distributors Ltd, In respect of: Diesel Storage Tank 5 kl. AS 1692:2006, AS 1210:2010 & AS/NZS 1170:5. Dated: 15/05/2015. Wind & Seismic file reference No.: 05689 - A, date 2/07/2014. If manufacturing of this tank is for a different site/s other than the one listed in the Certificate of Design, Certificate No.: 06206 and referenced Wind & Seismic file reference No.: 05689 - A above a new producer statement (PS1) will need to be provided to confirm the compliance with the wind & seismic requirements in the Health and Safety at Work (Hazardous Substances) Regulations 2017, Clause 17.6(3). Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced drawings or applicable standard/s. | 2032-03-31 | Pre 31/03/2022 FAB0078 (PK Engineering (Nelson) Ltd.) As of 31/03/2022 FAB0023 (Nymic Engineering Ltd. for NPD Ltd.) As of 27/03/2023 FAB0092 (A W TRINDER LIMITED)
TNK18046 | 2015-10-27 | Pre 31/03/2022 PK Engineering (Nelson) Ltd. As of 31/03/2022 NPD LIMITED PO Box 3412, Richmond, Nelson 13 McPherson Street, Richmond, 7020 | Pre 31/03/2022 FAB0078 (PK Engineering (Nelson) Ltd.) As of 31/03/2022 FAB0023 (Nymic Engineering Ltd. for NPD Ltd.) As of 27/03/2023 A W TRINDER LIMITED PO Box 3143, Richmond, 7050 2 Poutama Street, Richmond, 7020 FAB0092 | AS1692 – 2006, Category 3 | Pre 31/03/2022 10,000 L above ground steel stationary container with integral secondary containment Material: 6 mm mild steel inner and outer shell As of 31/03/2022 Description: 10,000 Litres Double Skinned Rectangular Above Ground Stationary Tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: NPD - AM Capacity: 11,030 Litres Maximum Safe Fill Level: 10,000 Litres Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Pre 31/03/2022 PK Engineering (Nelson) Ltd. As of 31/03/2022 NPD LIMITED PO Box 3412, Richmond, Nelson 13 McPherson Street, Richmond, 7020 | As of 31/03/2022 Design Certificate - Certificate No.: 06207. Issued by: Lance Kennedy Hope, Issued to: Nelson Petroleum Distributors Ltd, In respect of: Diesel Storage Tank 10 kl. AS 1692:2006, AS 1210:2010 & AS/NZS 1170:5. Dated: 15/05/2015. Wind & Seismic file reference No.: 05689 - A, date 2/07/2014. If manufacturing of this tank is for a different site/s other than the one listed in the Certificate of Design, Certificate No.: 06207 and referenced Wind & Seismic file reference No.: 05689 - A above a new producer statement (PS1) will need to be provided to confirm the compliance with the wind & seismic requirements in the Health and Safety at Work (Hazardous Substances) Regulations 2017, Clause 17.6(3). Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced drawings or applicable standard/s. | 2032-03-31 | Pre 31/03/2022 FAB0078 (PK Engineering (Nelson) Ltd.) As of 31/03/2022 FAB0023 (Nymic Engineering Ltd. for NPD Ltd.) As of 27/03/2023 FAB0092 (A W TRINDER LIMITED)
TNK18047 | 2015-05-15 | Pre 31/03/2022 PK Engineering (Nelson) Ltd. As of 31/03/2022 NPD LIMITED PO Box 3412, Richmond, Nelson 13 McPherson Street, Richmond, 7020 | Pre 31/03/2022 FAB0078 (PK Engineering (Nelson) Ltd.) As of 31/03/2022 FAB0023 (Nymic Engineering Ltd. for NPD Ltd.) As of 27/03/2023 A W TRINDER LIMITED PO Box 3143, Richmond, 7050 2 Poutama Street, Richmond, 7020 FAB0092 | AS1692 – 2006, Category 3 | Pre 31/03/2022 15,000 L above ground steel stationary container with integral secondary containment Material: 6 mm mild steel inner and outer shell As of 31/03/2022 Description: 15,000 Litres Double Skinned Rectangular Above Ground Stationary Tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: NPD - AM Capacity: 16,421 Litres Maximum Safe Fill Level: 15,000 Litres Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Pre 31/03/2022 PK Engineering (Nelson) Ltd. As of 31/03/2022 NPD LIMITED PO Box 3412, Richmond, Nelson 13 McPherson Street, Richmond, 7020 | As of 31/03/2022 Design Certificate - Certificate No.: 05862. Issued by: Lance Kennedy Hope, Issued to: Nelson Petroleum Distributors Ltd, In respect of: Diesel storage tank 15 kl. AS 1692:2006, AS 1210:2010 & AS/NZS 1170:5. Dated: 15/05/2015. Wind & Seismic file reference No.: 05689 - A, date 27/06/2014. If manufacturing of this tank is for a different site/s other than the one listed in the Certificate of Design, Certificate No.: 05862 and referenced Wind & Seismic file reference No.: 05689 - A above a new producer statement (PS1) will need to be provided to confirm the compliance with the wind & seismic requirements in the Health and Safety at Work (Hazardous Substances) Regulations 2017, Clause 17.6(3). Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced drawings or applicable standard/s. | 2032-03-31 | Pre 31/03/2022 FAB0078 (PK Engineering (Nelson) Ltd.) As of 31/03/2022 FAB0023 (Nymic Engineering Ltd. for NPD Ltd.) As of 27/03/2023 FAB0092 (A W TRINDER LIMITED)
TNK18048 | 2015-10-27 | Pre 31/03/2022 PK Engineering (Nelson) Ltd. As of 31/03/2022 NPD LIMITED PO Box 3412, Richmond, Nelson 13 McPherson Street, Richmond, 7020 | Pre 31/03/2022 FAB0078 (PK Engineering (Nelson) Ltd.) As of 31/03/2022 FAB0023 (Nymic Engineering Ltd. for NPD Ltd.) As of 27/03/2023 A W TRINDER LIMITED PO Box 3143, Richmond, 7050 2 Poutama Street, Richmond, 7020 FAB0092 | AS1692 – 2006, Category 3 | Pre 31/03/2022 20,000 L above ground steel stationary container with integral secondary containment Material: 6 mm mild steel inner and outer shell As of 31/03/2022 Description: 20,000 Litres Double Skinned Rectangular Above Ground Stationary Tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: NPD - AM Capacity: 21,362 Litres Maximum Safe Fill Level: 20,000 Litres Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Pre 31/03/2022 PK Engineering (Nelson) Ltd. As of 31/03/2022 NPD LIMITED PO Box 3412, Richmond, Nelson 13 McPherson Street, Richmond, 7020 | As of 31/03/2022 Design Certificate - Certificate No.: 06209. Issued by: Lance Kennedy Hope, Issued to: Nelson Petroleum Distributors Ltd, In respect of: Diesel storage tank 20 kl. AS 1692:2006, AS 1210:2010 & AS/NZS 1170:5. Dated: 20/05/2015. Wind & Seismic file reference No.: 05689 - A, date 27/06/2014. If manufacturing of this tank is for a different site/s other than the one listed in the Certificate of Design, Certificate No.: 06209 and referenced Wind & Seismic file reference No.: 05689 - A above a new producer statement (PS1) will need to be provided to confirm the compliance with the wind & seismic requirements in the Health and Safety at Work (Hazardous Substances) Regulations 2017, Clause 17.6(3). Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced drawings or applicable standard/s. | 2032-03-31 | Pre 31/03/2022 FAB0078 (PK Engineering (Nelson) Ltd.) As of 31/03/2022 FAB0023 (Nymic Engineering Ltd. for NPD Ltd.) As of 27/03/2023 FAB0092 (A W TRINDER LIMITED)
TNK18049 | 2015-10-27 | Pre 31/03/2022 PK Engineering (Nelson) Ltd. As of 31/03/2022 NPD LIMITED PO Box 3412, Richmond, Nelson 13 McPherson Street, Richmond, 7020 | Pre 31/03/2022 FAB0078 (PK Engineering (Nelson) Ltd.) As of 31/03/2022 FAB0023 (Nymic Engineering Ltd. for NPD Ltd.) As of 27/03/2023 A W TRINDER LIMITED PO Box 3143, Richmond, 7050 2 Poutama Street, Richmond, 7020 FAB0092 | AS1692 – 2006, Category 3 | Pre 31/03/2022 25,000 L above ground steel stationary container with integral secondary containment Material: 6 mm mild steel inner and outer shell As of 31/03/2022 Description: 25,000 Litres Double Skinned Rectangular Above Ground Stationary Tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: NPD - AM Capacity: 26,673 Litres Maximum Safe Fill Level: 25,000 Litres Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Pre 31/03/2022 PK Engineering (Nelson) Ltd. As of 31/03/2022 NPD LIMITED PO Box 3412, Richmond, Nelson 13 McPherson Street, Richmond, 7020 | As of 31/03/2022 Design Certificate - Certificate No.: 06210. Issued by: Lance Kennedy Hope, Issued to: Nelson Petroleum Distributors Ltd, In respect of: Diesel storage tank 25 kl. AS 1692:2006, AS 1210:2010 & AS/NZS 1170:5. Dated: 20/05/2015. Wind & Seismic file reference No.: 05689 - A, date 27/06/2014. If manufacturing of this tank is for a different site/s other than the one listed in the Certificate of Design, Certificate No.: 06210 and referenced Wind & Seismic file reference No.: 05689 - A above a new producer statement (PS1) will need to be provided to confirm the compliance with the wind & seismic requirements in the Health and Safety at Work (Hazardous Substances) Regulations 2017, Clause 17.6(3). Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced drawings or applicable standard/s. | 2032-03-31 | Pre 31/03/2022 FAB0078 (PK Engineering (Nelson) Ltd.) As of 31/03/2022 FAB0023 (Nymic Engineering Ltd. for NPD Ltd.) As of 27/03/2023 FAB0092 (A W TRINDER LIMITED)
TNK18050 | 2015-10-27 | Pre 31/03/2022 PK Engineering (Nelson) Ltd. As of 31/03/2022 NPD LIMITED PO Box 3412, Richmond, Nelson 13 McPherson Street, Richmond, 7020 | Pre 31/03/2022 FAB0078 (PK Engineering (Nelson) Ltd.) As of 31/03/2022 FAB0023 (Nymic Engineering Ltd. for NPD Ltd.) As of 27/03/2023 A W TRINDER LIMITED PO Box 3143, Richmond, 7050 2 Poutama Street, Richmond, 7020 FAB0092 | AS1692 – 2006, Category 3 | Pre 31/03/2022 30,000 L above ground steel stationary container with integral secondary containment Material: 6 mm mild steel inner and outer shell As of 31/03/2022 Description: 30,000 Litres Double Skinned Rectangular Above Ground Stationary Tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: NPD - AM Capacity: 31,493 Litres Maximum Safe Fill Level: 30,000 Litres Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Pre 31/03/2022 PK Engineering (Nelson) Ltd. As of 31/03/2022 NPD LIMITED PO Box 3412, Richmond, Nelson 13 McPherson Street, Richmond, 7020 | As of 31/03/2022 Design Certificate - Certificate No.: 06211. Issued by: Lance Kennedy Hope, Issued to: Nelson Petroleum Distributors Ltd, In respect of: Diesel storage tank 30 kl. AS 1692:2006, AS 1210:2010 & AS/NZS 1170:5. Dated: 20/05/2015. Wind & Seismic file reference No.: 05689 - A, date 27/06/2014. If manufacturing of this tank is for a different site/s other than the one listed in the Certificate of Design, Certificate No.: 06211 and referenced Wind & Seismic file reference No.: 05689 - A above a new producer statement (PS1) will need to be provided to confirm the compliance with the wind & seismic requirements in the Health and Safety at Work (Hazardous Substances) Regulations 2017, Clause 17.6(3). Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced drawings or applicable standard/s. | 2032-03-31 | Pre 31/03/2022 FAB0078 (PK Engineering (Nelson) Ltd.) As of 31/03/2022 FAB0023 (Nymic Engineering Ltd. for NPD Ltd.) As of 27/03/2023 FAB0092 (A W TRINDER LIMITED)
FAB0078 | 2015-05-15 |  | PK Engineering (Nelson) Ltd. | AS1692 – 2006, Category 3 | Above ground single compartment steel stationary containers with secondary containment | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | PK Engineering (Nelson) Ltd. | The approval becomes invalid if change of design or workshop quality assurance systems change. | 2018-05-15 | Fabricator of: TNK18045, TNK18046, TNK18047, TNK18048, TNK18049, TNK18050
TNK18053 | 2018-10-18 | Mercer Stainless Limited 53 Lunns Road Middleton Christchurch 8024 | Mercer Stainless Limited 53 Lunns Road Middleton Christchurch 8024 FAB0077 | AS1692-2006, Category 5 | 6,443 litre cylindrical, vertical above ground CIP rinse tank | Sodium hydroxide up to 5% concentration having hazard classifications of 6.1E, 6.9B, 8.1A, 8.2C, 8.3A or nitric acid up to 2% concentration having hazard classifications of 6.1E, 6.9B, 8.1A, 8.2C, 8.3A. | Mercer Stainless Limited 53 Lunns Road Middleton Christchurch 8024 | This approval becomes invalid following any change to the referenced design, service conditions or referenced drawings | 2028-10-17 | FAB0077
TNK18054 | 2018-10-18 | Mercer Stainless Limited 53 Lunns Road Middleton Christchurch 8024 | Mercer Stainless Limited 53 Lunns Road Middleton Christchurch 8024 FAB0077 | AS1692-2006, Category 5 | 6,443 litre cylindrical, vertical above ground pre-rinse tank | Sodium hydroxide up to 5% concentration having hazard classifications of 6.1E, 6.9B, 8.1A, 8.2C, 8.3A or nitric acid up to 2% concentration having hazard classifications of 6.1E, 6.9B, 8.1A, 8.2C, 8.3A. | Mercer Stainless Limited 53 Lunns Road Middleton Christchurch 8024 | This approval becomes invalid following any change to the referenced design, service conditions or referenced drawings | 2028-10-17 | FAB0077
TNK18055 | 2018-11-05 | Martin Engineering (PN) Ltd, Palmerston North | Martin Engineering (PN) Ltd, Palmerston North FAB0045 | AS 1692 – 2006, Category 4 | 5,000 to 16,000 litre cylindrical, horizontal, single skin above ground tank | Flammable liquid class 3.1A, B, C or D | Martin Engineering (PN) Ltd, Palmerston North | This approval becomes invalid following any change to the referenced design drawings. | 2028-11-04 | FAB0045
TNK18056 | 2018-12-13 | Martin Engineering (PN) Ltd, Palmerston North | Martin Engineering (PN) Ltd, Palmerston North FAB0045 | AS 1692 – 2006, Category 4 | 20,000 to 60,000 litre cylindrical, horizontal, single skin above ground tanks | Flammable liquids having hazard classifications of 3.1A, 3.1B, 3.1C or 3.1D | Martin Engineering (PN) Ltd, Palmerston North | Tank specific vent design required. Randalll & Associates Wind & Seismic Design Compliance Certificate MS 54848. | 2028-12-13 | FAB0045
TNK18057 | 2017-11-06 | Martin Engineering (PN) Ltd, Palmerston North | Martin Engineering (PN) Ltd, Palmerston North FAB0045 | AS 1692 – 2006, Category 4 | 52,350 litre three compartments above ground tank Manufacture Year: 2017 Safe fill level: 50,640 Litres | Methanol having a hazard classification of 3.1B, 6.1D, 6.4A, 6.8B, 6.9A, 9.3C | Martin Engineering (PN) Ltd, Palmerston North | This approval becomes invalid following any change to the referenced contents, design, duty, service conditions or referenced drawings | N/A | FAB0045
TNK18058 | 2017-11-06 | Martin Engineering (PN) Ltd, Palmerston North | Martin Engineering (PN) Ltd, Palmerston North FAB0045 | AS 1692 – 2006, Category 4 | 14,925 litre three compartments above ground tank Manufacture Year: 2017 Safe fill level: 14,480 Litres | Toluene having a hazard classification of 3.1B, 6.1D, 6.3A, 6.4A, 6.8B, 6.9B, 9.1D, 9.3C. | Martin Engineering (PN) Ltd, Palmerston North | This approval becomes invalid following any change to the referenced contents, design, duty, service conditions or referenced drawings | N/A | FAB0045
TNK18059 | 2017-11-06 | Martin Engineering (PN) Ltd, Palmerston North | Martin Engineering (PN) Ltd, Palmerston North FAB0045 | AS 1692 – 2006, Category 4 | 25,360 litre three compartments above ground tank Manufacture Year: 2017 Safe fill level: 24,605 Litres | Isopropyl alcohol having a hazard classification of 3.1B, 6.1E, 6.3B, 6.4A. | Martin Engineering (PN) Ltd, Palmerston North | This approval becomes invalid following any change to the referenced contents, design, duty, service conditions or referenced drawings | N/A | FAB0045
TNK19000 | 2019-01-22 | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu FAB0050 | AS 1692 - 2006, Category 3 | 600 litre overhead tank | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu | This approval becomes invalid following any change to the referenced design drawings. Approved to supply a burner or engine. | 2029-01-22 | FAB0050
TNK19001 | 2019-01-22 | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu FAB0050 | AS 1692 - 2006, Category 3 | 950 litre overhead tank | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu | This approval becomes invalid following any change to the referenced design drawings. Approved to supply a burner or engine. | 2029-01-22 | FAB0050
TNK19002 | 2019-01-22 | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu FAB0050 | AS 1692 - 2006, Category 3 | 1,350 litre overhead tank | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu | This approval becomes invalid following any change to the referenced design drawings. Approved to supply a burner or engine. | 2029-01-22 | FAB0050
TNK19003 | 2019-01-22 | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu FAB0050 | AS 1692 - 2006, Category 3 | 1,870 litre overhead tank | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu | This approval becomes invalid following any change to the referenced design drawings. Approved to supply a burner or engine. | 2029-01-22 | FAB0050
TNK19004 | 2019-02-11 | NYMIC Engineering Limited | NYMIC Engineering Ltd FAB0023 | AS 1692 - 2006, Category 4 | 59,700 litre single skin above ground horizontal fuel storage tank Safe Fill Level: 58,200 litres | Flammable liquids having hazard classifications of 3.1A, 3.1B, 3.1C or 3.1D | NYMIC Engineering Limited | This approval becomes invalid following any change to the BVT Consulting design, service conditions and/or referenced drawings. | N/A | FAB0023
TNK19005 | 2019-03-19 | IT Power Services Limited 13A Piermark Drive Albany, North Shore City, Auckland | Mainline Sheetmetals Limited 209 Ellis Street Frankton Hamilton FAB0018 (until 18/10/2019) | UL142 & Generator Set Safe Work Instrument (dated 15-11-17) | 2,300 litre rectangular generator base tank | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | IT Power Services Limited 13A Piermark Drive Albany, North Shore City, Auckland | This approval becomes invalid following any change to the referenced designs and drawings. | 2029-03-15 | FAB0018 (until 18/10/2019)
TNK19006 | 2019-09-26 | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland |  | ASME RTP-1:2015 | Description: 3m diameter x 6.18m high GRP hydrofluorosilicic acid tank Design Specification: ASME RTP-1:2015 Tank Type: Above Ground Stationary Tank Name of Designer: Maskell Productions Capacity: 39,000 L Compartments: 1 | Name: Hydrofluorosilicic acid 25% Class(es): 8.1A, 8.2A, 8.2B, 8.2C, 8.3A | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland | Tank serial number MT400. Product stored HFA 25%. UN No 1778. Max SG 1.3. Wind and seismic design to NZS1170.5 and NZS1170.2 Maskell Tank Design dated 18/1/19. Subsoil class D. Zone factor 0.2. Structural performance factor 1.0. Ductility factor 1.25. Limit state factor 1.0. Site location Ballance Agrinutrients, Tauranga. Design code ASME RPT-1:2011. Design pressure Atmospheric. Safe fill capacity 39,000 litres. Safe fill height 5.52m from base of tank. Venting to API2000 for maximum pump in and pump out rate of 17 cubic metres / hr. Top vent DN150. Tank height base to top of dome 6.642m. 8 number M24 Gr 8.8 hold down bolts. Material GRP, resin H992 colour moonstone. Hydrostatic pressure test 25 September 2019. | 2024-09-26
TNK19007 | 2020-03-13 | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland |  | UL 1316:1994 (2nd Edition) | Description: 30,000 L 2.5m diameter x 6.75 shell length UGST Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Name of Designer: Maskell Productions / Clarke Engineers Texas. Capacity: 30,000 L Compartments: 1 | Name: Methanol / waste oil Class(es): 3.1B, 6.1D | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland | Tank serial number 21728. Product stored Methanol / Waste oil. UN No. 1230. Max sg 1.0 Site location Omata, New Plymouth. Design code UL1316:2018. Double wall underground storage tank fitted with hydroguard monitoring system. Resin compatability with methanol : Derakane 470-300 Momentum epoxy vinylester resin / MEKP Norox 925H. Max service temperature 40 deg C. SG 0.79 to1.0. Max liquid level 29,413 L. Safe fill height 2245mm. Outside diameter 2590mm. Overall length 6750mm. John Milton Clark Engineers, Texas tank design dated 10/31/2019, and revision dated 12/11//19 for 10 rib configuration. Clark Engineers tank centre joint design sheets. Mat rove lay up exterior centre joint dated 10/31/2019. Mat only lay up interior centre joint dated 11/4/2019. Design pressure 35 kPa. Design vacuum -35 kPa. Venting calculation to API2000 for max pump in rate 98.8 cubic metres per hour and max pump out rate 50 cubic metres per hour. Installation in accordance with Envirotank Installation procedures for petroleum storage tanks. Publication No. INST INS 02 Rev Jan 2011. CA 0. | 2025-03-13
TNK19008 | 2020-02-11 | Contract Mechanical Services Limited 11 Harvard Way, Mt Maunganui |  | API Standard 650 | Description: 60,000 litre stainless steel resin storage tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Contract Mechanical Services Ltd Capacity: 60,000 litres Compartments: 1 | Name: Cascomel M5610, Sylvic M227 Class(es): 6.5B | Contract Mechanical Services Limited 11 Harvard Way, Mt Maunganui | 60,000 litre 304L grade stainless steel resin tank to API650 Annex S and Annex J. Design temperature 40 deg C. OD 4.3m x 5m high x 4 strakes 5 mm. 1.3 degree fall of floor. Joint efficience 0.7 (no radiography). Safe fill height 4.2m. High level alarm 4.35m. High high level alarm 4.5m. Overflow 4.65m. Roof pitch 10 degrees. Top curb angle 50 x 50 x 6mm. Design life 50 years. Location Hexion, 165 Totara Street, Mt Maunganui. Wind and seismic design to NZS1170-2 and 1170.5 Robin King Engineers Ltd report 7 August 2019. Seismic zone 0.2. Maximum specific gravity 1.29. Sp=1.0 Site subsoil class D. Tank design pressure 1.0 kPa. Design vacuum -0.25 KPa. Venting to API2000. Maximum fill rate 530.6 litres / minute. Maximum pump out rate 166.7litres / minute. 102.26 mm ID gooseneck natural vent fitted with birdmesh. Anchoring: 6 anchors required M24 with 160 mm embeddment Epcon C6. Minimum concrete thickness at anchors 200 mm, minimum edge distance 100 mm. Concrete strength 30 MPa. | 2025-02-11
TNK19009 | 2020-08-06 | Contract Mechanical Services Limited 11 Harvard Way, Mt Maunganui |  | API Standard 650 Annex S and Annex J. | 80,000 L, 304L grade stainless steel resin tank Above Ground Stationary Tank Tank serial number: 5T40 Design temperature: 40 degree Celsius Outer Diameter: 4.5m x 5.926m high x 5mm strakes 1.3 degree fall of floor Joint efficience: 0.7 (no radiography) Safe fill height: 5.2 m High level alarm: 5.35 m High high level alarm: 5.5 m Overflow: 5.65 m Roof pitch:10 degrees Top curb channel 100PFC Design life: 50 years Tank design pressure: 1.0 kPa Design vacuum: -0.25 KPa Venting to API2000 Maximum fill rate: 1,000 L / minute Maximum pump out rate: 3183.3 L / minute 102.26 mm ID goose neck natural vent fitted with birdmesh | Name: Melamine urea formaldehyde Casco resin(TM) U1189 and Phenol formaldehyde resin Cascophen TM P6621 Class(es): 6.1D, 8.2B, 8.3A | Contract Mechanical Services Limited 11 Harvard Way, Mt Maunganui | Location Hexion, 165 Totara Street, Mt Maunganui. Wind and seismic design to NZS1170-2 and 1170.5. NZSEE:2009 - Robin King Engineers Ltd report 3 February 2020. Seismic zone: 0.2. Maximum specific gravity: 1.29. Sp: 1.0 Site subsoil class D. Anchoring: 6 anchors required M30 on 4.63 m PCD. 280 mm embedment, Epcon C6. Minimum concrete thickness at anchors 350 mm, minimum edge distance 240 mm. Concrete strength 30 MPa. | 2025-08-06
TNK19010 | 2020-06-18 | Robin King Engineers Ltd |  | API Standard 650 | Description: 5,000 litre 316L grade stainless steel sulphuric acid tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Robin King Engineers Ltd Capacity: 5,000 L Compartments: 1 Tank serial number: 0601-ST17 | Name: 98% sulphuric acid Class(es): 6.1B, 8.1A, 8.2B, 8.3A | Contract Mechanical Services Limited 11 Harvard Way, Mt Maunganui | Design temperature: 40 degrees celcius O.D.: 1.69m x 2.5m high x 5mm strake, roof and floor Joint efficiency: 0.7 (no radiography) Safe fill height: 2.29m High level alarm: 2.315m High high level alarm: 2.34m Overflow: 2.36m Roor pitch: 10 degrees Design life 50 years Corrosion allowance: 0 Location: Ballance Agri Nutrients Ltd, 294 Kiwitahi Rd, Morrinsville. Wind and seismic design to NZS 1170.2 and 1170.5, Robin King Engineers Ltd, Report dated 9 April 2020. Seismic zone: 0.18 Maximum specific gravity: 1.84 Sp: 1.0 Site subsoil: class D Tank design pressure: 1.0kPa. Tank design vacuum: 0.25kPa. Tank venting to: API2000. Maximum fill rate: 500 litres / minute. Maximum pump out rate: 500 litres / minute. 100 mm gooseneck natural vent fitted with 140mm diameter rolled breather tube with 12 slots 16mm x 94mm equispaced with bottom drip collection plate return to top flange. Anchors four M24 with 160mm embedment Epcon C6. Minimum concrete thickness at anchors: 220mm Minimum edge distance: 150mm Anchor PCD: 1812mm | 2025-06-18
TNK19011 | 2019-04-30 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton FAB0071 | AS 1692-2006, Category 5 | 20,990 litre vertical cylindrical above ground tank. Safe Fill Level: 20,000 Litres | 50% sodium hydroxide solution having a hazard classification of 6.1D, 6.1E, 8.1A, 8.2B, 8.3A, 9.1D | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton FAB0071 | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | N/A | FAB0071
TNK19012 | 2019-04-30 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton FAB0071 | AS 1692-2006, Category 5 | 20,990 litre vertical cylindrical above ground tank Safe Fill Level: 20,000 Litres | 69% Nitric Acid having a hazard classification of 5.1.1C, 6.1D, 6.9B, 8.1A, 8.2B, 8.3A | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton FAB0071 | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | N/A | FAB0071
TNK19013 | 2019-04-30 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton FAB0071 | AS 1692 - 2006, Category 5 | 36,015 litre vertical cylindrical above ground CIP storage tank Safe Fill Level: 35,000 Litres | Nitric Acid 0.5% to 10% CIP solution having a hazard classification of 6.1E, 6.9B, 8.1A, 8.2C, 8.3A | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton FAB0071 | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | N/A | FAB0071
TNK19014 | 2019-04-16 | Greentank Limited | Greentank Ltd 16 Donald Street Kaikorai Valley Dunedin FAB0001 FAB0019 | UL 1316: 1194 second edition | Description: Below ground dual compartment Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Name of Designer: Greentank Ltd. Capacity: 51,299 L and 21,362 L dual compartment Split Tank: Yes Compartments: 2 | Name: Hazardous Liquids Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Greentank Limited 16 Donald Street, Kenmure, Dunedin, 9011 | This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | 2039-04-16 | FAB0001 (22/06/2007) FAB0019 (19/02/2012)
TNK19015 | 2019-04-24 | APD Ltd 49 McLauglins Road Wiri Auckland 2104 | APD Ltd PO Box 12663 Penrose, Auckland 1642 49 McLaughlins Road, Wiri, Auckland, 2104 FAB0032 | BS EN 12573 / Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Up to 60,000 L vertical cylindrical above ground tank | Hazardous liquids other than class 3.1 substances; sulphuric acid (>80% concentration); nitric acid (>10% concentration); hydrogen peroxide (>20% concentration); or sodium hypochlorite. | APD Ltd 49 McLauglins Road Wiri Auckland 2104 | Specific design based on approved APD tank design matrix. Individual tank specific serial number and compliant name plate required. This approval becomes invalid following any change to the referenced designs and drawings. | 2029-04-24 | FAB0032
TNK19016 | 2019-07-25 | NYMIC Engineering Limited | NYMIC Engineering Ltd FAB0023 | AS 1692-2006, Category 4 | 50,000 litre single skin above ground horizontal tank Safe Fill Level: 47,196 Litres | Flammable liquids having hazard classifications of 3.1A, 3.1B, 3.1C or 3.1D | NYMIC Engineering Limited | This approval becomes invalid following any change to the BVT Consulting design, service conditions and/or referenced drawings. | 2029-06-25 | FAB0023
TNK19017 | 2019-08-02 | IT Power Services Limited 13A Piermark Drive Albany, North Shore City, Auckland | Mainline Sheetmetals Limited 209 Ellis Street Frankton Hamilton FAB0018 (until 18/10/2019) | UL142, AS 1692 & Generator Set Safe Work Instrument 2017 | 2,100 litre generator base tank Safe Fill Level: 1,996 Litres | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | IT Power Services Limited 13A Piermark Drive Albany, North Shore City, Auckland | This approval becomes invalid following any change to the referenced designs and drawings. | 2029-08-02 | FAB0018 (until 18/10/2019)
TNK19018 | 2019-11-19 | Martin Engineering (PN) Ltd, Palmerston North | Martin Engineering (PN) Ltd, Palmerston North FAB0045 | AS 1692 - 2006, Category 4 | 22,000 litre single skin horizontal above ground tank Safe fill level: 1769 mm or 21,000 L | Name: Toluene Class(es): 3.1B, 6.1D, 6.8B, 6.9B | Martin Engineering (PN) Ltd, Palmerston North | This approval becomes invalid following any change to the referenced contents, design, duty, service conditions or referenced drawings | 2029-11-19 | FAB0045
TNK19019 | 2019-08-26 | RES (2013) Ltd 40 Ellis Street, Frankton, Hamilton |  | AS 1692 - 2006, Category 3 | Tank Type: Above Ground Stationary Tank Description: Welltest 2000L Double Skinned Tank Name of Designer: Rob Kelly Capacity: 2,000 Litres Safe Fill Level: 1,900 Litres Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | RES (2013) Ltd 40 Ellis Street, Frankton, Hamilton | This approval becomes invalid following any change to the referenced designs and drawings. Approved to supply a burner or engine. Individual tank serial numbers to be allocated. Individual tank QA records to be retained. | 2029-08-26 | FAB0043
TNK19020 | 2019-10-14 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton FAB0071 | AS 1692 - 2006, Category 5 | Tank Type: Above Ground Stationary Tank Name of Designer: A.Pakroo Capacity: 34,867 Litres Safe Fill Level: 33,267 Litres Compartments: 1 | Nitric acid 0.5-10% CIP solution having a hazard classification of 6.1E, 6.9B, 8.1A, 8.2C, 8.3A. | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton | This approval becomes invalid following any change to the referenced designs and drawings. | 2029-10-14 | FAB0071
TNK19021 | 2019-10-14 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton FAB0071 | AS 1692 - 2006, Category 5 | Tank Type: Above Ground Stationary Tank Name of Designer: A.Pakroo Capacity: 34,867 Litres Safe Fill Level: 33,267 Litres Compartments: 1 | Sodium hydroxide, 2-5% acqueous solution, having hazard classification of 6.1E, 8.1A, 8.2C, 8.3A. | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton | This approval becomes invalid following any change to the referenced designs and drawings. | 2029-10-14 | FAB0071
TNK19022 | 2019-10-14 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton FAB0071 | AS 1692 - 2006, Category 5 | Tank Type: Above Ground Stationary Tank Name of Designer: A.Pakroo Capacity: 22,929 Litres Safe Fill Level: 22,062 Litres Compartments: 1 | Sodium hydroxide, 2-5% acqueous solution, having a Hazard Classification of 6.1E, 8.1A, 8.2C, 8.3A | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton | This approval becomes invalid following any change to the referenced designs and drawings. | 2029-10-14 | FAB0071
TNK19023 | 2019-04-09 | Fuelchief Limited 5 Tanya Street PO Box 41 029 Bromley, Christchurch | Quindao Jinhuanghai Container Co Ltd FAB0069 | AS 1692-2006 | Tank Type: Above Ground Stationary Tank Description: FT68R Containerised Rectangular Integral Secondary Contained Safe Fill Capacity: 58,100 litres | Substance Name: Diesel UN1202/3082 and Waste Oil High Flash UN3082 Class(es):3.1D | Fuelchief Limited 5 Tanya Street PO Box 41 029 Bromley, Christchurch |  | 2024-04-09 | FAB0069
TNK19024 | 2020-01-30 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton FAB0071 | API Standard 650 | Description: Whau Valley Caustic Tank 01 & 02 Tank Type: Above Ground Stationary Tank Name of Designer: A.Pakroo Capacity: 10,100 Litres Maximum Safe Fill Volume: 9,835 Litres. Tank Serial Number: 23565-TANK-01-A01 Manufacture Year: 2019 Compartments: 1 | Sodium hydroxide > 5% acqueous solution, having a hazard classification of 6.1D, 6.1E, 8.1A, 8.2B, 8.3A, 9.1D | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton, Hamilton | Tank trace heated, insulated and clad. Approved for construction drawings and internal QA procedures. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2030-01-30 | FAB0071
TNK19025 | 2017-07-13 | Oilcon Ltd PO Box 11032 Whangarei Northland | Oilcon Ltd 14 Hewlett Street Whangarei FAB0081 | AS 1692 - 2006, Category 2 | 500 L cylindrical above ground tank (overhead or onground) | 3.1A, 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Oilcon Ltd PO Box 11032 Whangarei Northland | Design and fabricator registration are for tanks supplying a burner or a class 3.1 burning installation only. No registration requirements for standalone above ground tanks. The design is approved as per test certificates ST12102 and ST12103. | 2022-07-13 | FAB0081
TNK19026 | 2017-07-13 | Oilcon Ltd PO Box 11032 Whangarei Northland | Oilcon Ltd 14 Hewlett Street Whangarei FAB0081 | AS 1692 - 2006, Category 2 | 700 L cylindrical above ground tank (overhead or onground) | 3.1A, 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Oilcon Ltd PO Box 11032 Whangarei Northland | Design and fabricator registration are for tanks supplying a burner or a class 3.1 burning installation only. No registration requirements for standalone above ground tanks. The design is approved as per test certificates ST12102 and ST12103. | 2022-07-13 | FAB0081
TNK19027 | 2017-07-13 | Oilcon Ltd PO Box 11032 Whangarei Northland | Oilcon Ltd 14 Hewlett Street Whangarei FAB0081 | AS 1692 - 2006, Category 2 | 1000 L cylindrical above ground tank (overhead or onground) | 3.1A, 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Oilcon Ltd PO Box 11032 Whangarei Northland | Design and fabricator registration are for tanks supplying a burner or a class 3.1 burning installation only. No registration requirements for standalone above ground tanks. The design is approved as per test certificates ST12102 and ST12103. | 2022-07-13 | FAB0081
TNK19028 | 2017-07-13 | Oilcon Ltd PO Box 11032 Whangarei Northland | Oilcon Ltd 14 Hewlett Street Whangarei FAB0081 | AS 1692 - 2006, Category 2 | 1300 L cylindrical above ground tank (overhead or onground) | 3.1A, 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Oilcon Ltd PO Box 11032 Whangarei Northland | Design and fabricator registration are for tanks supplying a burner or a class 3.1 burning installation only. No registration requirements for standalone above ground tanks. The design is approved as per test certificates ST12102 and ST12103. | 2022-07-13 | FAB0081
FAB0081 | 2017-07-13 |  | Oilcon Ltd 14 Hewlett Street Whangarei | AS 1692 – 2006, Category 2 | 500 L, 700 L, 1000 L, 1300 L cylindrical above ground tanks (overhead or onground) | 3.1A, 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Oilcon Ltd PO Box 11032 Whangarei Northland | Design and fabricator registration are for tanks supplying a burner or a class 3.1 burning installation only. No registration requirements for standalone above ground tanks. The design is approved as per test certificate SCF12104. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2020-07-12 | Fabricator of: TNK19025, TNK19026, TNK19027, TNK19028
TNK19029 | 2020-02-03 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 110,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 3m. Overall length: 14.85m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 110,000 litres. Tank total volume: 112,200 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-03 | FAB0036
TNK19030 | 2020-02-03 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 105,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 3m. Overall length: 14.85m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 105,000 litres. Tank total volume: 106,190 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-03 | FAB0036
TNK19031 | 2020-02-03 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 100,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 3m. Overall length: 14.85m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 100,000 litres. Tank total volume: 101,240 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-03 | FAB0036
TNK19032 | 2020-02-03 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 95,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 3m. Overall length: 14.15m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 95,000 litres. Tank total volume: 96,290 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-03 | FAB0036
TNK19033 | 2020-02-03 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 90,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 3m. Overall length: 13.5m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 90,000 litres. Tank total volume: 91,700 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-03 | FAB0036
TNK19034 | 2020-02-03 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 85,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 3m. Overall length: 12.85m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 85,000 litres. Tank total volume: 87,100 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-03 | FAB0036
TNK19035 | 2020-02-03 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 80,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 3m. Overall length: 11.95m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 80,000 litres. Tank total volume: 80,740 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-03 | FAB0036
TNK19036 | 2020-02-03 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 75,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 3m. Overall length: 11.3m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 65,000 litres. Tank total volume: 76,150 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-03 | FAB0036
TNK19037 | 2020-02-03 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 70,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 3m. Overall length: 10.6m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 70,000 litres. Tank total volume: 71,200 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-03 | FAB0036
TNK19038 | 2020-02-03 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 65,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 3m. Overall length: 9.95m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 65,000 litres. Tank total volume: 66,600 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-03 | FAB0036
TNK19039 | 2020-02-03 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 60,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 3m. Overall length: 9.05m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 60,000 litres. Tank total volume: 60,240 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-03 | FAB0036
TNK19040 | 2020-02-03 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 55,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 3m. Overall length: 8.6m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 55,000 litres. Tank total volume: 55,650 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-03 | FAB0036
TNK19041 | 2020-02-03 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 50,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 3m. Overall length: 7.7m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 50,000 litres. Tank total volume: 50,700 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-03 | FAB0036
TNK19042 | 2020-02-03 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 45,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 3m. Overall length: 7.05m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 45,000 litres. Tank total volume: 46,100 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-03 | FAB0036
TNK19043 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 70,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2.5m. Overall length: 14.8m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 70,000 litres. Tank total volume: 70,490 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19044 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 65,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2.5m. Overall length: 13.8m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 65,000 litres. Tank total volume: 65,580 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19045 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 60,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2.5m. Overall length: 12.8m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 60,000 litres. Tank total volume: 60,680 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19046 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 55,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2.5m. Overall length: 11.8m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 55,000 litres. Tank total volume: 55,760 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19047 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 50,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2.5m. Overall length: 10.8m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 50,000 litres. Tank total volume: 50,850 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19048 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 45,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2.5m. Overall length: 9.75m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 45,000 litres. Tank total volume: 45,700 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19049 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 40,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2.5m. Overall length: 8.75m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 40,000 litres. Tank total volume: 40,800 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19050 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 35,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2.5m. Overall length: 7.75m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 35,000 litres. Tank total volume: 35,880 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19051 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 30,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2.5m. Overall length: 6.75m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 30,000 litres. Tank total volume: 35,980 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19052 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 25,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2.5m. Overall length: 5.7m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 25,000 litres. Tank total volume: 25,821 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19053 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 20,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2.5m. Overall length: 4.7m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 20,000 litres. Tank total volume: 20,910 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19054 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 15,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2.5m. Overall length: 3.7m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 15,000 litres. Tank total volume: 16,000 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19055 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 10,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2.5m. Overall length: 2.775m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 10,000 litres. Tank total volume: 11,460 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19056 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 30,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2m. Overall length: 9.95m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 30,000 litres. Tank total volume: 30,980 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19057 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 25,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2m. Overall length: 8.45m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 25,000 litres. Tank total volume: 26,680 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19058 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 20,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2.0m. Overall length: 6.95m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 20,000 litres. Tank total volume: 20,910 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19059 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 15,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2m. Overall length: 5.25m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 15,000 litres. Tank total volume: 16,000 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19060 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 10,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 2m. Overall length: 3.95m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 10,000 litres. Tank total volume: 11,300 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19061 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 5,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 1.2m. Overall length: 4.8m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 5,000 litres. Tank total volume: 5,190 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19062 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 4,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 1.2m. Overall length: 3.9m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 4,000 litres. Tank total volume: 4,170 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19063 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 3,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 1.2m. Overall length: 3m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 3,000 litres. Tank total volume: 3,150 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19064 | 2020-02-03 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 2,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 1.2m. Overall length: 2.1m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 2,000 litres. Tank total volume: 2,140 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
TNK19065 | 2020-02-04 | Clark Engineers | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316:2018 | Description: 1,000 L Below Ground Stationary Tank Design specification: UL1316:2018. Tank diameter: 1.2m. Overall length: 1.3m. Design pressure: Atmospheric. Test pressure: 35kPa. Tank safe fill volume: 1,000 litres. Tank total volume: 1,230 litres. Max sg: 0.832. | Petrol / Diesel 3.1A, 3.1D UN No. 1203 / 1202. | Maskell Productions Limited 24 Bowen Road, Mt Wellington, Auckland FAB0036 | UL1316 design performance tests accepted on Clark Engineers Inc, Texas certifying letter dated 12/2/2019. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. Compartmentalised versions of this design compliance certificate are authorised when fitted with: (a) Double wall bulkheads to Maskell drawing 1115/P2 Rev A. (b) Identical risers and manways are fitted to each compartment. (c) Envirotank Tested UL1316 labels specifying compartment volume / serial number are glassed in each manway along with the Worksafe NZ allocated TNK register number. | 2025-02-04 | FAB0036
FAB0083 | 2019-12-19 |  | Carlyon Civil Construction Ltd PO Box 10092 Te Rapa, Hamilton, 3241 12 - 15 Manchester Place Te Rapa Hamilton 3200 | Prior to 3/04/2023: AS 1692 – 2006, Category 4 & SWI 2017 From 3/04/2023: AS 1692-2006, Reduced Secondary Containment Safe Work Instrument 2017, UL142, Above Ground Stationary Tanks Connected to a Generator Set – Safe Work Instrument 2017, UL2085 (2 hour ﬁre rated) and API 650 From 29/01/2024 AS 1692-2006, Reduced Secondary Containment Safe Work Instrument 2017, UL142, Above Ground Stationary Tanks Connected to a Generator Set – Safe Work Instrument 2017, UL2085 (2 hour fire rated) and API 650. Includes the fabrication of UL2085 tanks for 2 hour fire rating, and SwRI 95-03 for 4 hour fire rating. | Tanks up to 110,000 L Prior to 3/04/2023 refer to individual TNK numbers: TNK0501, TNK0826, TNK0842, TNK843, TNK0844, TNK0845, TNK0883, TNK1001, TNK1017, TNK11006, TNK12023, TNK13044, TNK15003, TNK16019, TNK17001, TNK17002, TNK17009, TNK19066, TNK20006, TNK20008, TNK20024, TNK20025, TNK20113 From 3/04/2023 refer to individual TNK numbers: TNK0826, TNK0842, TNK843, TNK0844, TNK0845, TNK0883, TNK1001, TNK1017, TNK11006, TNK12023, TNK13044, TNK15003, TNK16019, TNK17001, TNK17002, TNK17009, TNK19066, TNK20006, TNK20008, TNK20024, TNK20025, TNK20113, TNK20179, TNK20180, TNK20181, TNK20244, TNK20265, TNK20295, TNK20328 From 29/01/2024 refer to individual TNK numbers: TNK0826, TNK0842, TNK0843, TNK0844, TNK0845, TNK0883, TNK1001, TNK1017, TNK11006, TNK12023, TNK13044, TNK15003, TNK16019, TNK17001, TNK17002, TNK17009, TNK19066, TNK20006, TNK20008, TNK20024, TNK20025, TNK20113, TNK20179, TNK20180, TNK20181, TNK20230, TNK20235, TNK20244, TNK20265, TNK20273, TNK20295, TNK20328 | 3.1A, 3.1B, 3.1C, 3.1D, 6.1E, 6.3B, 6.4A, 6.7B, 9.1B, 9.1C, 9.1D | Carlyon Civil Construction Ltd PO Box 10092 Te Rapa, Hamilton, 3241 12 - 15 Manchester Place Te Rapa Hamilton 3200 | Fabrication, inspection and testing in accordance with the specified tank design code, approved tank design drawings and approved for construction drawings. Allocation of unique individual tank serial number to be stamped on each individual tank and recorded. Retention of individual tank fabrication, testing records and QA records for each tank. The design is approved as per compliance certificate CC02081, CER-0097-101920 and CER-0097-118406. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the compliance certifier who issued the certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2027-01-29 | Fabricator of: TNK0826, TNK0842, TNK0843, TNK0844, TNK0845, TNK0883, TNK1001, TNK1017, TNK11006, TNK12023, TNK13044, TNK15003, TNK16019, TNK17001, TNK17002, TNK17009, TNK19066, TNK20006, TNK20008, TNK20024, TNK20025, TNK20113, TNK20179, TNK20180, TNK20181, TNK20230, TNK20235, TNK20244, TNK20265, TNK20273, TNK20295, TNK20328
TNK19066 | 2019-12-17 | Carlyon Civil Construction Ltd | Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692 - 2006, Category 4 | 15,219 L horizontal cylindrical above ground tank Safe Fill Level: 14,458 L | Substance Name: Ethanol Class(es): 3.1B, 6.4A, 9.1D | Carlyon Civil Construction Ltd | This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2029-12-17 | FAB0083
TNK20000 | 2020-01-16 | Hendl and Murray Engineering Limited 103 Tawa Street, Melville, Hamilton, 3206 | Hendl and Murray Engineering Limited 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | API 650, Twelth Edition, March 2013, Appendix J & S. | 32,460 L vertical, cylindrical, above ground tank Safe Fill Level: 30,000 L Tank Serial Number: 19928-01 Tank ID: T402 Manufacture Year: 2019 Name of Designer: AECOM | Substance Name: Arsenic Acid Class(es): 6.1B, 6.7A, 6.8A, 6.9A | Hendl and Murray Engineering Limited 103 Tawa Street, Melville, Hamilton, 3206 | This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2030-01-16 | FAB0033
TNK20001 | 2020-01-16 | Hendl and Murray Engineering Limited 103 Tawa Street, Melville, Hamilton, 3206 | Hendl and Murray Engineering Limited 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | AS 1692-2006, Category 5 | 21,050 L vertical, cylindrical, above ground tank Safe Fill Level: 20,000 L Tank Serial Number: 18707-03 Equipment Number: Q1TK0641 Manufacture Year: 2017 | Substance Name: CIP caustic solution maximum 5% concentration Class(es): 8.1A, 8.2C, 8.3A | Hendl and Murray Engineering Limited 103 Tawa Street, Melville, Hamilton, 3206 | This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2030-01-16 | FAB0033
TNK20002 | 2020-01-28 | R.Adams | Martin Engineering (Palmerston North) Ltd. FAB0045 | AS 1692 - 2006, Category 4 | Description: 3,000 Litre Single Skin Tank Tank Type: Above Ground Stationary Tank Capacity: 3,365 Litres Maximum Safe Fill Volume: 3,160 Litres. Compartments: 1 | 3.1A, 3.1B, 3.1C, 3.1D | Martin Engineering 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 | Approved to supply an engine or burner. Tank specific vent design required. Randall & Associates Wind & Seismic Design Compliance Certificate MS 58298. Allocate unique serial number for each tank and retain fabrication records. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2030-01-28 | FAB0045
TNK20003 | 2020-02-20 | Deon den Otter | Hendl and Murray Engineering Limited 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | AS 1692-2006 Category 3 | 2.6 cubic meter Dipping Tank Capacity: 4,152 Litres Maximum Safe Fill Level: 2,640 Litres. Compartments: 1 | Substances Name: Sodium Hydroxide or Phosphoric Acid Class(es): 6.1D, 6.1E, 8.1A, 8.2B, 8.3A, 9.1D or 6.1E, 6.1D, 8.1A, 8.2C, 8.3A, 9.1D, 9.3C | Hendl and Murray Engineering Limited 103 Tawa Street, Melville, Hamilton, 3206 | This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. Allocate unique serial numbers for each vat and retain individual fabrication & testing records. | 2035-02-20 | FAB0033
TNK20004 | 2020-03-04 | Zhanjiagang Superise Heavy Industry Maxhinery Co. Ltd |  | AS 1692-2006 Category 3 and SWI Reduced Secondary Containment for Tanks | Description: FP30 Containerised Rectangular Integral Secondary Contained Tank Type: Above Ground Stationary Tank Capacity: 30,500L Maximum Safe Fill Level: 27,450 L Compartments: 1 | Diesel having a hazard classification of 3.1D, 6.1E (All), 6.1E (O), 6.3B, 6.7B, 9.1B (All), 9.1B (F), 9.1B (C), 9.1B | Fuelchief Limited 5 Tanya Street PO Box 41 029 Bromley, Christchurch | Approved for construction drawings and internal QA procedures. Secondary containment is >100% and <110% This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2025-03-03
TNK20005 | 2020-03-19 | Martin Engineering (PN) Ltd 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 | Martin Engineering (PN) Ltd 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 FAB0045 | AS 1692-2006, Category 4, UL2085 and Reduced Secondary Containment Safe Work Instrument 2017 (Impact Protected) | 5,000 to 15,000 L Above Ground Double Skinned Fuel Tank Compartments: 1 | Flammable liquids having hazard classifications 3.1C or 3.1D only as specified per individual tank. | Martin Engineering Limited 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 | Double skin stationary tank - impact protected in accordance with CL20 (vehicle impact test) and CL21 (projectile test). Tank specific vent design required. Randall & Associates Wind & Seismic Design Compliance Certificate MS 37471. RSM Test Certificates 2011019 & 2015112. Allocation of unique serial number for each tank and retention of fabrication & testing records. Installation location in accordance with RSC SWI 2017. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2030-03-19 | FAB0045
TNK20006 | 2020-04-21 | Carlyon Civil Construction Ltd | Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692 – 2006, Category 4 and Reduced Secondary Containment Safe Work Instrument 2017 (Impact Protected) | 39,352 L double skin – impact protected, cylindrical, horizontal, above ground tank design Safe Fill Capacity: 37,385 L | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Carlyon Civil Construction Ltd | Tested in accordance with Clauses 20 (vehicle impact test) & 21 (projectile test) of UL2085. Cheal Consultants Limited Design Statement No. 19103. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2030-04-21 | FAB0083
TNK20007 | 2020-05-08 | Fuelcon Limited 84B Armstrong Street P O Box 9031 Palmerston North | Prior to 17/10/2023: Fuelcon Limited 84B Armstrong Street P O Box 9031 Palmerston North FAB0047 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692-2006, Category 3 | 901 L Double Skin rectangular above ground tank Safe Fill Level: 873 L | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuelcon Limited 84B Armstrong Street P O Box 9031 Palmerston North | Approved to supply an engine or burner. Allocate unique serial number for each tank and retain fabrication records. This approval becomes invalid following any change to the referenced contents, design, duty or drawings. | 2030-05-08 | Prior to 17/10/2023: FAB0047 As of 17/10/2023: FAB0096
TNK20008 | 2020-05-18 | Carlyon Civil Construction Ltd | Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692 – 2006, Category 4 | 970 L Double Skinned, Single Compartment diesel tank on feet with lockable spill box, above ground stationary tank Safe Fill Level: 920 L | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Carlyon Civil Construction Ltd | Approved to supply an engine or burner. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2030-05-18 | FAB0083
TNK20009 | 2020-05-26 | F.SILVA |  | API 650, 12th Ed. (March 2013), Addendum 2 (January 2016) | Description: 60m3 Bitumen Emulsion tanks Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: F.SILVA Capacity: 70,000 Litres Compartments: 1 Maximum Safe Fill Level: 9 m | Name: Bitumen emulsion (PAVEmuls F70 FC) Class(es): 6.7B, 6.8B, 6.9B | Fulton Hogan Limited 154 Hewletts Road, Mount Maunganui, 3116 | Allocate unique serial numbers for each tank and retain fabrication records. Re-certification required following any change to the design parameters or service conditions or referenced drawings. | 2030-05-26
TNK20010 | 2020-08-06 | Contract Mechanical Services Ltd. | FAB0076 | API Standard 650 Annex S and Annex J. | Description: 60,000 L, 316L grade stainless steel 98% sulphuric acid tank Tank serial number: 5131TK01 Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Contract Mechanical Services Ltd. Capacity: 60,000 L Compartments: 1 Design temperature: 40 deg C. OD 3.8m x 6.0m high x bottom strakes 6 mm, top strakes 5mm. 1.3 degree fall of floor. Joint efficience: 0.7 (no radiography). Safe fill height: 5.32m. High level alarm: 5.48m. High high level alarm: 5.54m. Overflow: 5.8m. Roof pitch: 10 degrees. Top curb angle: 75 x 6 EA. | Name: 98% sulphuric acid Class(es): 8.1A | Contract Mechanical Services Limited 11 Harvard Way, Mt Maunganui | Design life 50 years. Location Fonterra Clandeboye cnr Rolleston and Canal Rds, Temuka. Wind and seismic design to NZS1170-2 and 1170.5, NZSEE:2009 - Robin King Engineers Ltd report 11 March 2020. Seismic zone: 0.15. Maximum specific gravity: 1.84. Sp=1.0 Site subsoil class D. Tank design pressure: 1.0 kPa. Design vacuum: -0.25 KPa. Venting to API2000 / AS1940. Maximum fill rate 500 litres / minute. Maximum pump out rate 500 litres / minute. 102.26 mm ID gooseneck natural vent Anchoring: 8 anchors required M30 316 ss threaded rod on 3.924 m PCD. 250 mm embedment, Epcon C6. Minimum concrete thickness at anchors: 320 mm. Minimum edge distance: 380 mm. Concrete strength: 32 MPa. | 2025-08-06
TNK20011 | 2020-08-06 | Robin King Engineers Ltd. |  | API Standard 650 Annex S and Annex J. | 10,000 L, 304L grade stainless steel Tank serial number: 5132TK01. Design temperature: 10 to 40 deg C. Outer Diameter: 2.23m x 3.0m high x 5mm strakes. Joint efficience: 0.7 (no radiography). Safe fill height: 2.59 m. High level alarm: 2.68 m. High high level alarm: 2.77 m. Overflow: 2.85 m. Roof pitch: 10 degrees. Top curb channel: 75 x 6 EA. Design life: 50 years. Tank design pressure 1.0 kPa. Design vacuum -0.25 KPa. Venting to API2000 / AS1940. Maximum fill rate: 500 L / minute. Maximum pump out rate: 500 L / minute. 108.2 mm ID gooseneck natural vent fitted with 140 mm breather tube with 12 x slots 16mm x 94mm equispaced and 2 mm bottom drip collection plate. 15NB condensate drip return pipe. | Name: Sodium hydroxide 50% w/w UN1824 Class(es): 8.1A | Contract Mechanical Services Limited 11 Harvard Way, Mt Maunganui | Location Fonterra Clandeboye cnr Rolleston and Canal Rds, Temuka. Wind and seismic design to NZS1170-2 and 1170.5, NZSEE:2009 - Robin King Engineers Ltd report 13 March 2020. Seismic zone 0.15. Maximum specific gravity 1.525. Sp: 1.0 Site subsoil class D. Anchoring: 4 anchors required M24 on 2.34 m PCD. 160 mm embedment, Epcon C6. Minimum concrete thickness at anchors 220 mm, minimum edge distance 150 mm. Concrete strength 32 MPa. | 2025-08-06
TNK20012 | 2020-11-05 | CMK Engineering Pty Ltd |  | API 650 12th edition 2013 inc addendum 1 & 2. | Description: 10,450 L cylindrical tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: CMK Engineering Pty Ltd. Capacity: 10,450 litres. Compartments: 1 Tank serial number: T169SP1776 | Name: Tanalith C oxide (copper chrome arsenic wood preservative) HSR000835. UN No. 292 Class(es): 6.1B, 8.1A, 8.2B, 8.3A | CT Engineering Services Limited 10a Gateway Park Drive, Poneko | Maximum design: SG 2.0 Seismic design to: NZS 1170-5 CMK Engineering Pty Ltd design report C20026-T169SP1776. No wind loading assessment to NZS 1170-2 as tank stored indoors. Z factor: 0.27 Nelson Sub soil: class D Near fault factor: 1.0 Site location 67 Quarantine Road, Nelson Joint efficiency: 0.7 (no radiography) Shell: 6 mm m/s Floor: 8 mm m/s Roof: 6 mm m/s 10 degree pitch self supporting Venting to: API 2000, 1 number 65 mm gooseneck vent. Maximum pump in rate: 1,000 litres per minute Maximum pump out rate: 1,000 litres per minute | 2025-11-05
TNK20013 | 2021-02-19 | CT Engineering Services Limited |  | API Standard 650 | Description: Tanalith C oxide storage tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: CT Engineering Services Ltd. Capacity: 30,000 litres. Compartments: 1 | Name: Tanalith C Oxide Class(es): 6.1B, 6.5A, 6.5B, 6.6A, 8.1A, 8.2B, 8.3A | CT Engineering Services Limited 10a Gateway Park Drive, Pokeno | Tank serial number T174AR1797. Product stored Lonza Tanalith C Oxide CCA wood preservative. Hazchem code 2X. UN Number 2922. Max specific gravity 2.0 Seismic calculations to NZS1170-5. CMK Engineering Pty Ltd report C20060-T174AR1797 Rev 1. Z factor 0.13 Subsoil class D. Near fault factor 1.0 Site location: James Fletcher Drive, Otahuhu, Auckland. No wind assessment to NZS1170-2 since tank is situated inside the building. Design specification API650 12th edition :2013 inc Addendum 1 & 2. Joint efficiency 0.7 (no radiography). Corrosion allowance 2 mm. Seismic anchoring required, five number equi spaced hold down bolts M24 diameter Gr 8.8 Hydrostatic pressure test to 8.8m head witnessed 13 January 2021. 4 psi pressure test of all nozzle compensating plates witnessed 13 January 2021. Safe fill height 4.25m. Slosh wave height 0.212m. High level alarm 4.25m. High high level alarm 4.3m Venting to API2000. 80NB gooseneck natural vent. Maximum pump in rate 1000 litres/min. Maximum pump out rate 1000 litres/min | 2026-02-19
TNK20014 | 2021-02-03 | Clark Engineers Inc, Texas | Maskell Productions Limited 24 Bowden Road, Auckland FAB0084 | UL1316:2018 | Description: 5,000 litre sludge pigging waste UGST Design Specification: UL1316:2018 Tank Type: Below Ground Stationary Tank Name of Designer: Clark Engineers Inc, Texas Capacity: 5,000 L Compartments: 1 | Name: Pigging sludge waste Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Maskell Productions Limited 24 Bowden Road, Auckland, 1060 | UL1316 design performance tests accepted on Clark Engineers Inc certifying letter dated 12/2/2019. Max S.G.: 1.4 pigging sludge waste. Design specification: UL1316:2018 Design pressure: Atmospheric Test pressure: 50 kPa Tank inner diameter: 1.2 m. Overall length: 4.8 m. Tank safe fill volume: 5,000 litres. Tank total volume: 5,190 litres. Tanks to be installed strictly in accordance with Envirotank installation instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks only to be installed by Maskell Productions Ltd trained and authorised installers. TNK20014 registration to be glassed in the manway riser. The upstream pressure is to be limited to 5barg before drain use. The vent line is to be sized appropriately to ensure a back pressure on the sump tank is kept below 50 kPa. | 2026-02-03 | FAB0084
TNK20015 | 2020-06-08 | Martin Engineering (PN) Ltd 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 | Martin Engineering (PN) Ltd 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 FAB0045 | AS 1692-2006, Category 5 | Capacity: 10,857 L & 21,715 L Vertical single skin cylindrical above ground tank Safe Fill Level: 10,000 L or 2,210 mm & 20,000 L or 4,410 mm | CCA & MCA timber treatment chemicals as concentrates or dilutions having hazard classifications 5, 6, 8 & 9. | Martin Engineering (PN) Ltd | Tank specific vent design required. Randall & Associates Wind & Seismic design Compliance Certificate MS 59595. Allocate unique serial number for each tank and retain fabrication records. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2030-06-08 | FAB0045
TNK20016 | 2020-06-08 | Martin Engineering (PN) Ltd 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 | Martin Engineering (PN) Ltd 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 FAB0045 | AS 1692-2006, Category 5 | Capacity: 77,753 L Vertical single skin cylindrical above ground tank design Safe Fill Level: 75,343 L or 5,820 mm | CCA & MCA timber treatment chemicals as concentrates or dilutions having hazard classifications 5, 6, 8 & 9. | Martin Engineering (PN) Ltd | Tank specific vent design required. Randall & Associates Wind & Seismic design Compliance Certificate MS 59578. Allocate unique serial number for each tank and retain fabrication records. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2030-06-08 | FAB0045
TNK20017 | 2020-04-03 | Mohammed Aiyaaz |  | API Standard 650 | Description: Nitric Acid Storage Tank T401 Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Capacity: 20,000 L | Name: nitric acid 45% Class(es): 6.1D, 8.1A, 8.2B, 8.3A at 80 degrees Celcius | Kopper Performance Chemicals New Zealand 14 Mayo Road Wiri Auckland |  | N/A
TNK20018 | 2020-04-08 | Mohammed Aiyaaz |  | API Standard 650 | Description: Arsenic Acid Tank T402 Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Capacity: 30 cubic meters | Name: Arsenic Acid Class(es): 6.1B, 6.3B, 6.4A, 6.7A, 6.8A, 6.9A, 9.1A, 9.3A, 9.4B at 80 degrees Celcius | Kopper Performance Chemicals New Zealand 14 Mayo Road Wiri Auckland |  | N/A
TNK20019 | 2020-07-07 | DL | Fuelchief Limited 5 Tanya Street Bromley Christchurch 8042 FAB0076 As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS1692-2006 Category 3 | 10,000 litre single skin rectangular above ground tank Capacity: 10,525 L Safe fill level: 10,209 L Compartments: 1 | Name: Used lubricants (Toxic) having a flash point greater than 93 degree Celsius Class(es): 6.7B | Fuelchief Limited 5 Tanya Street Bromley Christchurch 8042 | SK Consulting Hydro-static & Seismic Design Report 1907-0227. Allocate unique serial number for each tank and retain fabrication records. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2030-07-07 | FAB0076 As of 19/03/2023 FAB0093
TNK20020 | 2020-07-08 | Fuelchief Limited 5 Tanya Street PO Box 41 029 Bromley, Christchurch | Fuelchief Limited 5 Tanya Street Bromley, Christchurch 8062 FAB0076 As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | BS 799-5: 2010 and Above ground stationary tanks connected to a generator set Safe Work Instrument 2017 | 1,175 L double skin rectangular generator base tank. Above Ground Stationary Tank Safe Fill Level: 1,139 L | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Fuelchief Limited 5 Tanya Street PO Box 41 029 Bromley, Christchurch | Approved to supply an engine or burner. Design Compliance Statement No. 5963-0001. Fabrication compliance and testing in accordance with BS 799. Individual tank serial numbers to be allocated. Individual tank QA records to be retained. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2030-07-08 | FAB0076 As of 19/03/2023 FAB0093
TNK20021 | 2020-09-16 | Mpaul | Mercer Stainless Limited New Plymouth Branch Corbett Road Bell Block New Plymouth 4341 FAB0072 | AS 1692 - 2006, Category 5 FAB0072 | 10,700 L cylindrical vertical above ground tank Safe Fill Level: 10,000 L | Name: 10 - 65% Nitric Acid solution Class(es): 6.1D, 6.9B, 8.1A, 8.2B, 8.3A | Mercer Stainless Limited 73 Corbett Road Bell Block New Plymouth 4312 | This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. Allocation of unique serial number for each tank and retention of fabrication and testing records. | 2030-09-16 | FAB0072
TNK20022 | 2020-09-16 | Mpaul | Mercer Stainless Limited New Plymouth Branch Corbett Road Bell Block New Plymouth 4341 FAB0072 | AS 1692 - 2006, Category 5 | 10,700 L cylindrical vertical above ground tank Safe Fill Level: 10,000 L | Name: 50% Sodium hydroxide solution Class(es): 6.1D, 8.1A, 8.2B, 8.3A | Mercer Stainless Limited 73 Corbett Road Bell Block New Plymouth 4312 | This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. Allocation of unique serial number for each tank and retention of fabrication and testing records. | 2030-09-16 | FAB0072
TNK20023 | 2020-07-30 | Fuelchief Limited 5 Tanya Street PO Box 41 029 Bromley, Christchurch | Fuelchief Limited 5 Tanya Street Bromley, Christchurch 8062 FAB0076 As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS 1692-2006, Category 3 | DC150 15,000 L Double-skinned Above Ground Fuel Storage Tank Safe Fill Level: 14,329 L | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Fuelchief Limited 5 Tanya Street PO Box 41 029 Bromley, Christchurch | BVT Design Compliance Certificate No. 17020183. Motovated seismic & wind Design Statement No. 5964-01. Allocate unique serial number for each tank built and retain fabrication and testing records. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2030-07-30 | FAB0076 As of 19/03/2023 FAB0093 As of 11/04/2024 FAB0069
TNK20024 | 2020-08-17 | Carlyon Civil Construction Ltd | Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692-2006, Category 4 | 600, 850, 1100, 1300, 1580 & 1850 L Single skinned horizontal cylindrical on ground/above ground tanks Safe Fill Level: 550, 849, 1,050, 1,234, 1,527 & 1,800 L, respectively. | Diesel having hazard classifications 3.1D, 6.1E, 6.3B, 6.7B, 9.1B or used lubricating oil with flash point greater than 93 °C having hazard classifications 6.3B, 6.7B, 9.1C. | Carlyon Civil Construction Ltd | Used for domestic or commercial installations. Approved to supply an engine or burner. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. Allocation of unique serial number for each tank and retention of fabrication & testing records. | 2030-08-17 | FAB0083
TNK20025 | 2020-08-17 | Carlyon Civil Construction Ltd | Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692-2006, Category 4 | 600, 850, 1100, 1300, 1580 & 1850 L Double skinned horizontal cylindrical on ground/above-ground tanks Safe Fill Level: 490, 757, 940, 1100, 1368 & 1611 L, respectively. | Diesel having hazard classifications 3.1D, 6.1E, 6.3B, 6.7B, 9.1B or used lubricating oil with flash point greater than 93 °C having hazard classifications 6.3B, 6.7B, 9.1C. | Carlyon Civil Construction Ltd | Used for domestic or commercial installations. Approved to supply an engine or burner. Allocation of unique serial number for each tank and retention of fabrication & testing records. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2030-08-17 | FAB0083
TNK20026 | 2020-08-14 | Logitank PTY Ltd. |  | AS 1692 Reduced Secondary Containment for Certain Above Ground Stationary Tanks Safe Work Instrument 2017 | Description: LSB-80-00 Containerized Rectangular Tank with Integral Secondary Containment Tank Type: 81,772 L Above Ground Stationary Tank Maximum Safe Fill Level: 77,425 L | Name: Diesel Class(es): 3.1D, 6.1E (All), 6.1E (O), 6.3B, 6.7B, 9.1B (All), 9.1B (F), 9.1B (C), 9.1B (A) | Petrotec Services Limited 12 Venture Place, Middleton, Christchurch, 8024 PO Box 10125, Philipstown, Christchurch, 8145 | This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2025-08-13 | 22/05/2025 - Updated PCBU company address from Petrotech Pacific Limited to Petrotec Services Limited
TNK20027 | 2020-07-08 | Index Engineering Limited 1209 Hinemaru Street Rotorua |  | API Standard 650 | Description: Vertical Duplex SS Cone Roof (API 650 App X) Design specification: API Standard 650 Tank Type: Above Ground Stationary Tank Design pressure: Atmospheric Capacity: 176,000 Litres Compartments: 1 Tank Serial Number: 21401 Tank ID: 52TK003 Manufacture Year: 2020 Manufacture: Kawerau Engineering Ltd | Name: Black Liquor Class(es): 6.1D, 6.9A, 8.1A | Index Engineering Limited 1209 Hinemaru Street Rotorua | 5 yearly API External Inspections and 1st Internal Inspection at 10 years | 2040-07-08
TNK20028 | 2020-07-26 | NDA Engineering Limited 709 Te Rapa Road, Te Rapa, Hamilton, 3200 |  | AS-1692:2006 Category 5 | Description: 316 S/S Vertical Silo Conical bottom skirted Design Specification: AS-1692:2006 Tank Type: Above Ground Stationary Tank Capacity: 100,000 Litres Compartments: 1 | Name: Spent Caustic Class(es): 6.1D, 8.1A, 8.2B, 8.3A | National Dairy Association Limited Private Bag 3018 Waikato Mail Centre Hamilton 3240 | Design fatigue life 50 years based on daily cyclic filling. Wind: 46m/s AS/NZS 1170.2 - 2011 Seismic: AS/NZS 1170.5 - 2004 and NZSEE 2009 Product Design 10% NaOH SG 1.11 Certificate expiry date based on 1/2 design life for review | 2045-07-31
TNK20029 | 2020-07-26 | NDA Engineering Limited 709 Te Rapa Road, Te Rapa, Hamilton, 3200 |  | AS-1692:2006 Category 5 | Description: 316 S/S Vertical Silo Conical bottom skirted Design Specification: AS-1692:2006 Tank Type: Above Ground Stationary Tank Capacity: 100,000 Litres Compartments: 1 | Name: 10% Nitric Acid Class(es): 6.9B, 8.1A, 8.2C, 8.3A | National Dairy Association Limited Private Bag 3018 Waikato Mail Centre Hamilton 3240 | Design fatigue life 50 years based on daily cyclic filling. Wind: 46m/s AS/NZS 1170.2 - 2011 Seismic: AS/NZS 1170.5 - 2004 and NZSEE 2009 Product design SG 1.11, 10% Nitric Acid. Certificate expiry date based on 1/2 design life for review | 2045-07-31
TNK20030 | 2020-07-26 | NDA Engineering Limited 709 Te Rapa Road, Te Rapa, Hamilton, 3200 |  | AS-1692:2006 Category 5 | Description: 316 S/S Vertical Silo Conical bottom skirted Design Specification: AS-1692:2006 Tank Type: Above Ground Stationary Tank Capacity: 100,000 Litres Compartments: 1 | Name: 10% Sodium Hydroxide Class(es): 6.1D, 8.1A, 8.2B, 8.3A | National Dairy Association Limited Private Bag 3018 Waikato Mail Centre Hamilton 3240 | Design fatigue life 50 years based on daily cyclic filling. Wind 46m/s AS/NZS 1170.2 - 2011 Seismic: AS/NZS 1170.5 - 2004 and NZSEE 2009. Product Design SG 1.11. 10% Sodium Hydroxide. Certificate expiry date based on 1/2 design life for review | 2045-07-31
TNK20031 | 2020-11-17 | G Fleming | Nymic Engineering Limited 9 Kilronan Place Wigram Christchurch FAB0023 | AS-1692-2006 Category 4 | Description: 80,000 L Single Skin Cylindrical Horizontal Tank Design Specification: AS1692 - 2006, Category 4 Tank Type: Above Ground Stationary Tank Name of Designer: G Fleming Capacity: 79,962 litres Maximum Safe Fill Level: 76,059 litres (2,695mm). Compartments: 1 | Name: Flammable Liquids Class(es): 3.1A, 3.1B, 3.1C or 3.1D | Nymic Engineering Limited 9 Kilronan Place Wigram, Christchurch 8042 | Tank specific vent design required. LogiCamms Wind & Seismic Design Compliance Certificate 11-01023.00-06-RPT-0001 Rev 2. Allocation of unique serial number for each tank and retention of fabrication & testing records. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. | 2030-11-17 | FAB0023
TNK20034 | 2020-09-01 | NDA Engineering |  | AS 1692:2006 | Description: 304 S/S Vertical Conical bottom on legs Design Specification: AS 1692:2006 Tank Type: Above Ground Stationary Tank Capacity: 10,000 Litres | Name: 2.5% Caustic Soda Class(es): 8.1A, 8.2C, 8.3A | National Dairy Association Limited 709 Te Rapa Road, Te Rapa, Hamilton, 3200 | Built for Dairy Goat Co-operative. Wind design NZS 1170.2 Seismic design NZS 1170.5 Hazard Factor Z=0.16 (Hamilton), Soil = D. Design Compliance Certificate expiry is design life. | 2045-09-01
TNK20035 | 2020-09-01 | NDA Engineering |  | AS 1692:2006 | Description: 304 S/S Vertical Conical bottom on legs Design Specification: AS 1692:2006 Tank Type: Above Ground Stationary Tank Capacity: 10,000 Litres | Name: 2.5% Caustic Soda Class(es): 8.1A, 8.2C, 8.3A | National Dairy Association Limited 709 Te Rapa Road, Te Rapa, Hamilton, 3200 | Built for Dairy Goat Co-operative. Wind Design NZS 1170.2 (43 m/s) Seismic Design NZS 1170.5 Hazard factor Z= 0.16 (Hamilton), Soil = D. Design Compliance Certificate expiry is Design Life. | 2045-09-01
TNK20036 | 2020-09-23 | Cam Besley | Mainline Sheetmetals Limited 209 Ellis Street, Frankton, Hamilton, 3204 FAB0018 | AS1692-2006 Category 3 | Description: 4900 L Rectangular Double Skin Tank Design Specification: AS 1692 – 2006, Category 3 Tank Type: Above Ground Stationary Tank Capacity: 4,990 Litres Safe Fill Level: 4,740 Litres Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Mainline Sheetmetals Limited 209 Ellis Street, Frankton, Hamilton, 3204 | Approved to supply a burner or engine. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. Allocation of unique serial number for each tank and retention of fabrication & testing records. | 2030-09-23 | FAB0018
TNK20037 | 2020-10-06 | ROCKHAUSS | Martin Engineering (PN) Ltd 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 FAB0045 | AS1692-2006 Category 3 | Description: Chorus 2500 L 110% Bunded Tank Design Specification: AS1692-2006 Category 3 Tank Type: Above Ground Stationary Tank Capacity: 2,640 Litres Safe Fill Volume: 2,500 litres. Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Martin Engineering (PN) Ltd 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 | Approved to supply a burner or engine. Tank specific vent design required. Randall & Associates Wind & Seismic Design Compliance Certificate MS 58292. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. Allocation of unique serial number for each tank and retain fabrication & testing records. | 2030-10-06 | FAB0045
TNK20038 | 2020-12-04 | C Hayes | FAB0050 | AS1692-2006 Category 3 | Description: 4800 L DS Tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: C Hayes Capacity: 4,950 Litres Maximum safe fill level: 4,800 Litres Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu | Approved to supply a burner or engine. LogiCamms statement of design compliance certificate No. 11-01038.01-06-RPT-001 Rev 0. This approval becomes invalid following any change to the referenced design drawings. Allocation of unique serial number for each tank and retain fabrication & testing records. | 2030-12-04 | FAB0050
TNK20039 | 2020-11-19 | Logitank PTY Ltd | As of 12/12/2023 Zhangjiagang Fuel Equipment Systems Company. Ltd Trading as FES 3 Hai Xin North Road, Nanfeng Town, Zhangjiagang City, Jiangsu Province P.R. China, 215600 FAB0052 | AS1692: 2006 | Description: LSB-80-NZ00 Containerized Rectangular Tank with Integral Secondary Containment Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Logitank PTY Ltd Capacity: 79,581 Litres Maximum Safe Fill Level: 75,581 Litres >110% tank secondary containment capacity Compartments: 1 As of 25/03/2026: Description: LTKKL-080 Containerized Rectangular Tank with Integral Secondary Containment Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: LTKKL-080-GA-00, Rev B, MDA corrected, Sheets 1 to 4, LTKKL80 Bulk Fuel Tank, Date: 13/02/2026 Name of Designer: Logitank PTY Ltd. Capacity: 79,581 Litres Maximum Safe Fill Level: 75,602 Litres >110% tank secondary containment capacity Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | PETROTEC SERVICES LIMITED 12 Venture Place, Middleton, Christchurch, 8024 | Approved For: The storage and transfer of diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. References: Design Statement: 8575-1000, Logitank Range, Design Statement, Rev01, Released, 25Feb26, Issued to Petrotec, in respect of Logitank Tank Range. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank name plate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-03-25 | FAB0052
TNK20041 | 2021-01-26 | Logitank PTY Ltd | As of 12/12/2023 Zhangjiagang Fuel Equipment Systems Company. Ltd Trading as FES 3 Hai Xin North Road, Nanfeng Town, Zhangjiagang City, Jiangsu Province P.R. China, 215600 FAB0052 | AS1692: 2006 | Description: LTKKL-012 Containerized Rectangular Tank with Integral Secondary Containment Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Logitank PTY Ltd Capacity: 11,395 Litres Maximum Safe Fill Level: 10,800 Litres >110% tank secondary containment capacity Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | PETROTEC SERVICES LIMITED 12 Venture Place, Middleton, Christchurch, 8024 | Approved For: The storage and transfer of diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. References: Design Statement: 8575-1000, Logitank Range, Design Statement, Rev01, Released, 25Feb26, Issued to Petrotec, in respect of Logitank Tank Range. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank name plate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-03-25 | FAB0052
TNK20042 | 2021-01-26 | Logitank PTY Ltd | As of 12/12/2023 Zhangjiagang Fuel Equipment Systems Company. Ltd Trading as FES 3 Hai Xin North Road, Nanfeng Town, Zhangjiagang City, Jiangsu Province P.R. China, 215600 FAB0052 | AS1692: 2006 | Description: LTKKL-020 Containerized Rectangular Tank with Integral Secondary Containment Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Logitank PTY Ltd. Capacity: 17,500 Litres Maximum Safe Fill Level: 16,625 Litres >110% tank secondary containment capacity Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | PETROTEC SERVICES LIMITED 12 Venture Place, Middleton, Christchurch, 8024 | Approved For: The storage and transfer of diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. References: Design Statement: 8575-1000, Logitank Range, Design Statement, Rev01, Released, 25Feb26, Issued to Petrotec, in respect of Logitank Tank Range. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank name plate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-03-25 | FAB0052
TNK20043 | 2020-12-18 | Logitank PTY Ltd | As of 12/12/2023 Zhangjiagang Fuel Equipment Systems Company. Ltd Trading as FES 3 Hai Xin North Road, Nanfeng Town, Zhangjiagang City, Jiangsu Province P.R. China, 215600 FAB0052 | AS1692: 2006 | Description: LTKBL-026 Containerized Rectangular Tank with Integral Secondary Containment Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Logitank PTY Ltd. Capacity: 23,847 Litres Maximum Safe Fill Level: 22,655 Litres >110% tank secondary containment capacity Split Tank: Yes Compartments: 2 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | PETROTEC SERVICES LIMITED 12 Venture Place, Middleton, Christchurch, 8024 | Before 25/03/2026: Second compartment is used to store a Low Hazard substance, which does not require a compliance certificate. This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. As of 25/03/2026:Approved For: The storage and transfer of diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Second compartment is used to store Low Hazard Substance, which does not require a compliance certificate. References: Design Statement: 8575-1000, Logitank Range, Design Statement, Rev01, Released, 25Feb26, Issued to Petrotec, in respect of Logitank Tank Range. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank name plate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2025-12-18 | FAB0052
TNK20044 | 2020-12-18 | Logitank PTY Ltd | As of 12/12/2023 Zhangjiagang Fuel Equipment Systems Company. Ltd Trading as FES 3 Hai Xin North Road, Nanfeng Town, Zhangjiagang City, Jiangsu Province P.R. China, 215600 FAB0052 | AS1692: 2006 | Description: LTKKL-030 Containerized Rectangular Tank with Integral Secondary Containment Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Logitank PTY Ltd. Capacity: 29,676 Litres Maximum Safe Fill Level: 28,150 Litres >110% tank secondary containment capacity Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | PETROTEC SERVICES LIMITED 12 Venture Place, Middleton, Christchurch, 8024 | Approved For: The storage and transfer of diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. References: Design Statement: 8575-1000, Logitank Range, Design Statement, Rev01, Released, 25Feb26, Issued to Petrotec, in respect of Logitank Tank Range. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank name plate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-03-25 | FAB0052
TNK20045 | 2020-12-18 | Logitank PTY Ltd | As of 12/12/2023 Zhangjiagang Fuel Equipment Systems Company. Ltd Trading as FES 3 Hai Xin North Road, Nanfeng Town, Zhangjiagang City, Jiangsu Province P.R. China, 215600 FAB0052 | AS1692: 2006 | Description: LTKKL-038 Containerized Rectangular Tank with Integral Secondary Containment Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Logitank PTY Ltd Capacity: 35,776 Litres Maximum Safe Fill Level: 33,987 Litres >110% tank secondary containment capacity Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | PETROTEC SERVICES LIMITED 12 Venture Place, Middleton, Christchurch, 8024 | Approved For: The storage and transfer of diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. References: Design Statement: 8575-1000, Logitank Range, Design Statement, Rev01, Released, 25Feb26, Issued to Petrotec, in respect of Logitank Tank Range. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank name plate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-03-25 | FAB0052
TNK20046 | 2020-12-18 | Logitank PTY Ltd | As of 12/12/2023 Zhangjiagang Fuel Equipment Systems Company. Ltd Trading as FES 3 Hai Xin North Road, Nanfeng Town, Zhangjiagang City, Jiangsu Province P.R. China, 215600 FAB0052 | AS1692: 2006 | Description: LTKKL-060 Containerized Rectangular Tank with Integral Secondary Containment Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Logitank PTY Ltd Capacity: 59,900 Litres Maximum Safe Fill Level: 56,900 Litres >110% tank secondary containment capacity Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | PETROTEC SERVICES LIMITED 12 Venture Place, Middleton, Christchurch, 8024 | Approved For: The storage and transfer of diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. References: Design Statement: 8575-1000, Logitank Range, Design Statement, Rev01, Released, 25Feb26, Issued to Petrotec, in respect of Logitank Tank Range. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank name plate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-03-25 | FAB0052
TNK20047 | 2020-12-18 | Logitank PTY Ltd | As of 12/12/2023 Zhangjiagang Fuel Equipment Systems Company. Ltd Trading as FES 3 Hai Xin North Road, Nanfeng Town, Zhangjiagang City, Jiangsu Province P.R. China, 215600 FAB0052 | AS1692: 2006 | Description: LTKBL-060 Containerized Rectangular Tank with Integral Secondary Containment Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Logitank PTY Ltd. Capacity: 56,858 Litres Maximum Safe Fill Level: 54,015 Litres >110% tank secondary containment capacity Split Tank: Yes Compartments: 2 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | PETROTEC SERVICES LIMITED 12 Venture Place, Middleton, Christchurch, 8024 | Approved For: The storage and transfer of diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Second compartment is used to store Low Hazard Substance, which does not require a compliance certificate. References: Design Statement: 8575-1000, Logitank Range, Design Statement, Rev01, Released, 25Feb26, Issued to Petrotec, in respect of Logitank Tank Range. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank name plate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-03-25 | FAB0052
TNK20048 | 2020-12-18 | Logitank PTY Ltd | As of 12/12/2023 Zhangjiagang Fuel Equipment Systems Company. Ltd Trading as FES 3 Hai Xin North Road, Nanfeng Town, Zhangjiagang City, Jiangsu Province P.R. China, 215600 FAB0052 | AS1692: 2006 | Description: LTKKL-075 Containerized Rectangular Tank with Integral Secondary Containment Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Logitank PTY Ltd Capacity: 72,340 Litres Maximum Safe Fill Level: 68,685 Litres >110% tank secondary containment capacity Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | PETROTEC SERVICES LIMITED 12 Venture Place, Middleton, Christchurch, 8024 | Approved For: The storage and transfer of diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. References: Design Statement: 8575-1000, Logitank Range, Design Statement, Rev01, Released, 25Feb26, Issued to Petrotec, in respect of Logitank Tank Range. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank name plate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-03-25 | FAB0052
TNK20049 | 2020-12-18 | Logitank PTY Ltd | As of 12/12/2023 Zhangjiagang Fuel Equipment Systems Company. Ltd Trading as FES 3 Hai Xin North Road, Nanfeng Town, Zhangjiagang City, Jiangsu Province P.R. China, 215600 FAB0052 | AS1692: 2006 | Description: LTKBL Containerized Rectangular Tank with Integral Secondary Containment Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Logitank PTY Ltd Capacity: 70,907 Litres Maximum Safe Fill Level: 67,362 Litres >110% tank secondary containment capacity Split Tank: Yes Compartments: 2 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | PETROTEC SERVICES LIMITED 12 Venture Place, Middleton, Christchurch, 8024 | Approved For: The storage and transfer of diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Second compartment is used to store Low Hazard Substance, which does not require a compliance certificate. References: Design Statement: 8575-1000, Logitank Range, Design Statement, Rev01, Released, 25Feb26, Issued to Petrotec, in respect of Logitank Tank Range. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank name plate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-03-25 | FAB0052
TNK20050 | 2021-05-03 | Polymaster Pty Ltd 161 Karinie Street Victoria 3585 Australia | Polymaster Pty Ltd 161 Karinie Street Victoria 3585 Australia FAB0086 | AS/NZS 4766:2006; Above Ground Rotationally-Moulded Polyethylene Stationary Tanks) Safe Work Instrument 2017 | 13,000 L self bunded polyethylene tank Design Specification: AS/NZS 4766:2006; Above Ground Rotationally-Moulded Polyethylene Stationary Tanks) Safe Work Instrument 2017 Capacity: Limited to 12,000 L Maximum specific gravity: 2 | Class(es): 6.1, 8.1 and 8.2 substances | Polymaster Pty Ltd 161 Karinie Street Victoria 3585 Australia | Code Compliance Check of 3 Bunded PE Tanks, 3 May 2021 Version 5 Agitation of contents not permitted Maximum operating temperature: 40 degrees Celsius Seismic region: 0.45 or less | 2031-05-03 | FAB0086
TNK20051 | 2021-05-14 | Polymaster Pty Ltd 161 Karinie Street Victoria 3585 Australia | Polymaster Pty Ltd 161 Karinie Street Victoria 3585 Australia FAB0086 | AS/NZS 4766:2006; Above Ground Rotationally-Moulded Polyethylene Stationary Tanks) Safe Work Instrument 2017 | Description: Self Bunded Polyethylene Tank 10,000L. Design Specification: AS/NZS 4766:2006; Above Ground Rotationally-Moulded Polyethylene Stationary Tanks) Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Polymaster Pty Ltd Capacity: Limited to 9,000 L | Class(es): 6.1A, 6.1B, 6.1C, 6.1D, 8.1A, 8.2A, 8.2B, 8.2C substances | Polymaster Pty Ltd 161 Karinie Street Victoria 3585 Australia | Design in Accordance with Code Compliance Check of 3 Bunded PE Tanks Prepared for Polymaster Pty Ltd, Matrix Applied Computing Ltd, 12 May 2021, Version 7. Agitation of contents is not permitted. Tank life limited to 10 years. Maximum operating temperature limited to 40 degrees Celsius. Tank to be installed in a seismic region of 0.45 or less. Hazardous substances class 6.1, 8.1, 8.2 with maximum specific gravity of 2 | 2031-05-14 | FAB0086
TNK20052 | 2021-05-19 | Polymaster Pty Ltd 161 Karinie Street Victoria 3585 Australia | Polymaster Pty Ltd 161 Karinie Street Victoria 3585 Australia FAB0086 | AS/NZS 4766:2006; Above Ground Rotationally-Moulded Polyethylene Stationary Tanks) Safe Work Instrument 2017 | Description: Self Bunded Polyethylene Tank 5,000L. Design Specification: AS/NZS 4766:2006; Above Ground Rotationally-Moulded Polyethylene Stationary Tanks) Safe Work Instrument 2017 Name of Designer: Polymaster Pty Ltd Capacity: 5000 L | Class(es): 6.1A, 6.1B, 6.1C, 6.1D, 8.1A, 8.2A, 8.2B, 8.2C substances | Polymaster Pty Ltd 161 Karinie Street Victoria 3585 Australia | Design in Accordance with Code Compliance Check of 3 Bunded PE Tanks Prepared for Polymaster Pty Ltd, Matrix Applied Computing Ltd, 12 May 2021, Version 7. Agitation of contents is not permitted. Tank life limited to 10 years. Maximum operating temperature limited to 40 degrees Celsius. Tank to be installed in a seismic region of 0.45 or less. Hazardous substances class 6.1, 8.1, 8.2 with maximum specific gravity of 2 | 2031-05-19 | FAB0086
TNK20055 | 2021-01-25 | Longveld Limited PO Box 5538, Frankton, Hamilton, 3242 153 Ellis Street, Frankton, Hamilton, 3204 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton FAB0071 | AS1692: 2006 | Description: 316L S/S Vertical Cone Roof Design Specification: AS 1692:2006 Tank Type: Above Ground Stationary Tank Name of Designer: Longveld Capacity: 51500 L Equipment No: WWVE5120 Supplier Serial Number: 25270-TANK 01-A01 Compartments: 1 | Name: Sulfuric Acid 98% Class(es): 6.1A, 6.7A, 6.9A, 8.1A, 8.2A, 8.3A | Tetra Pak (New Zealand) Limited 6-8, Melody Ln, Ruakura, Hamilton 3216 |  | 2070-01-25 | FAB0071
FAB0084 | 2021-02-04 |  | Maskell Productions Limited 24 Bowden Road, Auckland | UL1316:2018 | Fibre reinforced underground 5,000 litre pigging waste sludge sump tanks Reference: TNK20014 | Name: Pigging sludge waste Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Maskell Productions Limited 24 Bowden Road, Auckland | UL1316:2018 design performance tests are accepted on Clark Engineers Inc certifying letter dated 12/2/2019. Worksafe NZ registered tank design TNK20014 is to be glassed in the manway riser. New pressure test procedure 9.5.2 (amended for TNK20014 - 5,000 litre pigging waste UST sump tanks) dated 20 May 2020 covering elevated test pressure included in QA/QC documentation. Product stored pigging waste sludge max sg 1.4. Tanks to be installed strictly in compliance with Envirotank Installation Instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tanks are only to be installed by Maskell Productions Ltd trained and authorised installers. All tanks to be fitted with hydroguard monitoring systems. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. FAB0084. Maskell Productions are authorised to manufacture fibre reinforced underground 5,000 litre pigging waste sludge sump tanks to UL1316:2018 under Worksafe NZ registered design TNK20014. The upstream pressure is to be limited to 50 kPa before drain use. The vent line of the installation is to be sized appropriately to ensure a back pressure on the sump tank is kept below 50 kPa. | 2024-02-04 | Fabricator of: TNK20014
TNK20056 | 2021-03-30 | Maskell Productions Limited 24 Bowden Road, Auckland, 1060 |  | AS2634:1983 | Description: 20,000 L sodium hypochlorite storage tank. Design Specification: AS2634:1983 Tank Type: Above Ground Stationary Tank Name of Designer: Maskell Productions Site location: Watercare Services Ltd, Waikato, water treatment plant, Hayward Road, Tuakau. Capacity: 20,000 L Compartments: 1 | Name: Sodium hypochlorite Class(es): 8.2A, 8.2C, 8.3A | Maskell Productions Limited 24 Bowden Road, Auckland, 1060 | Product stored: Sodium hypochlorite solution (10-15% available chlorine). UN No.: 1791. Max s.g.: 1.23. Seismic design: NZS 1170.5 Subsoil class C. Zone factor: 0.13. Structural performance factor: 1.0. Ductility factor: 1.25. Limit state factor: 1.0. Design pressure: atmospheric. Safe fill capacity: 20,000 litres. Safe fill height: 2.83 m from base. Venting to API2000 for maximum pump in rate 39.6 cubic metres / hr. Maximum pump out rate 230.4 cubic metres / hr. Tank height: 4.08m base to dome. Material FRP Derakane 411-350 epoxy vinyl ester resin. Tank to sit on foam pad provided from Maskell Productions. Hydrostatic pressure test witnessed on Thursday 18 March 2021 | 2026-03-30
TNK20057 | 2021-04-03 | Maskell Productions Limited 24 Bowden Road, Auckland, 1060 |  | AS2634:1983 | Description: 35,000 L sodium hypochlorite storage tank Design Specification: AS2634:1983 Tank Type: Above Ground Stationary Tank Drawing Numbers: 2272.00 Rev 3. Name of Designer: Maskell Productions. Site location Watercare, Waikato water treatment plant, Trigg road, Tuakau 2694. Capacity: 35,000 L Compartments: 1 | Name: Sodium hypochlorite Class(es): 8.2A, 8.3A | Maskell Productions Limited 24 Bowden Road, Auckland, 1060 | Serial number: 2021/64. Product stored: Sodium hypochlorite. UN No.: 1791. Maximum specific gravity: 1.23 Seismic design: NZS 1170.2 and NZS 1170.5. Subsoil class C. Zone factor: 0.13. Structural performance factor: 1.0 Ductility factor: 1.25 Limit state factor: 1.0 Design life: 25 years. Design pressure: atmospheric. Safe fill capacity: 35,000 litres. Safe fill height from base: 2.785 m. Venting to API2000. Maximum pump in rate 1.875 cubic metres / hr. Maximum pump out rate 220.87 cubic metres / hr. Top vent DN100 ANSI 150 connection vented through roof. Tank height base to dome 4.473 m. Material FRP Derakane 411-350 epoxy vinylester. Hydrostatic pressure test witnessed 1 April 2021. | 2026-04-03
TNK20058 | 2021-04-03 | Maskell Productions Limited 24 Bowden Road, Auckland, 1060 |  | AS2634:1983 | Description: 35,000 L sodium hypochlorite storage tank. Design Specification: AS2634:1983 Tank Type: Above Ground Stationary Tank Drawing Numbers: 2272.01 Rev 1 Name of Designer: Maskell Productions. Site location Watercare, Waikato water treatment plant, Trigg road, Tuakau 2694. Capacity: 35,000 L. Compartments: 1 | Name: Sodium hypochlorite Class(es): 8.2A, 8.3A | Maskell Productions Limited 24 Bowden Road, Auckland, 1060 | Serial number: 2021/65. Product stored: Sodium hypochlorite. UN No.: 1791. Maximum specific gravity: 1.23 Seismic design: NZS 1170.2 and NZS 1170.5. Subsoil class C. Zone factor: 0.13. Structural performance factor: 1.0 Ductility factor: 1.25 Limit state factor: 1.0 Design life: 25 years. Design pressure: atmospheric. Safe fill capacity: 35,000 litres. Safe fill height from base: 2.785 m. Venting to API2000. Maximum pump in rate 1.875 cubic metres / hr. Maximum pump out rate 220.87 cubic metres / hr. Top vent DN100 ANSI 150 connection vented through roof. Tank height base to dome 4.473 m. Material FRP Derakane 411-350 epoxy vinylester. Hydrostatic pressure test witnessed 1 April 2021. | 2026-04-03
TNK20059 | 2021-03-17 | Robin King Engineers Ltd. |  | API Standard 650 | Description: 15,000 L 98% sulphuric acid tank 001 Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Robin King Engineers Ltd. Site location: Mercer Mushrooms, 55 Morrison Road, Pukekawa. Capacity: 15,000 L Compartments: 1 | Name: 98% sulphuric acid Class(es): 8.1A | Contract Mechanical Services Limited 11 Harvard Way, Mt Maunganui, Mt Maunganui | Tank serial number 194. 15,000 litre 316L grade stainless steel 98% sulphuric acid tank. Design temperature -10 to 40 degrees Celsius. Outer Diameter: 2.5m x 3.5m high, 5 mm strakes. Joint efficiency: 0.7 no radiography. Safe fill height: 3.07 m. High level alarm: 3.145 m. High high level alarm: 3.22 m. Overflow: 3.3 m. Roof pitch: 10 degrees. Top curb angle: 50 x 6 EA. Design life 50 years. Wind and seismic design: NZS 1170.2 and 1170.5, NZSEE : 2009. Robin King Engineers Ltd report 17 July 2020. Seismic zone: 0.18. Maximum specific gravity: 1.84. Sp = 1.0. Site subsoil class D. Tank design pressure: 1 kPa. Design vacuum: -0.25 kPa. Venting to API 2000 / AS 1940. Maximum fill rate: 500 litres/min. Maximum pump out rate: 250 litre / min. 80 NB Sch 10 gooseneck natural vent fitted with 141 OD mm breather tube with 12 slots equispaced and 2 mm bottom drip collection plate. 15 mm NB condensate drip return pipe. Anchoring 8# anchors M24 on 2.612 m PCD. 160 mm embedment, Epcon C6. Minimum concrete thickness at anchors 220 mm, minimum edge distance 294mm. Concrete strength 30 MPa. | 2026-03-17
TNK20060 | 2021-04-12 | Robin King Engineers Ltd. |  | API Standard 650 | Description: 45,000 L Flame Pro timber preservative tank. Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Robin King Engineers Ltd. Site location: Red Stag Timber, State Mill Road, Waipa, Rotorua. Capacity: 45,000 L. Compartments: 1 | Name: Frame Pro timber treatment HSR 000907 Class(es): 6.1D, 8.3A | Contract Mechanical Services Limited 11 Harvard Way, Mt Maunganui, Mt Maunganui | Tank serial number: 195. 45,000 litre 304L grade stainless steel tank to API650 Annex S and Annex J. Design temperature: -10 to 40 deg C. Outer Diameter: 3.8m x 4.515m high x 5mm strakes. Joint efficiency: 0.7 (no radiography). Safe fill height: 3.983 m. High level alarm: 4.155 m. Hi Hi level alarm 4.327 m. Roof pitch: 10 degrees. Top curb channel: 75 x 6 EA. Design life: 50 years. Wind and seismic design: NZS1170.2 and NZS1170.5, NZSEE:2009 Robin King Engineers Ltd report dated 20 Nov 2020. Seismic zone: 0.24. Maximum specific gravity: 1.232. Sp = 1.0. Site subsoil Class D. Tank design pressure: 3kPa. Design vacuum: -0.25kPa. Venting to API2000, AS1940. Maximum fill rate 500 litres / minute. Maximum pump out rate 500 litres / minute. 100 NB Sch 10 gooseneck natural vent fitted with 141 mm breather tube with 12 equi spaced slots and 2mm bottom drip collection plate with 15NB condensate drip return pipe. Anchoring: 8 M24 anchors on 3.92m PCD. 160 mm embedment Epcon C6. Minimum concrete thickness at anchors: 220 mm. Minimum edge distance: 150 mm. Concrete strength: 32 MPa. Hydro test level to top vent nozzle TN0. Hydrostatic pressure test witnessed 7 April 2021. | 2026-04-12
TNK20061 | 2021-03-08 | Ecolab New Zealand 2 Daniel Place, Te Rapa, Hamilton, 3241 |  | API Standard 650 | Description: 55,000 litre 50% caustic soda tank SS57784-T21 Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Ecolab New Zealand Site Location: 2 Daniel Place, Te Rapa, Hamilton. Capacity: 55,000 litres Compartments: 1 | Name: Sodium hydroxide 50% w/w UN1824 Class(es): 6.1D, 8.1A, 8.2B, 8.3A | Ecolab New Zealand 2 Daniel Place, Te Rapa, Hamilton, 3241 | Tank serial number SS57784-T21. 48,760 litre 316L grade stainless steel caustic soda 50% w/w storage tank to API 650 12th edition 2013. Design temperature: 48 degrees Celsius. I.D.: 3.18m x 7.5m high x 6mm strakes. Joint efficiency: 0.7. Safe fill height: 6.147m. High level alarm: 6.221m. Hi Hi level alarm: 6.515m. Overflow: 7.0m. Roof pitch: 10.7 degrees. Top curb angle: 75x75x6. Design life: 25 years. Wind and seismic design: NZS1170.2 and NZS1170.5. Seismic zone: 0.16. Maximum specific gravity: 1.52. Seismic user group: I. Site subsoil: class D. Tank design pressure: 1 kPa. Tank design vacuum: -0.5 kPa. Importance level 3. Annual probability of exceedance: 1:500. Venting: API2000/AS1940. Maximum pump in rate 500L/min. Maximum pump out rate 500L/min. 100mm Sch 80 gooseneck natural vent nozzle fitted with sch 40 elbows to form gooseneck. Tank anchoring by 8 equi spaced M30 stainless steel hold down bolts to drawing ECOLAB-ME-111-AB Rev 1. PCD 3.304 m. Minimum embedment: 400 mm. Minimum concrete edge distance: 500 mm. Concrete strength: 40 MPa. Hydrostatic pressure test carried out with product filled to Hi Hi level on Friday 19th March 2021. Tank physically dipped to top of foam layer to verify tank filled to Hi Hi level. Hi Hi level readings and lock out checked in control room. | 2026-03-08
TNK20062 | 2021-03-08 | Ecolab New Zealand 2 Daniel Place, Te Rapa, Hamilton, 3241 |  | API Standard 650 | Description: 48,760 litre 50% caustic soda tank SS57784-T22 Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Ecolab New Zealand Site Location: 2 Daniel Place, Te Rapa, Hamilton Capacity: 48,760 litres. Compartments: 1 | Name: Sodium hydroxide 50% w/w UN1824 Class(es): 6.1D, 8.1A, 8.2B, 8.3A | Ecolab New Zealand 2 Daniel Place, Te Rapa, Hamilton, 3241 | Tank serial number SS57784-T22. 48,760 litre 316L grade stainless steel caustic soda 50% w/w storage tank to API 650 12th edition 2013. Design temperature: 48 degrees Celsius. I.D.: 3.18m x 7.5m high x 6mm strakes. Safe fill height: 6.147m. High level alarm: 6.221m. Hi Hi level alarm: 6.515m. Overflow: 7m. Roof pitch: 10.7 degrees. Top curb angel: 75x75x6. Design life: 25 years. Wind and seismic design: NZS1170-2 and NZS1170-5. Seismic zone: 0.16. Maximum specific gravity: 1.53. Seismic user group I. Site subsoil Class D. Tank design pressure: 1 kPa. Tank design Vacuum: -0.5 kPa. Importance level 3. Annual probability of exceedance 1:500. Venting: API2000/AS1940. Maximum pump in rate :500L/min. Maximum pump out rate: 500L/min. 100mm Sch 80 gooseneck vent nozzle fitted with sch 40 elbows to form gooseneck. Tank anchoring by 8 equi spaced 30mm dia stainless steel hold down bolts to drawing ECOLAB-ME-121-AB Rev 1. PCD 3.304 mm. Minimum embedment: 400 mm. Minimum concrete edge distance: 500 mm. Concrete strength: 40 MPa. Hydrostatic pressure test carried out with product filled to Hi Hi level on Friday 19th March 2021. Tank physically dipped to top of foam layer to verify tank filled to Hi Hi level. Hi Hi level readings and lock out checked in control room. | 2026-03-08
TNK20063 | 2021-03-08 | Ecolab New Zealand 2 Daniel Place, Te Rapa, Hamilton, 3241 |  | API Standard 650 | Description: 48,760 litre 316L grade stainless steel CIPMAXX storage tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Ecolab New Zealand Site Location: 2 Daniel Place, Te Rapa, Hamilton. Capacity: 48,760 litres. Compartments: 1 | Name: CIPMAXX Class(es): 6.1D, 8.1A, 8.2B, 8.3A | Ecolab New Zealand 2 Daniel Place, Te Rapa, Hamilton, 3241 | Tank serial number SS57784-T23. 48,760 litre 316L grade stainless steel CIPMAXX storage tank to API650 11th edition 2012. Design temperature: 48 degrees Celsius. I.D.: 3.18m x 7.5m high x 6mm strakes. Fabricated by Page Macrae Engineering Jan 2018. Safe fill height: 6.147 m. High level alarm: 6.221 m. Hi Hi level alarm: 6.515 m. Overflow: 7.0 m. Roof pitch: 10.7 degrees. Top curb angle: 75 x 75 x 6mm. Design life: 25 years. Wind and seismic: NZS1170-2 and NZS1170-5. Seismic zone: 0.16. Maximum specific gravity: 1.525. Seismic user group I. Site subsoil class D. Tank design pressure: 1 kPa. Tank design vacuum: -0.5 kPa. Importance level 3. Annual probability of exceedance 1:500. Venting: API2000/AS1940. Maximum pump in rate: 500L/min. Maximum pump out rate: 500L/min. 100 mm sch 80 gooseneck vent nozzle fitted with sch 40 elbows to form gooseneck. Tank anchored by 8 equi spaced 30 mm diameter stainless steel hold down bolts to drawing ECOLAB-ME-131-AB Rev 1. PCD 3.304 mm. Minimum embedment: 400 mm. Minimum concrete edge distance: 500 mm. Concrete strength: 40MPa. Hydrostatic pressure test carried out with product filled to Hi Hi level on Friday 19th March 2021. Tank physically dipped to top of foam layer to verify tank filled to Hi Hi level. Hi Hi level readings and lock out checked in control room. | 2026-03-08
TNK20064 | 2021-03-08 | Ecolab New Zealand 2 Daniel Place, Te Rapa, Hamilton, 3241 |  | API Standard 650 | Description: 39,850 litre nitric acid storage tank. Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Ecolab New Zealand Site Location: 2 Daniel Place, Te Rapa, Hamilton. Capacity: 39,850 litres. Compartments: 1 | Name: Acid blend N600 Nitric acid UN2031. Class(es): 8.2B, 8.3A | Ecolab New Zealand 2 Daniel Place, Te Rapa, Hamilton, 3241 | Tank serial number SS57784-T26. 39,850 litre 316L grade stainless steel nitric acid storage tank to API650 12th edition 2013. Design temperature: 48 degrees Celsius. I.D.: 3.18m x 6.8m high x 6mm strakes. Fabricated by Page Macrae Engineering Jan 2018. Safe fill height: 5.025 m. High level alarm: 5.368 m. Hi Hi level alarm: 5.711 m. Overflow: 6.3 m. Roof pitch: 10.7 degrees. Top curb angle 75x75x6 304L stainless steel angle. Design life: 25 years. Wind and seismic: NZS 1170-2 and NZS1170-5. Seismic zone: 0.16. Maximum specific gravity: 1.42. Seismic user group I. Site sub soil class D. Tank design pressure: 1 kPa. Tank design vacuum: -0.5 kPa. Importance level 3. Annual probability of exceedence 1:500. Venting: API2000/AS1940. Maximum pump in rate: 333.33 litres/min. Maximum pump out rate: 500 litres/min. 100 mm sch 80 nozzle vent, 100 mm sch 40 elbows for goose neck. Tank anchored by 8 equi spaced 30 mm diameter threaded stainless rod to drawing ECOLAB-ME-203-AB Rev 1. PCD 3.304 mm. Minimum embedment: 400 mm. Minimum concrete edge distance: 500 mm. Concrete strength: 40 MPa. Hydrostatic pressure test carried out with product filled to Hi Hi level on Friday 19th March 2021. Tank physically dipped to verify tank filled to Hi Hi level. Hi Hi level readings and lock out checked in control room. | 2026-03-08
TNK20069 | 2022-03-03 | Robin King Engineers Ltd. |  | AS1692 - 2006 | Description: 27,000 litre Alpha Decanter 2Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Robin King Engineers Ltd. Capacity: 27,000 L. Compartments: 1 | Name: Alpha Pinene (Pinechem 500) UN2368 Class(es): 3.1C, 6.1D, 8.3A | Contract Mechanical Services Limited 11 Harvard Way, Mt Maunganui | Tank serial number PC157. 27,000 litre 316L grade s/s tank to AS1692 Category 5. Design temperature 70 deg C. 3m OD x 4.5m high x 5mm strake. Joint efficiency 0.7 (no radiography). Safe fill height 3.8m. High level alarm 4.0m Hi Hi level alarm 4.12m. Roof pitch 10 degrees. Top EA 50x50x6. Design life 50 years. Location: Lawter NZ, 211 Totara Street, Mt Maunganui. Wind and seismic design to NZS1170.2 and NZS 1170.5, NZSEE:2009 Robin King Engineers Ltd Report 19 May 2021. Seismic zone 0.2 Maximum specific gravity 1.0 design. Sp=1.0 Site subsoil Class D. Tank design pressure 1.6 kPa. Design vacuum -0.75 kPa. Venting to API2000, AS1940. Maximum fill rate 250L/min. Maximum pump out rate 333L/min. End of line PV vent with integral deflagration arrestor Protectoseal Series 830. Emergency pressure manhole cover vent Protectoseal Series 51600. Anchoring 8 M24 anchors on 3.11m PCD. 160 mm embedment Epcon C6. Minimum concrete thickness at anchors 220 mm. Minimum edge distance 150 mm. Concrete strength 32 MPa. | 2026-12-03
TNK20070 | 2021-09-14 | Robin King Engineers Ltd |  | AS1692 - 2006 | Description: 27,000 litre Beta desulph decanting tank. Design Specification: AS1692 - 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Robin King Engineers Ltd Capacity: 27kL. Compartments: 1 | Name: Beta Pinene and hydrogen peroxide 4% Class(es): 3.1C, 6.5B, 8.3A | Contract Mechanical Services Limited 11 Harvard Way, Mt Maunganui | Tank serial number 198. 27,000 litre 304L grade stainless steel tank to AS1692: 2006 Category 5. Design temperature 70 deg C. 3m OD x 4.5m high x 5mm strakes. Joint efficiency 0.7 (no radiography). Safe fill height 4.244 m. High level alarm 4m. Hi hi level alarm 4.12m. Roof pitch 10 degrees. Top curb channel 50 x 50 x 6mm. Design life 50 years. Location: Lawter NZ, 211 Totara Street, Mt Maunganui. Wind and seismic design to NZS 1170.2 and NZS 1170.5 Robin King Engineers report Revision A dated 23 August 2021. Seismic zone 0.2. Maximum specific gravity sg = 1.0 Sp = 1.0 Site sub soil class D. Tank design pressure 1.6 kPa. Design vacuum -0.7 kPa. Venting to API2000, AS1940. Maximum fill rate 250 L/min. Maximum pump out rate 333 L/min. Vent fitted with end of line PV vent with integral deflagration arrestor - Protectoseal Series 51600. Emergency pressure relief manhole cover vent Protectoseal Series 51600. Tank anchored by 8 number M24 anchors on 3.11 m PCD. Anchor bolt minimum embeddment 160 mm Epcon C6 grout. Minimum concrete thickness at anchors 220 mm. Minimum edge distance 150 mm. Concrete strength 32 MPa. Hydrotest level to explosion manway. Hydrostatic pressure test witnessed Friday 10 September 2021. | 2026-09-14
FAB0085 | 2021-04-22 |  | Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 | AS 1692-2006 | Steel tanks up to 60,000 litres Reference: TNK12005, TNK12006, TNK12007, TNK12008, TNK12009, TNK12010, TNK13023, TNK13027, TNK13057, TNK13078, TNK15004, TNK16009, TNK16015, TNK16016, TNK17000, TNK18003, TNK18004, TNK18036, TNK20007, TNK20082, TNK20227. | Class 3.1A, B, C or D hazardous substances | Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 | This approval applies to designs for which TNK numbers have been registered with ERMA/EPA/WorkSafe New Zealand. Unique serial number to be stamped on each individual tank and recorded. Retention of individual tank fabrication and testing records. Allocation of individual tank serial numbers. Retention of individual tank QA records. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2025-07-14 | Fabricator of: TNK12005, TNK12006, TNK12007, TNK12008, TNK12009, TNK12010, TNK13023, TNK13027, TNK13057, TNK13078, TNK15004, TNK16009, TNK16015, TNK16016, TNK17000, TNK18003, TNK18004, TNK18036, TNK20007, TNK20082, TNK20227.
TNK20071 | 2021-04-09 | Christian Cas |  | AS1692: 2006 | Description: 25,000 litre single skin above ground insulated cylindrical vertical tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Christian Cas Capacity: 25,000 Litres Compartments: 1 Maximum Safe Fill Level: 24,150 Litres | Name: Sodium hydroxide, > 5% aqueous solution Class(es): 6.1D, 8.1A, 8.2B, 8.3A | Steelfort Engineering Company Limited 500 Rangitikei Street, Cloverlea, Palmerston North, 4412 | This approval becomes invalid following any change to the referenced contents, designs, duty and drawings. Randall & Associates Ltd - Statement of Design Compliance - Wind and Seismic Certification - Certificate No.: MS60916, dated 24/03/2021. Compliance with AS1692:2006. | N/A
TNK20072 | 2021-04-29 | APD Limited |  | AS 2634 - 1983 | Description: Vertical cylindrical acid storage tank Design Specification: AS 2634 - 1983 Tank Type: Above Ground Stationary Tank Name of Designer: APD Limited Capacity: 10,725 litres Compartments: 1 Internal PVC lining. Maximum safe fill level: 2,272 mm. | Name: 98% Sulphuric acid Class(es): 6.1D, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A | Ecolab Limited 6 Daniel Place, Te Rapa, Hamilton, 3200 | This approval becomes invalid following any change to the referenced drawings, duty or service. | N/A
TNK20073 | 2021-04-21 | Longveld Limited PO Box 5538, Frankton, Hamilton, 3242 153 Ellis Street, Frankton, Hamilton, 3204 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton FAB0071 | AS1692: 2006 | Description: 316 S/S Vertical Insulated Cone Roof Conical bottom on legs Design Specification: AS 1692:2006 Tank Type: Above Ground Stationary Tank Name of Designer: Longveld Capacity: 14,305 L Compartments: 1 | Substance Name: 1-4% Nitric Acid Class(es): 6.9B, 8.1A, 8.2C, 8.3A | Tetra Pak (New Zealand) Limited 6-8, Melody Ln, Ruakura, Hamilton 3216 | Seismic to AS/NZS 1170.5:2004 Coeff 0.31, Wind to AS/NZs 1170.2:2004. | 2071-12-31 | FAB0071
TNK20074 | 2021-04-16 | Index Engineering Limited 1340 Hinemoa Street, Rotorua, 3010 |  | ASME 8 Division 1 2018 | Description: 304L S/S Horizontal Vessel Dished Ends Design Specification: ASME 8 Div 1 2018 Tank Type: Process Container Name of Designer: Index Engineering Capacity: 37,380 L Compartments: 1 Site ID 41TK013 | Substance Name: Wood Turpentine Class(es): 3.1B, 6.1D |  | Vessel designed to replace carbon steel vessel at OJI Fibre Solutions Tasman Pulp Mill, Fletcher Ave Kawerau. Build is PFS Engineering 175 Riverlea Road Hillcrest, Hamilton, New Zealand. PO Box 350 Hamilton 3240 New Zealand Hamilton Seismic to NZS 1170.5:2004 | 2051-12-31
TNK20075 | 2021-04-23 | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 FAB20076 As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | SWRI 95-03 | Description: Supervault Tank 327-54630 Design Specification: SWRI 95-03 Tank Type: Above Ground Stationary Tank Name of Designer: Fuelchief Capacity: 54,630 L | Substance Name: Flammable Liquids Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 | SWRI Report 01-26260-01-701 SWRI Approval ID 14177-03-04 (2740mm H x 3000mm W x 8771mm L) AS1692 Type 3 | 2026-04-23 | FAB0076 As of 19/03/2023 FAB0093
TNK20076 | 2021-04-23 | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 FAB20076 As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | SWRI 95-03 | Description: Supervault Tank 327-73630 Design Specification: SWRI 95-03 Tank Type: Above Ground Stationary Tank Name of Designer: Fuelchief Capacity: 73,630 L | Substance Name: Flammable Liquids Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 | SWRI Report 01-26260-01-701 SWRI Approval ID 14177-03-04 (2740mm H x 3000mm W x 12160mm L) AS1692 Type 3 | 2026-04-23 | FAB0076 As of 19/03/2023 FAB0093
TNK20077 | 2021-04-23 | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 FAB0076 As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | SWRI 95-03 | Description: Supervault Tank 327-88000 Design Specification: SWRI 95-03 Tank Type: Above Ground Stationary Tank Name of Designer: Fuelchief Capacity: 88,000 L | Substance Name: Flammable Liquids Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 | SWRI Report 01-26260-01-701 SWRI Approval ID 14177-03-04 (2740mm H x 3000mm W x 14478mm L) AS1692 Type 3 | 2026-04-23 | FAB0076 As of 19/03/2023 FAB0093
TNK20078 | 2021-05-12 | Longveld Limited PO Box 5538, Frankton, Hamilton, 3242 153 Ellis Street, Frankton, Hamilton, 3204 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton FAB0071 | AS1692: 2006 | Description: 316L SS Vertical Cone Roof & Floor on legs. Cat 5 Design Specification: AS1692: 2006 Tank Type: Process Container Name of Designer: Longveld NZ Capacity: 9,985 L Compartments: 1 | Substances Name: Nitric Acid 2% Class(es): 6.9B, 8.1A, 8.2C, 8.3A | Tetra Pak (New Zealand) Limited 6-8, Melody Ln, Ruakura, Hamilton 3216 | Tank is designed for Christchurch seismic and environmental conditions. | 2071-05-12 | FAB0071
TNK20079 | 2021-05-12 | Longveld Limited PO Box 5538, Frankton, Hamilton, 3242 153 Ellis Street, Frankton, Hamilton, 3204 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton FAB0071 | AS1692: 2006 | Description: 316L SS Vertical Cone Roof & Floor on legs. Design Specification: AS1692: 2006 Tank Type: Process Container Name of Designer: Longveld NZ Capacity: 9,985 L Compartments: 1 | Substances Name: Caustic 2% Class(es): 8.1A, 8.2C, 8.3A | Tetra Pak (New Zealand) Limited 6-8, Melody Ln, Ruakura, Hamilton 3216 | Tank is designed for Christchurch seismic and environmental conditions. | 2071-05-30 | FAB0071
FAB0086 | 2021-05-21 |  | Polymaster Pty Ltd 161 Karinie Street Victoria 3585 Australia | AS/NZS 4766:2006; Above Ground Rotationally-Moulded Polyethylene Stationary Tanks Safe Work Instrument 2017 | Refer to individual TNK numbers: TNK20050, TNK20051, TNK20052 | Class(es): 6.1A, 6.1B, 6.1C, 6.1D, 8.1A, 8.2A, 8.2B, 8.2C substances | Polymaster Pty Ltd 161 Karinie Street Victoria 3585 Australia | Fabricator must maintain ISO 9001:2015 certification | 2024-04-07 | Fabricator of: TNK20050, TNK20051, TNK20052
TNK20080 | 2021-07-01 | Mercer Stainless - P.Claridge | Mercer Stainless Limited 53 Lunns Road, Middleton Christchurch 8024. FAB0077 | AS1692: 2006 | Description: 12,428 litre single skin above ground insulated cylindrical vertical tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Mercer Stainless - P.Claridge Capacity: 12,428 litres Compartments: 1 Maximum Safe Fill Level: 12,000 litres | Name: Nitric acid up to 2%Class(es): 6.9B, 8.1A, 8.2C, 8.3A Name: Sodium hydroxide up to 5% Class(es): 6.9B, 8.1A, 8.2C, 8.3A | Mercer Stainless Limited 53 Lunns Road, Middleton, Christchurch, 8024 | This approval becomes invalid following any change to the referenced contents, designs, duty service, drawings or applicable standards. Compliant with AS 1692:2006, Category 5. Producer Statement - PS1 - Design: 12m3 Dilute Acid Tank, by Bevan White, CPEng #108276, dated 2/06/2021, on behalf of: Calibre Consulting Ltd. Calibre Consulting Ltd - Calculations for: 12m3 Acid Tank at Hokitika – Legs and Bolts review, dated 25/05/2021. | N/A | FAB0077
TNK20081 | 2021-06-22 | Hendl & Murray Engineering Limited - Deon den Otter | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | AS1692: 2006 | Description: Myrcene Decanter Vessel - 3,750L above ground cylindrical vertical single skin process container Design Specification: AS1692: 2006 Tank Type: Process Container Name of Designer: Hendl & Murray Engineering Limited - Deon den Otter Capacity: 3,750 litres Compartments: 1 Maximum Safe Fill Level: 3,560 litres | Name: Myrcene Class(es): 3.1C, 6.1E, 6.3A, 6.4A, 6.8B, 9.1A, 9.1B. | Hendl & Murray Engineering Limited PO Box 5492, Frankton, Hamilton, 3242 103 Tawa Street, Melville, Hamilton, 3206 | This approval becomes invalid following any change to the referenced contents, designs, duty service, drawings or applicable standards. Design Statement – Mainstream Engineering Limited – Mohammed Aiyaaz CPEng – MS977 – 10/06/2021 - PC 165: AS 1692 - 2006 with seismic stress checks done to AS 1210 - 2010 using seismic coefficients derived from NZS 1170.5 - 2004 (Seismic is worst case not wind) and anchor bolts checks to AS 3990 - 1993. | N/A | FAB0033
TNK20082 | 2021-06-15 | Daniel Thomas | Prior to 17/10/2023: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS1692: 2006 | Description: 1,460 litres double skin above ground rectangular tank design Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Daniel Thomas Capacity: 1,460 Litres Compartments: 1 Safe Fill Level: 1,416 Litres | Name: Diesel Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Protank Industries Limited PO Box: Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 | This approval becomes invalid following any change to the referenced contents, designs, duty service, drawings or applicable standards. Approved to supply a generator (engine). | N/A | Prior to 17/10/2023: FAB0085 As of 17/10/2023: FAB0096
TNK20083 | 2021-06-29 | Fuel Storage Limited - Baz | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu 3840 FAB0050 | AS1692: 2006 Category 3 | Description: 7,780 litre double skinned above ground rectangular horizontal stationary tank Design Specification: AS1692: 2006 Category 3 Tank Type: Above Ground Stationary Tank Name of Designer: Fuel Storage Limited - Baz Capacity: 7,780 Litres Compartments: 1 Safe Fill Level: 7,160 litres | Name: Diesel Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuel Storage Limited 700 Bond Road, Te Awamutu, 3800 700 Bond Road, Te Awamutu, 3800 | This approval becomes invalid following any change to the referenced contents, designs, duty service, drawings or applicable standards. 10,000L Double Skin Tank HSWA Compliance Report LCZ Project No: 1101038.02 (11-01038.02-06-RPT-0001 (wet), Rev 0) – Note that this 7,500L tank is a cutdown version of the 10,000 litres tank so the wind and seismic loading would be adequate and held to the same restraint requirements as the 10,000 litres tank. | N/A | FAB0050
TNK20084 | 2021-06-22 | Fuelchief Limited | Quindao Jinhuanghai Container Co Ltd c/- Fuelchief Ltd 5 Tanya Street Bromley, Christchurch FAB0069 | AS1692: 2006 Category 3 | Description: DC200 Fuel Tank - 19,430 litres double skinned above ground rectangular horizontal stationary tank Design Specification: AS1692: 2006, Category 3 Tank Type: Above Ground Stationary Tank Name of Designer: Fuelchief Limited Capacity: 19,430 litres Compartments: 1 Safe Fill Level: 18,300 litres | Name: Diesel Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuelchief Limited PO Box 41 029, Christchurch, 8247 5 Tanya Street, Bromley, Christchurch, 8062 | This approval becomes invalid following any change to the referenced contents, designs, duty service, drawings or applicable standards. Motovated Design & Analysis - Design Statement - Seismic Assessment of DC200 Double-Skin Above ground fuel Storage Tank - Certificate Number: 5997-0003 - Drawing Number DC200_v3 - 25 August 2020 - Joseph Bain CPEng 248672: - Maximum Horizontal Elastic Site Spectra = 1.0 - Maximum Vertical Elastic Site Spectra = 1.0 Under these actions, the tank must be restrained to the foundation with minimum six anchors per long side, with the specified anchors being sufficient to resist the following maximum forces - 10.5kN (Tension Force) & 10.1kN (Shear Force) Motovated Design & Analysis - Design Statement - DC200 Double-Skin Above ground Fuel Storage Tank - Certificate Number: 5997-0002 - 4/8/2020 - Joseph Bain CPEng 248672: Hydrostatic pressure tests defined by AS 1692:2006 clause 2.8.2 for both the inner and outer tanks & deflection of the tank walls under these test conditions is within the limits defined by AS 1692:2006 clause 3.4.2. | N/A | FAB0069
TNK20085 | 2021-06-18 | AECOM | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 |  | Description: 10,910 litres single skin above ground insulated cylindrical vertical tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: AECOM Capacity: 10,910 litres Compartments: 1 Safe Fill Level: 9,500 litres | Name: Antisapstain Class(es): 3.1D, 6.1D, 6.5A, 6.6A, 6.8A, 6.9A, 8.2B, 8.3A | Hendl & Murray Engineering Limited PO Box 5492, Frankton, Hamilton, 3242 103 Tawa Street, Melville, Hamilton, 3206 | This approval becomes invalid following any change to the referenced contents, designs, duty service, drawings or applicable standards. MechEng report 201791 RP01 RevA Koopers Performance Chemicals Design Report 09/11/2020 by Tom Roberts CPEng, CMEngNZ, MEng. | N/A | FAB0033
TNK20086 | 2021-07-28 | Mercer Stainless Limited - M Paul | Mercer Stainless Limited 53 Lunns Road, Middleton Christchurch 8024. FAB0077 | AS 1692:2006, Category 5 | Description: 10,240 litre single skin above ground insulated cylindrical vertical tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Mercer Stainless Limited - M Paul Capacity: 10,240 litres Compartments: 1 Safe Fill Level: 9,927 litres | Name: Nitric acid up to 2% Class(es): 6.9B, 8.1A, 8.2C, 8.3A Name: Sodium hydroxide up to 5% Class(es): 6.9B, 8.1A, 8.2C, 8.3A Name: Sodium hypochlorite up to 5% Class(es):8.3A | Mercer Stainless Limited PO Box 6020, Christchurch, 8442 53 Lunns Road, Middleton, Christchurch, 8024 | Also approved for the different tank drawing of drawing No.: 21204, Rev C, Sheets 1 of 1, Dated: 25/06/2021, Drawn by: MPaul1, Title: General Arrangement - 10m3 Re-Use Acid CIP Tank - Hokitika - Vertex Engineers Ltd. Includes the storage and transfer of Principal having hazard classification of 9.1D and for substance/product name AC-300. Producer Statement - PS1 - Design: 10m3 Re-Use Acid CIP tank and 10m3 Recovered Caustic tank (excludes foundation), by Bevan White, CPEng #108276, dated 19/07/2021, on behalf of: Calibre Consulting Ltd. Installed tank location specific to 56 Livingstone Street, Hokitika. Calibre Consulting Ltd - Calculations for: 10m3 Re-use Acid CIP Tank at Hokitika – PS1 review, dated 8/06/2021. This approval becomes invalid following any change to the referenced contents, designs, duty service, drawings or applicable standards. | N/A | FAB0077
TNK20088 | 2021-11-25 | Robin King Engineers Ltd. |  | AS1692: 2006 Category 5 | Description: 27,000 L 314 grade stainless steel Alpha desulph decanting tank 1 Design Specification: AS1692:2006 Category 5 Tank Type: Above Ground Stationary Tank Name of Designer: Robin King Engineers Ltd. Capacity: 27kL. Compartments: 1 | Name: Alpha Pinene (Pinechem 500) UN2368 Class(es): 3.1C, 6.1D, 8.3A | Contract Mechanical Services Limited 11 Harvard Way, Mt Maunganui | Tank serial number 200. Design temperature 70 deg C. 3m OD x 4.5m high x 5mm strakes. Joint efficiency 0.7 (no radiography). Safe fill height 4.224m. High level alarm 4m. Hi Hi level alarm 4.12m. Roof pitch 10 degrees. Top curb angle 50x50x6 mm. Design life 50 years. Location Lawter NZ, 211 Totara Street, Mt Maunganui. Wind and seismic design to NZS 1170.2 and NZS 1170.5 Robin King Engineers report 21027 dated 17 Nov 2021. Seismic zone 0.2. Maximum specific gravity 1.0. Sp = 1.0 Site sub soil class D. Tank design pressure 1.6 kPa. Design vacuum -0.75 kPa. Venting to API2000, AS1940. Maximum fill rate 250L/min. Maximum pump out rate 333L/min. Vent fitted with end of line PV vent with integral deflagration arrestor. (Protectoseal Series 51600). Emergency pressure relief manhole cover vent (Protectoseal Series 51600). Tank anchored by 8 number M24 316 ss anchor bolts on 3.11m PCD. Anchors cast in 8 drossbach 102 mm diameter tubes. Sika 212 grout. Minimum embedment of anchor in grout 61 mm. Minimum embedment of drossbach tube into concrete 183 mm. Minimum concrete thickness at anchors based on minimum embedment to be 285mm. Minimum edge distance 150 mm. Concrete strength 32 MPa. Hydrotest level to explosion manway. Hydrostatic pressure test witnessed 19 November 2021. | 2026-11-25
TNK20089 | 2021-10-11 | Proto Cold Services Ltd |  | AS1692: 2006 Category 5 | Description: 6,000 litre CIP tank No.2 Design Specification: AS1692: 2006 Category 5 Tank Type: Above Ground Stationary Tank Name of Designer: Proto Cold Services Ltd Capacity: 6,000 litres Compartments: 1 | Name: CIP acid/caustic 1-2% max sg 1.02 Class(es): 6.1D, 8.3A | Etech NZ Limited 130 Kaimanawa Street, Palmerston North, 4414 | The tank data plate is to be stamped in accordance with the Health and Safety at Work (Hazardous Substances) Regulations 2017 Subpart 15 Regulation 17.76 Marking stationary tanks. Tank serial number T129. Design temperature 85 deg C. 6,000 L 316 s/s tank to AS1692 category 5. Joint efficiency 0.7 (no radiography). No dye pen NDT carried out on instructions of Fonterra. 1.724m ID x 4.05m high from floor datum x 4 mm strakes. Safe fill height 3.375m from floor. Hi level alarm at 6410L capacity. Hi Hi level alarm 6570L capacity. Roof pitch 15 degrees. Design life 50 years. Location Fonterra, Kapanui, Kaponga. Seismic design to NZS 1170.5 Proto Cold Services Ltd report Job 4046 T129. Seismic zone 0.18. Max S.G. 1.02. Importance level 2.0. Site subsoil class B. Tank design pressure Atmospheric. Venting to API2000, AS1940. Max pump in rate 100cu.m/hr. Max pump out rate 100cu.m/hr. 273mm Sch 10 natural vent. Foundations to be designed by others and PS1 to be provided to Fonterra for producing to the site location test certifier on request. | 2026-10-11
TNK20090 | 2021-10-11 | Proto Cold Services Ltd |  | AS1692: 2006 Category 5 | Description: 6,000 litre CIP Caustic Tank T160 Design Specification: AS1692: 2006 Category 5 Tank Type: Above Ground Stationary Tank Name of Designer: Proto Cold Services Ltd. Capacity: 6,000 litres. Compartments: 1 | Name: Dilute caustic soda max S.G. 1.02 Class(es): 6.1D, 8.1A, 8.2B, 8.3A | Etech NZ Limited 130 Kaimanawa Street, Palmerston North, 4414 | The tank data plate is to be stamped in accordance with the Health and Safety at Work (Hazardous Substances) Regulations 2017 Subpart 15 Regulation 17.76 Marking stationary tanks. Tank serial number T160. Design temperature 85 deg C. 6,000 L 316 s/s tank to AS1692 category 5. Joint efficiency 0.7 (no radiography). No dye pen NDT carried out on instructions of Fonterra. 1.724m ID x 4.49m high from floor datum x 4 mm strakes. Safe fill height 3.685m from floor. Hi level alarm at 6272L capacity. Hi Hi level alarm 6335L capacity. Roof pitch 15 degrees. Design life 50 years. Location Fonterra, Kapanui, Kaponga. Seismic design to NZS 1170.5 Proto Cold Services Ltd report Job 4046 T129. Seismic zone 0.18. Max S.G. 1.02. Importance level 2.0. Site subsoil class B. Tank design pressure Atmospheric. Venting to API2000, AS1940. Max pump in rate 100cu.m/hr. Max pump out rate 100cu.m/hr. 273mm Sch 10 natural vent. Foundations to be designed by others and PS1 to be provided to Fonterra for producing to the site location test certifier on request. | 2026-10-11
TNK20091 | 2021-10-11 | Proto Cold Services Ltd |  | AS1692: 2006 Category 5 | Description: 10,000 litre nitric acid storage tank max. SG 1.02 Design Specification: AS1692: 2006 Category 5 Tank Type: Above Ground Stationary Tank Name of Designer: Proto Cold Services Ltd. Capacity: 10,000 litres Compartments: 1 | Name: Dilute nitric acid max SG 1.02 Class(es): 6.1D, 8.3A | Etech NZ Limited 130 Kaimanawa Street, Palmerston North, 4414 | The tank data plate is to be stamped in accordance with the Health and Safety at Work (Hazardous Substances) Regulations 2017 Subpart 15 Regulation 17.76 Marking stationary tanks. Tank serial number T161. Design temperature 85 deg C. 10,000 L 316 s/s tank to AS1692 category 5. Joint efficiency 0.7 (no radiography). No dye pen NDT carried out on instructions of Fonterra. 1.75m ID x 6.195m high from floor datum x 4 mm strakes. Safe fill height 5.385m from floor. Hi level alarm at 10,568L capacity. Hi Hi level alarm 10,675L capacity. Roof pitch 15 degrees. Design life 50 years. Location Fonterra, Kapanui, Kaponga. Seismic design to NZS 1170.5 Proto Cold Services Ltd report Job 4046 T129. Seismic zone 0.18. Max S.G. 1.02. Importance level 2.0. Site subsoil class B. Tank design pressure Atmospheric. Venting to API2000, AS1940. Max pump in rate 100cu.m/hr. Max pump out rate 100cu.m/hr. 273mm Sch 10 natural vent. Foundations to be designed by others and PS1 to be provided to Fonterra for producing to the site location test certifier on request. | 2026-10-11
TNK20092 | 2021-10-11 | Proto Cold Services Ltd |  | AS1692: 2006 Category 5 | Description: 8,000 litre CIP rinse recovery tank T162 Design Specification: AS1692: 2006 Category 5 Tank Type: Above Ground Stationary Tank Name of Designer: Proto Cold Services Ltd. Capacity: 8,000 litres. Compartments: 1 | Name: CIP rinse recovery Class(es): 6.1D, 8.3A | Etech NZ Limited 130 Kaimanawa Street, Palmerston North, 4414 | The tank data plate is to be stamped in accordance with the Health and Safety at Work (Hazardous Substances) Regulations 2017 Subpart 15 Regulation 17.76 Marking stationary tanks. Tank serial number T162. Design temperature 85 deg C. 8,000 L 316 s/s tank to AS1692 category 5. Joint efficiency 0.7 (no radiography). No dye pen NDT carried out on instructions of Fonterra. 1.75m ID x 5.19m high from floor datum x 4 mm strakes. Safe fill height 4.385m from floor. Hi level alarm at 8120L capacity. Hi Hi level alarm 8202L capacity. Roof pitch 15 degrees. Design life 50 years. Location Fonterra, Kapanui, Kaponga. Seismic design to NZS 1170.5 Proto Cold Services Ltd report Job 4046 T129. Seismic zone 0.18. Max S.G. 1.02. Importance level 2.0. Site subsoil class B. Tank design pressure Atmospheric. Venting to API2000, AS1940. Max pump in rate 100cu.m/hr. Max pump out rate 100cu.m/hr. 273mm Sch 10 natural vent. Foundations to be designed by others and PS1 to be provided to Fonterra for producing to the site location test certifier on request. | 2026-10-11
TNK20093 | 2021-09-22 | Fuel Storage Limited | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu 3840 FAB0050 | AS 1692-2006, Category 3 | Description: Rectangular double skin Design Specification: AS 1692-2006, Category 3 Tank Type: Above Ground Stationary Tank Name of Designer: Fuel Storage Limited Capacity: 10,300 litres Compartments: 1 Safe Fill Level: 10,000 litres | Name: Diesel Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuel Storage Limited PO Box 108, Te Awamutu, 3840 700 Bond Street, Te Awamutu, 3800 | This approval becomes invalid following any change to the referenced drawings, contents, duty, service and / or original design parameters. Refer Logicamms statement of design compliance No. 11-01038.02-06-RPT-001, Rev 0. Allocate unique serial number for each tank and retain individual tank fabrication records. | N/A | FAB0050
TNK20095 | 2021-08-11 | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 FAB0069 | AS 1692: 2006 Reduced Secondary Containment for Certain Above Ground Stationary Tanks Safe Work Instrument 2017 | Description: SC50CAB, Category 3 Rectangular Tank 2870mmL x 1304mmH x 2256mmW x 5mmWT Design Specification: AS 1692:2006 and SWI Reduced Secondary Containment for Tanks Tank Type: Above Ground Stationary Tank Name of Designer: Fuelchief Capacity: 4500 L (Safe Fill Level) Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 |  | 2026-08-11 | FAB0069
TNK20096 | 2021-08-31 | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 FAB0069 | AS 1692: 2006 Reduced Secondary Containment for Certain Above Ground Stationary Tanks Safe Work Instrument 2017 | Description: FC30, Category 3 Rectangular Tank 6000mmL x 2438mmH x 2896mmW x 5mmWT Design Specification: AS 1692:2006 and SWI Reduced Secondary Containment for Tanks Tank Type: Above Ground Stationary Tank Name of Designer: Fuelchief Capacity: 28,500 L (Safe Fill Level) Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 |  | 2026-08-31 | FAB0069
TNK20097 | 2021-10-28 | Maskell Productions Limited |  | UL 1316:1994 | Description: 15,000 litre two compartment Fuel additive UGST Design Specification: UL 1316:1994 Tank Type: Below Ground Stationary Tank Name of Designer: Maskell Productions. Capacity: 15,000 litres. Split Tank Compartments: 2 | Name: Diesel and gasoline fuel additives #29527(9889) and diesel additive #29528(9043F) Class(es): 3.1C, 3.1D, 6.1C, 6.1D, 6.5B, 8.3A | Maskell Productions Limited 24 Bowen Road, Auckland, 1060 | Tank serial number 21053419. Design drawing 1037.15.19 Rev 1. Maximum s.g. 0.975. Design specification UL1316:2018. Design pressure Atmospheric. Test pressure 50 kPa. Tank inside diameter 2m. Overall length 5.25m. Tank safe fill volume Compartment 1 petrol additive 8,200L Compartment 2 diesel additive 6,200L. Tank total volume Compartment 1 petrol additive 8,790L Compartment 2 diesel additive 6597L. Hetron 980-35 epoxy vinyl ester resin inner liner minimum thickness 2.5 mm. Tank to be installed strictly in accordance with Envirotank installation instructions for petroleum storage tanks Publication No. Inst Ins 02 Rev 2017. Tank to be installed by Maskells Productions Ltd trained and authorised installers. | 2026-10-28
TNK20104 | 2021-08-04 | Colin MacKay (CMK Eng) (Mech), RPEQ (6101) |  | API Standard 650 | Description: Mild Steel vertical single skin self supported roof Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Colin MacKay (CMK Eng). (Mech), RPEQ (6101) Capacity: 30.2 cubic meters Compartments: 1 | Name: Sarmix Oxcel C Class(es): 6.1B, 6.1C, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 6.9A, 8.1A, 8.2B, 8.3A | CMK Engineering P.O. Box 2236, Queensland Australia, North Ipswich, 4306 519 Riverside Drive, Pine Mountain QLD, North Ipswich, 4306 | T-10 originally designed and constructed by CT Engineering, Pokeno for Arch Wood Protect Ltd Feb 2021. Tank has been relocated within the bund and design verified to API 650 13th edition:2020 by CMK Engineering with the increase of seismic anchors to NZS 1170.5:2004. Shell weld efficiency of 70% is used for the calculations. Appendix A 7.2 applies to low set nozzles. Set on black steel BS1740 is not API 650, but is accepted for the no-load instrument mount service. Tank to be located at Archwood Protection NZ Limited - 265 James Fletcher Drive, Otahuhu, Auckland. | N/A
TNK20105 | 2021-11-12 | Hendl & Murray Engineering Limited - M.Singh | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | AS1629:2006, Category 5 | Description: 5,000 litres single skin above ground insulated cylindrical vertical tank Design Specification: AS1629:2006, Category 5 Tank Type: Above Ground Stationary Tank Name of Designer: Hendl & Murray Engineering Limited - M.Singh Capacity: 5,395 Litres Compartments: 1 Safe Fill Level: 5,000 Litres | Name: Sodium hydroxide concentration 46% - 50% Class(es): 6.1D, 6.1E, 8.1A, 8.2B, 8.3A, 9.1D | Hendl & Murray Engineering Ltd PO Box 5492, Frankton, Hamilton, 3242 103 Tawa Street, Melville, Hamilton, 3206 | Producer Statement – PS1 – Design: Issued By: Totara Engineering Limited, To: Deon den Otter, Hendl & Murray Engineering, In Respect of: 5,000 Litre Caustic Soda Vessel, At: Fontera Lichfield, State Highway 1, AS 1692 2006 and NZSEE Seismic design of storage tanks 2009, Dated: 27 Aug 2021, CPEng Ben Smit (CPEng # 228812). Design calculations for the Fonterra Lichfield 5000 litre Caustic soda tank - 0207-ME-CAL-001 Tank calculation worksheet Rev A. By: Totara Engineering, Issue date: 2021-Aug-27. This approval becomes invalid following any change to the referenced contents, designs, duty, service, drawings or applicable standards. | N/A | FAB0033
TNK20106 | 2021-11-23 | Johnathan Burtt | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu 3840 FAB0050 | AS1692-2006, Category 3 | Description: Rectangular single skin tank Design Specification: AS1692-2006, Category 3 Tank Type: Service Tank Name of Designer: Johnathan Burtt Capacity: 272 litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Fuel Storage Limited 700 Bond Road, Te Awamutu, 3800 | Approved to supply an engine or burner. Manufacturer to allocate a unique serial number for each tank built. Manufacturer to retain individual tank fabrication and test records. This approval becomes invalid following any change to the original design, duty, service conditions or referenced drawings. | 2046-11-23 | FAB0050
TNK20107 | 2021-10-04 | Longveld Limited PO Box 5538, Frankton, Hamilton, 3242 153 Ellis Street, Frankton, Hamilton, 3204 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton FAB0071 | AS1692: 2006 Category 5 | Description: 316L SS Vertical Cone Roof Tank Type: Above Ground Stationary Tank Name of Designer: Longveld NZ Capacity: 21,540 Litres Compartments: 1 | Name: Sulfuric Acid 98% Class(es): 6.1B, 6.7A, 8.1A, 8.2B, 8.3A | Tetra Pak (New Zealand) Limited 6-8, Melody Ln, Ruakura, Hamilton 3216 | Tank to be located at Fonterra Te Awamutu waste treatment, 415 Factory Rd, Te Awamutu 3800. Tank Seismic design life is 50 years. | N/A | FAB0071
TNK20108 | 2021-10-04 | Longveld Limited PO Box 5538, Frankton, Hamilton, 3242 153 Ellis Street, Frankton, Hamilton, 3204 | Longveld Limited 153-157 Ellis Street PO Box 5538 Frankton Hamilton FAB0071 | AS1692: 2006 Category 5 | Description: 316L SS Vertical Cone Roof Tank Type: Above Ground Stationary Tank Name of Designer: Longveld NZ Capacity: 21,540 Litres Compartments: 1 | Name: Caustic Soda 48% Class(es): 6.1D, 8.1A, 8.2B, 8.3A | Tetra Pak (New Zealand) Limited 6-8, Melody Ln, Ruakura, Hamilton 3216 | Tank to be located at Fonterra Te Awamutu waste treatment, 415 Factory Rd, Te Awamutu 3800. Tank Seismic design life is 50 years. | N/A | FAB0071
TNK20109 | 2021-11-08 | NDA Engineering Limited 709 Te Rapa Road, Te Rapa, Hamilton, 3200 |  | AS1692: 2006 | Description: 316L SS Vertical Cone Roof Tank Type: Above Ground Stationary Tank Name of Designer: NDA Engineering Capacity: 45,000 Litres | Name: Desmodur T-80 Class(es): 6.1A, 6.1B, 6.7B, 6.9B | NDA ENGINEERING LIMITED Private Bag 3018, Waikato Mail Centre, Hamilton, 3240 709 Te Rapa Road, Te Rapa, Hamilton, 3200 | Tanks to be located at Sleepyhead 88 Lumsden road Ohinewai | 2071-11-10
TNK20110 | 2021-12-06 | Petro Industrial | Zhangjiagang Fuel Equipment System Co. Ltd. 3 Haixin North Road, Nanfeng, Zhangjiagang, Jiangsu, China FAB0087 | AS 1692:2006, Category 3, UL 2085, SwRI 93-01, SWI Reduced Secondary Containment for Tanks | Description: 2,000 Litres Above Ground Double Skin Rectangular Fireguard(R) 93-01 Tank Design Specification: AS 1692:2006, Category 3, UL 2085, SwRI 93-01, SWI Reduced Secondary Containment for Tanks Tank Type: Above Ground Stationary Tank Name of Designer: Petro Industrial Capacity: 2,113 Litres Maximum Safe Fill Level: 2,000 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petro Industrial Pty. Ltd. PO Box 407, Narangba, Queensland, Australia, 4504 | Approved to supply a burner or engine. Compliant with UL 2085. SwRI 93-01 Tank, 4 hour fire rated tank. Structural Engineering Certification to AS/NZS 1170.2, NZS 1170.5 & AS 1657: Austica Pty. Ltd. Rev 0, Date 09/10/2021. Peter Kairu. Producer Statement – PS1 – Design: Issued by: Design Consulting Engineers & Inspection (DE International Ltd.), To: Petro Industrial, To be supplied to: All building consent authorities within NZ, In respect of: 2000L Diesel Fuel Tank (Z=0.6) All indoor. Drawing referred to FGC2000L-GA-F sheets 1-3. Signed by: Jhonnal L. Calleja CPEng # 263893 dated 18/10/21. SwRI Document of Compliance for Fireguard® 93-01 Tank, Revision No. 8. Issue Date: February 2021, SwRI Project No. 01.25000.02.077. SwRI Reference No. 15077-01/100-08. Petro Industrial - QA Documentation Package - Petro FGC2000 - Date: September 2021. Zhangjiagang Fuel Equipment System Co. Ltd. is a member of Steel tank Institute - Licensed Manufacturer of Fireguard - Certificate. Petro Industrial Pty. Ltd. and (FES) Zhangjiagang Fuel Equipment System Co. Ltd. responsibility to ensure each individual tank manufactured is installed with the suitable SwRI labelling. Allocate unique serial number for each tank and retain individual tank fabrication and test records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture / pressure test, AS 1692:2006 Category 3, test pressure in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Petro Industrial – Working Procedure – Pressure tests, Rev No. 3d, dated 03/06/2021. UL Test Report - MH17883-19940124 - Latest issue: 2020-10-19. Steel Tank Institute - Fireguard® - Document. UL 2085 Certificate of Compliance - Certificate Number: 20180129-MH62698 - Report Reference: MH17883-19940124 - Issue Date: 2018-JANUARY-29 - Issued to: Zhangjiagang Fuel Equipment System Co. Ltd. This approval becomes invalid following any change to the referenced contents, original design, duty, service conditions, referenced drawings or applicable standards | 2031-12-06 | FAB0087
TNK20111 | 2021-11-26 | NYMIC Engineering Limited | NYMIC Engineering Ltd FAB0023 | AS1692-2006, Category 3. Reduced Secondary Containment for Certain Above Ground Stationary Tanks Safe Work Instrument 2017 | Description: Rectangular double skin Design Specification: AS1692 SWI Reduced Secondary Containment for Tanks Tank Type: Above Ground Stationary Tank Name of Designer: Cameron Smith Capacity: 4,780 Litres Compartments: 1 Safe Fill Level: 4,540 Litres | Name: Diesel Class(es): 3.1D, 6.7B | Nymic Engineering Limited PO Box 17596, Sumner, Christchurch, 8042 19 Kilronan Place, Wigram, Christchurch, 8042 | Approved to supply an engine or burner. This approval becomes invalid following any change to the original design, duty, service conditions or referenced drawings Manufacturer to allocate a unique serial number for each tank built. Manufacturer to retain individual tank fabrication and test records. | 2046-11-26 | FAB0023
TNK20112 | 2021-11-26 | NYMIC Engineering Limited | NYMIC Engineering Ltd FAB0023 | AS1692-2006, Category 3. Reduced Secondary Containment for Certain Above Ground Stationary Tanks Safe Work Instrument 2017 | Description: Rectangular double skin Design Specification: AS 1692 SWI Reduced Secondary Containment for Tanks Tank Type: Above Ground Stationary Tank Name of Designer: Cameron Smith Capacity: 9,980 Litres Compartments: 1 Safe Fill Level: 9,480 Litres. | Name: Diesel Class(es): 3.1D, 6.7B | Nymic Engineering Limited PO Box 17596, Sumner, Christchurch, 8042 19 Kilronan Place, Wigram, Christchurch, 8042 | Approved to supply an engine or burner. This approval becomes invalid following any change to the original design, duty, service conditions or referenced drawings Manufacturer to allocate a unique serial number for each tank built. Manufacturer to retain individual tank fabrication and test records. | 2046-11-26 | FAB0023
FAB0087 | 2021-12-14 |  | Zhangjiagang Fuel Equipment System Co. Ltd. 3 Haixin North Road, Nanfeng, Zhangjiagang, Jiangsu, China | AS1692 / UL142 / UL2085 | Tanks up to 110,000 litres Licensed by Southwest Research Institute (SwRI) to manufacture tanks tested in accordance with SwRI 93-01, 95-03, 97-04 Testing Procedures. Reference: TNK20110, TNK20159, TNK20326, TNK20327 | 3.1A, 3.1B, 3.1C and 3.1D | Zhangjiagang Fuel Equipment System Co. Ltd. 3 Haixin North Road, Nanfeng, Zhangjiagang, Jiangsu, China | Fabrication, inspection and testing in accordance with the specified tank design and fabrication code, approved tank design drawings and approved for construction drawings. Allocation of individual tank serial numbers. Retention of individual tank QA records. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2024-12-14 | Fabricator of: TNK20110, TNK20159, TNK20326, TNK20327
TNK20113 | 2021-12-06 | Carlyon Civil Construction Ltd | Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | UL 142 Above Ground Stationary Tanks Connected to a Generator Set – Safe Work Instrument 2017 | Description: 500 Litre Rectangular single skin tank Design Specification: UL 142 SWI Above Ground Tank Connected to Gen Set Tank Type: Service Tank Name of Designer: Carlyon Civil Construction Limited - ANUP Capacity: 496 Litres Compartments: 1 Safe Fill Level: 471 Litres | Diesel having hazard classifications of 3.1D, 6.1E, 6.3B, 6. 7B, 9.1B. | Carlyon Civil Construction Ltd PO Box 10092, Te Rapa, Hamilton, 3200 3 Ellis Street, Frankton, Hamilton, 3204 | Approved to supply an engine or burner. Design, fabrication and testing compliance with UL 142. Producer Statement - PS1 - Design: Issed by: Chris W Howell & Associates Limited, To: Vocus, To be Supplied To: Auckland Council, In Respect of: Chiller Unit Support Platforms & Building Alterations, At: 7 Parkhead Place, Rosedale 0632, Town/City: Auckland, Lot: 12, DP: 117850. Signed by: Robert Good, CPEng # 142660, Dated 08.12.2020. If manufacturing of these service tanks are for a different site other than 7 Parkhead Place a new producer statement (PS1) will need to be provided to confirm the compliance with the wind & seismic requirements in the Health and Safety at Work (Hazardous Substances) Regulations 2017, Clause 17.6(3). 6475-0000, 500L Day Tank Support Design Statement, Rev00, Release, 25Nov21 - Design statement for tank supports to satisfy Clause 30.1.2 of UL142. Singed by: Joseph Bain, CPEng # 248672, Dated 25/11/21. Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. This approval becomes invalid following any change to the eferenced contents, original design, duty, service conditions, referenced Carlyon drawings or applicable standards. | 2031-12-06 | FAB0083
TNK20114 | 2021-12-13 | Hendl & Murray Engineering Limited - Deon den Otter | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | AS1692-2006, Category 5 | Description: Vertical cylindrical process container Design Specification: AS1692: 2006 Tank Type: Process Container Name of Designer: Deon den Otter Capacity: 7,070 Litres Compartments: 1 Safe Fill Level: 6,340 Litres | Name: Nitric acid up to 5% concentration Class(es): 6.9B, 8.1A, 8.2C, 8.3A | Hendl & Murray Engineering Ltd PO Box 5492, Frankton, Hamilton, 3242 103 Tawa Street, Melville, Hamilton, 3206 | Design Report By: MechEng, 211605 RP01 RevB, Techo HASNO Tanks Tank 8m3 Recovered Nitric Design Report, dated 27/09/2021 by Tom Roberts CPEng #1024350. Producer Statement – PS1 – Design: Issued By: Mech Eng Ltd, To: Hendl & Murray Engineering Ltd, In Respect of: Techno Fonterra, Te Awamutu 8m3 Recovered Nitric Acid Tank. Reference Number: 211605. Dated: 26 Nov 2021, CPEng Tom Roberts (CPEng # 1024350). Manufacturer to allocate a unique serial number for each tank built. Manufacturer to retain individual tank fabrication and test records. This approval becomes invalid following any change to the referenced contents, designs, duty, service, drawings or applicable standards. | 2046-12-13
TNK20115 | 2021-12-10 | Hendl & Murray Engineering Limited - M.Singh | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | AS 1692:2006, Category 5 | Description: 15,000 Litres single skin above ground insulated cylindrical vertical tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Hendl & Murray Engineering Limited - M.Singh Capacity: 16,000 Litres Maximum Safe Fill Level: 15,000 Litres (3,740mm) Compartments: 1 | Name: Sodium hydroxide concentration 5% - 45% Class(es): 6.1D, 8.1A, 8.2B, 8.3A, 9.1D | Hendl & Murray Engineering Limited PO Box 5492, Frankton, Hamilton, 3242 | Design Report: By: MechEng: 211601 RP01 RevA, Techo HASNO Tanks Tank 15m3 Clean and Recovered Caustic Design Report, dated 22/09/2021 by Tom Roberts CPEng #1024350. Producer Statement – PS1 – Design: Issued By: Mech Eng Ltd, To: Hendl & Murray Engineering Ltd, In Respect of: Techno Fonterra, Te Awamutu 15m3 Clean Caustic Tank, At: Fonterra Te Awamutu, 1498 Alexandra Street, Te Awamutu 3800. Reference Number: 211601. Design Actions: NZS 1170.5:2004, AS/NZS 1170.2:2011, NZSEE SDST:2009, Hold Down Bolts: EOTA TR 029:210, EOTA TR 045:2013, Supporting Structure: NZSEE SDST:2009, Strake/Wall Design: NZSEE SDST:2009, Ventilation: API 2000 5th Edition, Design Standard: AS 1692:2006, Dated: 26 Nov 2021, CPEng Tom Roberts (CPEng # 1024350). Producer Statement – PS1 – Design: Issued By: Mech Eng Ltd, To: Hendl & Murray Engineering Ltd, In Respect of: Techno Fonterra, Te Awamutu 15m3 Recovered Caustic Tank, At: Fonterra Te Awamutu, 1498 Alexandra Street, Te Awamutu 3800. Reference Number: 211602. Design Actions: NZS 1170.5:2004, AS/NZS 1170.2:2011, NZSEE SDST:2009, Hold Down Bolts: EOTA TR 029:210, EOTA TR 045:2013, Supporting Structure: NZSEE SDST:2009, Strake/Wall Design: NZSEE SDST:2009, Ventilation: API 2000 5th Edition, Design Standard: AS 1692:2006, Dated: 26 Nov 2021, CPEng Tom Roberts (CPEng # 1024350). If manufacturing of the reference tank drawings are for a different site other than the ones listed in the PS1's above new producer statements (PS1's) will need to be provided to confirm the compliance with the wind & seismic requirements in the Health and Safety at Work (Hazardous Substances) Regulations 2017, Clause 17.6(3). Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. This approval becomes invalid if any change to the referenced contents, original design, duty, service conditions, referenced Hendl & Murray Engineering Limited drawings or applicable standard/s. | 2031-12-10 | FAB0033
TNK20116 | 2021-12-10 | Hendl & Murray Engineering Limited - Deon den Otter | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | AS 1692:2006, Category 5 | Description: 2,000 Litres single skin above ground insulated cylindrical vertical process container Design Specification: AS1692: 2006 Tank Type: Process Container Name of Designer: Hendl & Murray Engineering Limited - Deon den Otter Capacity: 2,000 Litres Compartments: 1 Maximum Safe Fill Level: 1,720 Litres (1,095mm) | Nitric Acid up to 5% concentration having a hazard classification of 6.1E, 6.9B, 8.1A, 8.2C, 8.3A and Caustic (Sodium Hydroxide) up to 5% concentration having a hazard classification of 6.1E, 8.1A, 8.2C, 8.3A. | Hendl & Murray Engineering Ltd PO Box 5492, Frankton, Hamilton, 3242 103 Tawa Street, Melville, Hamilton, 3206 | Design Report: By: MechEng: 211603 RP01 RevA, Techo HASNO Tanks Tank 2m3 Recovered Chemical Balance Design Report, dated 08/09/2021 by Tom Roberts CPEng #1024350. Producer Statement – PS1 – Design: Issued By: Mech Eng Ltd, To: Hendl & Murray Engineering Ltd, In Respect of: Techno Fonterra, Te Awamutu 2m3 Recovered Chemical Balance Tank, At: Fonterra Te Awamutu, 1498 Alexandra Street, Te Awamutu 3800. Reference Number: 211603. Design Actions: NZS 1170.5:2004, AS/NZS 1170.2:2011, NZSEE SDST:2009, Hold Down Bolts: EOTA TR 029:210, EOTA TR 045:2013, Supporting Structure: NZSEE SDST:2009, Strake/Wall Design: NZSEE SDST:2009, Ventilation: API 2000 5th Edition, Design Standard: AS 1692:2006, Dated: 26 Nov 2021, CPEng Tom Roberts (CPEng # 1024350). If manufacturing of this tank is for a different site other than the one listed in the PS1 above a new producer statement (PS1) will need to be provided to confirm the compliance with the wind & seismic requirements in the Health and Safety at Work (Hazardous Substances) Regulations 2017, Clause 17.6(3). Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. This approval becomes invalid following any change to the referenced contents, original design, duty, service conditions, referenced Hendl & Murray Engineering Limited drawings or applicable standard/s. | 2031-12-10 | FAB0033
TNK20117 | 2021-12-10 | Hendl & Murray Engineering Limited - M.Singh | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | AS 1692:2006, Category 5 | Description: 30,000 Litres single skin above ground insulated cylindrical vertical tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Hendl & Murray Engineering Limited - M.Singh Capacity: 31,500 Litres Compartments: 1 Maximum Safe Fill Level: 30,000 Litres (3,765mm) | Nitric Acid up to 5% concentration having a hazard classification of 6.1E, 6.9B, 8.1A, 8.2C, 8.3A. | Hendl & Murray Engineering Ltd PO Box 5492, Frankton, Hamilton, 3242 103 Tawa Street, Melville, Hamilton, 3206 | Design Report: By: MechEng: 211604 RP01 RevA, Techo HASNO Tanks Tank 30m3 Recovered Nitric Design Report, dated 22/09/2021 by Tom Roberts CPEng #1024350. Producer Statement – PS1 – Design: Issued By: Mech Eng Ltd, To: Hendl & Murray Engineering Ltd, In Respect of: Techno Fonterra, Te Awamutu 30m3 Recovered Nitric Acid Tank, At: Fonterra Te Awamutu, 1498 Alexandra Street, Te Awamutu 3800. Reference Number: 211604. Design Actions: NZS 1170.5:2004, AS/NZS 1170.2:2011, NZSEE SDST:2009, Hold Down Bolts: EOTA TR 029:210, EOTA TR 045:2013, Supporting Structure: NZSEE SDST:2009, Strake/Wall Design: NZSEE SDST:2009, Ventilation: API 2000 5th Edition, Design Standard: AS 1692:2006, Dated: 26 Nov 2021, CPEng Tom Roberts (CPEng # 1024350). If manufacturing of this tank is for a different site other than the one listed in the PS1 above a new producer statement (PS1) will need to be provided to confirm the compliance with the wind & seismic requirements in the Health and Safety at Work (Hazardous Substances) Regulations 2017, Clause 17.6(3). Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. This approval becomes invalid following any change to the referenced contents, original design, duty, service conditions, referenced Hendl & Murray Engineering Limited drawings or applicable standard/s. | 2031-12-10 | FAB0033
TNK20118 | 2021-12-10 | Isaac Walker | PLASPOKE LIMITED 35 Saleyards Road, Ōtāhuhu, Auckland, 1062 FAB0094 | BS EN 12573 and Hazardous Substances - Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: Vertical cylindrical storage tank Design Specification: BS EN 12573 SWI Thermoplasic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: PLASCT-01, Sheets 1-4 incl., Rev A, dated 08-12-2021 Name of Designer: Isaac Walker Capacity: Up to 60,000 litres Compartments: 1 | Name: Class 6, 8 & 9 hazardous liquids Class(es): 6.1A, 6.5A, 6.6A, 6.7A, 6.8A, 6.9A | PLASPOKE LIMITED 35 Saleyards Road (Unit 8), Otahuhu, Auckland, 1062 | Motovated Design Statement 6334-2001 dated 8 December 2021 issued by Jasin Long CPEng 1018331. Motovated PS1 - Design dated 8 December 2021 issued by Jasin Long CPEng 1018331. Safe Fill Level to be stated for each tank. Manufacturer to allocate a unique serial number for each tank built. Manufacturer to retain individual tank fabrication and test records. Recertification required following any change to the original design, duty, service conditions or referenced drawings. | 2046-12-10 | FAB0094 | N/A
TNK20119 | 2021-09-02 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: T#3206 HDPE 1900mm diameter x 1900 high x 24/12mm wall thickness single walled Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 5,000 litres Compartments: 1 | Name: Caustic soda 50% w/w aqueous solution Class(es): 6.1D, 8.1A, 8.2B, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2026-09-02
TNK20120 | 2021-09-02 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: #3212: HDPE single skinned 2300mm diameter x 1900mm high x 24/12mm wall thickness Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 7,000 litres Compartments: 1 | Name: Sodium hypochlorite 30% w/w aqueous solution Class(es): 8.2C, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2026-09-02
TNK20121 | 2021-02-03 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: #3132: HDPE 1900mm diameter x 3387mm high, double contained 12mm WT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 7,500 litres Compartments: 1 | Name: Acetic acid 50% w/w Class(es): 6.1D, 6.9B, 8.1A, 8.2C, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2026-02-03
TNK20122 | 2021-08-09 | Mech Eng Limited |  | AS 2634: 1983 | Description: #3145: GRP/PVC 2700mm diameter x 3860mm high, 27/12 mm WT Design Specification: AS 2634 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 15,000 litres Compartments: 1 | Name: Sulphuric acid 98% Class(es): 6.1B, 6.7A, 8.1A, 8.2B, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2026-08-09
TNK20123 | 2021-06-04 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: #3173: HDPE 1900mm diameter x 1900mm high, single skinned 24/12mm WT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 5,000 litres Compartments: 1 | Name: Sodium hydroxide aqueous solution 50%w/w Class(es): 6.1D, 8.1A, 8.2B, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2026-06-04
TNK20124 | 2021-05-11 | TRL Engineering Pty Ltd |  | UL 1316: 1994 | Description: Z-100403-1 (Z Newton) Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Name of Designer: TRL Engineering Pty Ltd Capacity: 20,000 litres | Name: Diesel UN1202 and Petrol UN1203 Class(es): 3.1D and 3.1A | Z Energy Limited 175 Roydvale Avenue, Burnside, Christchurch, 8053 | Field constructed tank Construction verified Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) Double skin GRP, Continuous interstitial monitoring | 2026-05-11
TNK20125 | 2021-11-22 | TRL Engineering Pty Ltd |  | UL 1316: 1994 | Description: Z-103705-T1 - Z Te Rapa, Pukete Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Name of Designer: TRL Engineering Pty Ltd Capacity: 30,000 litres Safe Fill Level: 28,500 litres | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z Energy Limited 175 Roydvale Avenue, Burnside, Christchurch, 8053 | Field constructed tank Construction verified Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) Double skin GRP, Continuous interstitial monitoring | 2026-11-22
TNK20126 | 2021-11-22 | TRL Engineering Pty Ltd |  | UL 1316: 1994 | Description: Z-103705-T2 - Z Te Rapa, Pukete Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Name of Designer: TRL Engineering Pty Ltd Capacity: 50,000 litres Safe Fill Level: 49,000 litres | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z Energy Limited 175 Roydvale Avenue, Burnside, Christchurch, 8053 | Field constructed tank Construction verified Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) Double skin GRP, Continuous interstitial monitoring | 2026-11-22
TNK20127 | 2021-11-22 | TRL Engineering Pty Ltd |  | UL 1316: 1994 | Description: Z-103705-T3 - Z Te Rapa, Pukete Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Name of Designer: TRL Engineering Pty Ltd Capacity: 40,000 litres Safe Fill Level: 36,500 litres | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z Energy Limited 175 Roydvale Avenue, Burnside, Christchurch, 8053 | Field constructed tank Construction verified Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) Double skin GRP, Continuous interstitial monitoring | 2026-11-22
TNK20128 | 2021-03-11 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: #3175: HDPE 3500mm diameter x 3871mm high, double contained 50mm WT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 30,000 litres | Name: Poly Aluminium Chloride (PAC) aqueous solution Class(es): 6.1D | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2026-03-11
TNK20129 | 2021-05-20 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: #3198: HDPE 1800mm diameter x 2371mm high, single skinned 36/12mm WT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 5,000 litres Compartments: 1 | Name: Sodium hydroxide aqueous solution 50%w/w Class(es): 6.1D, 8.1A, 8.2B, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2026-05-20
TNK20130 | 2021-03-24 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: #3174: HDPE 3500mm diameter x 3871mm high, double contained 50mm WT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 30,000 litres Compartments: 1 | Name: Sodium hydroxide aqueous solution 30%w/w Class(es): 6.1D, 8.1A, 8.2B, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2026-03-24
TNK20131 | 2021-11-02 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: #3220 1390mmD x 1480mmH x 10/12/15mmWT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 1,500 litres Compartments: 1 | Name: Sodium bisulphite aqueous solution Class(es): 8.2C, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2026-11-02
TNK20132 | 2021-11-02 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: T#3224 2038mmD x 3087mmH x 12mmWT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 7,600 litres Compartments: 1 | Name: Poly Aluminium Chloride (PAC) aqueous solution Class(es): 6.1D | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2026-11-02
TNK20133 | 2021-11-02 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: T#3225 2038mmD x 3087mmH x 12mmWT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 7,600 litres Compartments: 1 | Name: Poly Aluminium Chloride (PAC) aqueous solution Class(es): 6.1D | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2026-11-02
TNK20134 | 2021-09-21 | Mech Eng Limited |  | AS 2634: 1983 | Description: #3205 GRP/PVC 1800mm diameter x 2550mm high, 10mm WT Design Specification: AS 2634 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 5,000 litres Compartments: 1 | Name: Sulphuric acid 98% Class(es): 6.1B, 6.7A, 8.1A, 8.2B, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction Secondary containment integral with tank assembly | 2026-09-21
TNK20135 | 2021-11-02 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: #3219 1390mmD x 1480mmH x 10/12/15mmWT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 1,500 litres Compartments: 1 | Name: Citric acid aqueous solution Class(es): 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2026-11-02
TNK20136 | 2021-11-02 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: T#3223 2038mmD x 2062mmH x 12/15/25mmWT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 4,400 litres Compartments: 1 | Name: Caustic soda 50% w/w aqueous solution Class(es): 6.1A, 6.1D, 6.7A, 8.1A, 8.2B, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2026-11-02
TNK20137 | 2021-11-02 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: T#3222 2038mmD x 2062mmH x 12/15/25mmWT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 4,400 litres Compartments: 1 | Name: Caustic soda 50% w/w aqueous solution Class(es): 6.1B, 6.1D, 6.7A, 8.1A, 8.2B, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2026-11-02
TNK20138 | 2021-11-02 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: T#3221 2038mmD x 2217mmH x 12/15/25mmWT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 5,000 litres Compartments: 1 | Name: Hydrofluorosilic acid Class(es): 6.1D, 8.1A, 8.2C, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2026-11-02
TNK20139 | 2022-06-30 | 2E Consulting |  | AS1692:2006 | Description: 13,000 L duplex 2205 / 316L stainless steel food grade mix tank. Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: 2E Consulting. Capacity: 13,000 L Compartments: 1 | Name: Calcium chloride, Citric acid, Sodium bisulphate Activate 1500, Caustic Pearl, Potassium hydroxide. Class(es): 6.1A, 6.1C, 8.1A, 8.2B, 8.2C, 8.3A | CONTRACT MECHANICAL SERVICES LIMITED 11 Harvard Way, Mt Maunganui | Tank design verified to AS1692:2006 reconfirmed 2016. Tank serial number 204. Contract Mechanical Services QA pack June 2022 ; Rev 1. Manufacturers tank number 33-01-005001. 13 kL Duplex 2205/316L stainless steel food grade mix tank to AS1692 Category 5. Design temperature 95 deg C. 3.006m OD x 2m strake x 3mm duplex 2250 stainless steel. Top cone 0.443m high by 15 degree pitch. Bottom cone 0.444m high by 15 degree pitch. Safe fill height 2.23m from bottom of base cone. High level alarm 2.47m from bottom of base cone. Design life 50 years. Joint efficiency 0.7. Corrosion allowance 0. Loacation IXOM, Morrinsville. Seismic design to 1170.5 / NZSEE:2009. Wind design not applicable, vessel stored indoors. Seismic zone 0.18 Maximum specific gravity of product 1.6. Sp = 1.0 Site subsoil Class D. Tank design pressure 4.5 kPa. Design Vacuum -2.0 kPa. Venting to API2000 / AS1940. Maximum fill rate 8333.3 L/min. Maximum pump out rate 585 L/min. Tank anchoring by 24 number 20mm hold down bolts. 4 bolts on PCD 280mm per each of the 6 leg supports. | 2027-06-30
TNK20141 | 2022-11-28 | 2E Consulting |  | AS1692:2006 | Description: 8,300 L 316L grade stainless steel acid tank Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: 2E Consulting. Capacity: 8,300 L Compartments: 1 | Name: 98% sulphuric acid UN 1830, Approval No. HSR001572. Class(es): 6.1D, 8.1A, 8.2B, 8.3A | CONTRACT MECHANICAL SERVICES LIMITED 11 Harvard Way, Mt Maunganui | Tank serial number CMS205. Fonterra tank reference number W49. 8.3 kL 316L grade stainless steel sulphuric acid tank to AS1692 Cat 5. QA Pack Nov 2022 Whareroa Cogen Demin 98% sulphuric acid. Hydro test date 25 Oct 2022. Hydro test pressure 53.96 kPa. (2 m riser pipe from top flange on cone roof). Design temperature 95 deg c. 1.9m OD x 3m strake x 6mm 316 L grade. Cone top 183.3 mm high x 10 degree pitch. Cone bottom 374.8 mm high x 20 degree pitch. Total height of tank shell 3.558 m. Safe fill height from bottom of base cone 2.974 m. High level alarm from bottom of base cone 3.018 m. Design life 50 years. Joint efficiency 0.7 (No radiography). Corrosion allowance 1 mm. Location Fonterra, Whaeroa, Hawera. Seismic design to 1170.5 / NZSEE : 2009. Wind design to 1170.2. Design wind speed 215 km/hr. Seismic zone 0.18. Maximum specific gravity 1.85. Sp = 1.0 Site subsoil Class D. Tank design pressure 1 kPa. Design vacuum -0.25 kPa. Venting to API 2000 / AS 1940. Maximum fill rate 30,000 L/hr. Maximum pump out rate 800 L/hr. Tank anchorage by 24 number 20 mm hold down bolts. 4 bolts on PCD 270 mm per each of the 6 leg supports. | 2027-11-28
TNK20144 | 2022-01-26 | Edgar Vandendgen | Acme Engineering Limited PO Box 38 064, Wellington Mail Centre, Wellington, 5045 11-29 Hutt Road, Petone, Lower Hutt, 5012 FAB0060 | API Standard 650 | Description: Vertical cylindrical skid tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Edgar Vandendgen Capacity: 63,125 litres Maximum Safe Fill Level: 5.700m Compartments: 1 | Name: Crude oil or condensate Class(es): 3.1A, 3.1B | ACME ENGINEERING LIMITED PO Box 38 064, Wellington Mail Centre, 5045 11-29 Hutt Road, Petone, Wellington, 5012 | Refer producer Statement – 63m3 Skid Mounted Storage Tank Design, Ref.: ATM1221, Dated: 21 December 2021. Refer Design Calculations Document No.: DC-570, Issue: 1. Allocate a unique serial number for each tank produced and retain individual tank fabrication records. Recertification required following any change to the referenced drawings, change of duty or change of service. | 2037-01-26
TNK20145 | 2021-09-15 | TRL Engineering Pty Ltd |  | UL 1316: 1994 | Description: Z-102957-T1 (Z Oamaru) Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Name of Designer: TRL Engineering Pty Ltd Capacity: 40,000 litres Safe Fill Level: 37,000 litres | Name: Refined Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z Energy Limited 175 Roydvale Avenue, Burnside, Christchurch, 8053 | Field constructed tank Construction verified Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) Double skin GRP, Continuous interstitial monitoring | 2026-09-15
TNK20146 | 2021-09-15 | TRL Engineering Pty Ltd |  | UL 1316: 1994 | Description: Z-102957-T2 (Z Oamaru) Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Name of Designer: TRL Engineering Pty Ltd Capacity: 40,000 litres Safe Fill Level: 37,000 litres | Name: Refined Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z Energy Limited 175 Roydvale Avenue, Burnside, Christchurch, 8053 | Field constructed tank Construction verified Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) Double skin GRP, Continuous interstitial monitoring | 2026-09-15
TNK20147 | 2021-09-15 | TRL Engineering Pty Ltd |  | UL 1316: 1994 | Description: Z-102957-T3 (Z Oamaru) Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Name of Designer: TRL Engineering Pty Ltd Capacity: 40,000 litres Safe Fill Level: 37,000 litres | Name: Refined Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z Energy Limited 175 Roydvale Avenue, Burnside, Christchurch, 8053 | Field constructed tank Construction verified Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) Double skin GRP, Continuous interstitial monitoring | 2026-09-15
TNK20148 | 2021-02-11 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: #3188: HDPE 2100mm diameter x 2500mm high, single skin 12mm WT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Safe Fill Level: 7,000 litres Compartments: 1 | Name: Aluminium chlorohydrate aqueous solution 1.3sg max Class(es): 6.1D, 8.1A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction Seismic Design meets NZS1170-IL3 | 2025-02-11
TNK20149 | 2021-02-11 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: #3189: HDPE 2100mm diameter x 2500mm high, single skin 12mm WT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Safe Fill Level: 7,000 litres Compartments: 1 | Name: Sodium hydroxide aqueous solution 30%w/w Class(es): 6.1D, 8.1A, 8.2B, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction Seismic Design meets NZS1170-IL3 | 2024-02-11
TNK20150 | 2022-01-11 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: #3217 2900mm D x 3781mm H x 27/15mm WT HDPE Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 20,000 litres Compartments: 1 | Name: "Anti-blu" (HSR 000870/000871) Class(es): 6.1D, 6.5A, 6.5B, 6.6A, 6.7B, 6.8A, 6.9A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2027-01-11
TNK20151 | 2022-01-31 | Mercer Stainless Limited - J. Camp | Mercer Stainless Limited 53 Lunns Road, Middleton Christchurch 8024. FAB0077 | AS 1692:2006, Category 5 | Description: 4,095 litres single skin above ground vertical cylindrical stationary tank Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Mercer Stainless Limited - J. Camp Capacity: 4,095 Litres Compartments: 1 Maximum Safe Fill Level: 50mm below top barrel ring seam | Gasoline fuel additive having hazard classifications of 3.1C, 6.1E, 6.3A, 6.5B, 9.1B, 9.1D | Mercer Stainless Limited PO Box 6020, Christchurch, 8442 53 Lunns Road, Middleton, Christchurch, 8024 | Producer Statement - PS1 - Design: Issued By: Calibre Consulting Ltd, To: Z Energy Ltd / Mercer Stainless, To be supplied to: Christchurch City Council, In Respect of: 4000 litre HSNO Additive tank (excludes foundation), At: 51 Godley Quay, Lyttelton, General Arrangement 4000L Lyttelton Additive Tank 21452 Rev F, Signed By: Bevan White (CPEng # 108276), Dated: 21/01/2022. Calibre Consulting Ltd – Calculations: 712535.006, Rev 0, 4000L SS Additive tank Strl Calcs, Dated: 21/12/2021, Reviewer: Bevan White. This approval becomes invalid following any change to the referenced contents, designs, duty service, drawings or applicable standards. | 2032-01-31 | FAB0077
TNK20152 | 2022-03-11 | Hendl & Murray Engineering Limited - Deon den Otter | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | API650, 13th Edition, Addendum 2020, Annex A & S. | Description: Vertical cylindrical storage tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Deon den Otter Capacity: 72,700 Litres Compartments: 1 Maximum Safe Fill Level: 69,535 Litres. | Name: Pinechem 700 Class(es): 3.1C | Hendl & Murray Engineering Ltd PO Box 5492, Frankton, Hamilton, 3242 103 Tawa Street, Melville, Hamilton, 3206 | Refer Tom Roberts CPEng 1024350 - PS1 - Design Statement - 212001, dated 20/12/2021. Refer Tom Roberts, CPEng 1024350, Design Report No. 212001 RP01, Rev B, dated 22/11/2021 This approval becomes invalid following any change to the referenced contents, designs, duty service, drawings or applicable standards. | 2052-03-10 | FAB0033
TNK20153 | 2022-03-11 | Hendl & Murray Engineering Limited - Deon den Otter | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | API650, 13th Edition, Addendum 2020, Annex A & S. | Description: Vertical cylindrical storage tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Deon den Otter Capacity: 72,700 litres Compartments: 1 Maximum Safe Fill Level: 69,535 Litres | Name: Pinechem 500 Class(es): 3.1C | Hendl & Murray Engineering Ltd PO Box 5492, Frankton, Hamilton, 3242 103 Tawa Street, Melville, Hamilton, 3206 | Refer Tom Roberts CPEng 1024350 - PS1 - Design Statement - 212001, dated 20/12/2021. Refer Tom Roberts, CPEng 1024350, Design Report No. 212001 RP01, Rev B, dated 22/11/2021 This approval becomes invalid following any change to the referenced contents, designs, duty service, drawings or applicable standards. | 2052-03-10 | FAB0033
TNK20154 | 2022-03-11 | Hendl & Murray Engineering Limited - Deon den Otter | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | API650, 13th Edition, Addendum 2020, Annex A & S. | Description: Vertical cylindrical storage tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Deon den Otter Capacity: 72,700 Litres Compartments: 1 Maximum Safe Fill Level: 69,535 Litres | Name: Pinechem 500 Pinechem 600 Class(es): 3.1C and 3.1C, 6.5B | Hendl & Murray Engineering Ltd PO Box 5492, Frankton, Hamilton, 3242 103 Tawa Street, Melville, Hamilton, 3206 | Refer Tom Roberts CPEng 1024350 - PS1 - Design Statement - 212001, dated 20/12/2021. Refer Tom Roberts, CPEng 1024350, Design Report No. 212001 RP01, Rev B, dated 22/11/2021 This approval becomes invalid following any change to the referenced contents, designs, duty service, drawings or applicable standards. | 2052-03-10 | FAB0033
TNK20155 | 2022-03-08 | Hendl & Murray Engineering Limited - Deon den Otter | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | API650, 13th Edition, Addendum 2020, Annex A & S. | Description: Vertical cylindrical storage tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Deon den Otter Capacity: 72,700 Litres Compartments: 1 Maximum Safe Fill Level: 69,535 Litres. | Name: Pinechem 500 Pinechem 600 Class(es): 3.1C and 3.1C, 6.5B | Hendl & Murray Engineering Ltd PO Box 5492, Frankton, Hamilton, 3242 103 Tawa Street, Melville, Hamilton, 3206 | Refer Tom Roberts CPEng 1024350 - PS1 - Design Statement - 212001, dated 20/12/2021. Refer Tom Roberts, CPEng 1024350, Design Report No. 212001 RP01, Rev B, dated 22/11/2021 This approval becomes invalid following any change to the referenced contents, designs, duty service, drawings or applicable standards. | 2052-03-08 | FAB0033
TNK20156 | 2022-05-04 | Hendl & Murray Engineering Limited - Deon den Otter | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | AS 1692:2006, Category 5 | Description: 7,700 Litres single skin above ground, vertical, cylindrical insulated process container Design Specification: AS1692: 2006 Tank Type: Process Container Name of Designer: Hendl & Murray Engineering Limited - Deon den Otter Capacity: 7,700 Litres Compartments: 1 Maximum Safe Fill Level: 2,050mm (6,000 Litres) | Caustic (sodium hydroxide) up to 5% concentration having a hazard classification of 6.1E, 8.1A, 8.2C, 8.3A or nitric acid up to 10% concentration having a hazard classification of 6.1E, 6.9B, 8.1A, 8.2C, 8.3A | Hendl & Murray Engineering Ltd PO Box 5492, Frankton, Hamilton, 3242 103 Tawa Street, Melville, Hamilton, 3206 | Design Report: By: Mech Eng, dated 27/01/2022, entitled 221051 RP01 RevA Simmonds Process 6000L CIP Balance Tank Design Report Producer Statement – PS1 – Design: PS1 documentation dated 08/03/2022, signed by CPEng 1024350. Design Actions: NZS 1170.5:2004, AS/NZS 1170.2:2011, NZSEE SDST:2009, Hold Down Bolts: EOTA TR 029:210, EOTA TR 045:2013, Supporting Structure: AS 3990:1993, Strake/Wall Design: NZSEE SDST:2009, Ventilation: API 2000 5th Edition, Design Standard: AS 1692:2006. If manufacturing of this tank is for a different site other than the one listed in the PS1 above a new producer statement (PS1) will need to be provided to confirm the compliance with the wind & seismic requirements in the Health and Safety at Work (Hazardous Substances) Regulations 2017, Clause 17.6(3). Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. This approval becomes invalid following any change to the referenced contents, designs, duty service, drawings or applicable standards. | 2032-05-04 | FAB0033
TNK20157 | 2022-02-08 | Zhangjiagang Superise Heavy Machine Co Ltd |  | AS 1692: 2006 Reduced Secondary Containment for Certain Above Ground Stationary Tanks Safe Work Instrument 2017 | Description: T38-FCT38202102/SPTU1034145, Category 3, 5992 mm L x 2374 mm W x 2690 mm H x 6 mm WT Design Specification: AS 1692:2006 SWI Reduced Secondary Containment for Tanks Tank Type: Above Ground Stationary Tank Name of Designer: Zhangjiagang Superise Heavy Machine Co Ltd Capacity: 35,380 L (Safe Fill Level) Compartments: 1 | Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. | Fuelchief Limited 5 Tanya Street, Bromley, Christchurch, 8062 | Construction Verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2027-02-08
TNK20158 | 2022-03-10 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: T#3234 HDPE Single skin vertical cylindrical; 2900mm D x 3373mm H x 24/12mm WT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 20,000 litres SFL Compartments: 1 | Name: Aluminium sulphate 28% aqueous soution Class(es): 6.1D, 8.1A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction Verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2027-03-09
TNK20159 | 2022-05-05 | Petro Industrial - JS | Zhangjiagang Fuel Equipment System Co. Ltd. 3 Haixin North Road, Nanfeng, Zhangjiagang, Jiangsu, China FAB0087 | AS 1692:2006, Category 3 | Description: 28,880 Litres Above Ground Double Skin Rectangular Stationary Tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 68041-ASM-001-E, Rev J, Pages 1 to 7 Name of Designer: Petro Industrial - JS Capacity: 28,880 Litres Compartments: 1 Maximum Safe Fill Level: 25,100 Litres | Name: Diesel Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | Petro Industrial Pty. Ltd. PO Box 407, Narangba, Queensland, Australia, 4504 Factory 2/106 Potassium Street, Narangba, Queensland, Australia, 4504 | Approved for supplying a burner or engine. Structural Engineering Certification to AS/NZS 1170.2, NZS 1170.5 & AS 1657: Austica Pty. Ltd. Rev C, Date 20/01/2022. Titled: Container Skid-2 Fuel Storage Tank and the Internal 100x100x5 SHS Bracing, signed by Peter Kairu. CPEng no.: 3473760 (Aus). Producer Statement – PS1 – Design: Issued by: Design Consulting Engineers & Inspection (DE International Ltd.), To: Petro Industrial, To be supplied to: All building consent authorities within NZ, In respect of: 40ft Generator base tank AT: as applicable , Signed by: Jhonnal L. Calleja CPEng # 263893 dated 19/07/21. PS1 documentation no. 28390, Issue: 1 Date 18/01/2022. QA documentation from Zhangjiagang Fuel Equipment System Co. Ltd. – PIEPO37354 40ft, Date: 2021.12.03. Allocate unique serial number for each tank and retain individual tank fabrication and test records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture / pressure test, AS 1692:2006 Category 3, test pressure in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. PS1 and structural assessment done on tank only. And this compliance certificate is only on the tank referenced. Verification of the whole system with the generator subject to installed stationary container system compliance certificate checks. Weld details and compliance with AS/NZS 1554 series is subject to QA inspection before installation. Tank venting arrangement subject to installed stationary container system compliance certificate checks for discharge point. Pressure test compliance is subject to QA inspection and testing before installation. Must not be installed in non-fire resistant construction - Installation location stipulated in clause 17.63 of Heath and Safety at Work (Hazardous Substances) Regulations 2017. The following clauses from the Heath and Safety at Work (Hazardous Substances) Regulations 2017, are requirements to be met on installation for this stationary tank supplying an engine (generator): 17.6 (2), 17.25, 17.27, Part 17 Subpart 11 -13, 17.75, 17.78 & 17.79. This approval becomes invalid following any change to the referenced contents, designs, duty service, drawings or applicable standards. | 2032-05-05 | FAB0087
TNK20160 | 2022-04-19 | Pandey |  | AS1692-2006 | Description: 316L SS Vertical Cone Roof Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Pandey Capacity: 16,308 L Operating capacity: 15,000 L Compartments: 1 | Name: Caustic Soda 50% Class(es): 6.1D, 8.1A, 8.2B, 8.3A | National Dairy Association Limited Private Bag 3018, Waikato Mail Centre, Hamilton, 3240 709 Te Rapa Road, Te Rapa, Hamilton, 3200 | Installation at Tauhara Geothermal Power Plant (Contact Energy) Broadlands Road East Taupo | 2047-04-19
TNK20161 | 2022-04-19 | Pandey |  | AS1692-2006 | Description: 316L SS Vertical Cone Roof Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Pandey Capacity: 2,830 L Operating capacity: 2,500 L Compartments: 1 | Name: Biocide Class(es): 6.1C, 6.5A, 6.5B, 6.9B, 8.2B, 8.3A | National Dairy Association Limited Private Bag 3018, Waikato Mail Centre, Hamilton, 3240 709 Te Rapa Road, Te Rapa, Hamilton, 3200 | Installation at Tauhara Geothermal Power Plant (Contact Energy) Broadlands Road East Taupo | 2047-04-19
TNK20162 | 2022-04-20 | Pandey |  | AS1692-2006 | Description: 316L SS Vertical Cone Roof Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Pandey Capacity: 2,830 L Operating capacity: 2,500 L Compartments: 1 | Name: Micro-Biocide Class(es): 6.1D, 8.2C, 8.3A | National Dairy Association Limited Private Bag 3018, Waikato Mail Centre, Hamilton, 3240 709 Te Rapa Road, Te Rapa, Hamilton, 3200 | Installation at Tauhara Geothermal Power Plant (Contact Energy) Broadlands Road East Taupo | 2047-04-20
TNK20163 | 2022-05-12 | Totara Engineering |  | AS1692: 2006 category 5 | Description: TK0110, Vertical Cylinder 316 Stainless Steel Design Specification: AS 1692 Tank Type: Process Container Name of Designer: Totara Engineering Capacity: 1,000 litres Safe fill level: 1498 mm | Name: Phosphoric acid (maximum 10% w/w) Classes: 6.1D, 8.1A, 8.2C, 8.3A Name: Sodium hydroxide aqueous solution (maximum 10% w/w) Classes: 6.1D, 8.1A, 8.2B, 8.3A | Protech Stainless Limited PO Box 10012, Te Rapa, Hamilton, 3241 40 Te Kowhai Road East, Burbush, Hamilton, 3288 | Construction verified. Satisfies Regulation part 17.91(2)(b)(ii) for Tank Construction | 2027-05-12
TNK20164 | 2022-05-12 | Totara Engineering |  | AS1692: 2006 category 5 | Description: TK0120, Vertical Cylinder 316 Stainless Steel Design Specification: AS 1692 Tank Type: Process Container Name of Designer: Totara Engineering Capacity: 1,000 litres Safe fill level: 1498 mm | Name: Phosphoric acid (maximum 10% w/w) Classes: 6.1D, 8.1A, 8.2C, 8.3A Name: Sodium hydroxide aqueous solution (maximum 10% w/w) Classes: 6.1D, 8.1A, 8.2B, 8.3A | Protech Stainless Limited PO Box 10012, Te Rapa, Hamilton, 3241 40 Te Kowhai Road East, Burbush, Hamilton, 3288 | Construction verified. Satisfies Regulation part 17.91(2)(b)(ii) for Tank Construction | 2027-05-12
TNK20165 | 2022-05-12 | Totara Engineering |  | AS1692: 2006 category 5 | Description: TK0130, Vertical Cylinder 316 Stainless Steel Design Specification: AS 1692 Tank Type: Process Container Name of Designer: Totara Engineering Capacity: 1,000 litres Safe fill level: 1498 mm | Name: Phosphoric acid (maximum 10% w/w) Classes: 6.1D, 8.1A, 8.2C, 8.3A Name: Sodium hydroxide aqueous solution (maximum 10% w/w) Classes: 6.1D, 8.1A, 8.2B, 8.3A | Protech Stainless Limited PO Box 10012, Te Rapa, Hamilton, 3241 40 Te Kowhai Road East, Burbush, Hamilton, 3288 | Construction verified. Satisfies Regulation part 17.91(2)(b)(ii) for Tank Construction | 2027-05-12
TNK20166 | 2022-05-12 | Totara Engineering |  | AS1692: 2006 category 5 | Description: TK0261, Vertical Cylinder 316 Stainless Steel Design Specification: AS 1692 Tank Type: Process Container Name of Designer: Totara Engineering Capacity: 4,000 litres Safe fill level: 4120 mm | Name: Phosphoric acid (maximum 10% w/w) Classes: 6.1D, 8.1A, 8.2C, 8.3A Name: Sodium hydroxide aqueous solution (maximum 10% w/w) Classes: 6.1D, 8.1A, 8.2B, 8.3A | Protech Stainless Limited PO Box 10012, Te Rapa, Hamilton, 3241 40 Te Kowhai Road East, Burbush, Hamilton, 3288 | Construction verified. Satisfies Regulation part 17.91(2)(b)(ii) for Tank Construction | 2027-05-12
TNK20167 | 2022-05-12 | Totara Engineering |  | AS1692: 2006 category 5 | Description: TK0267, Vertical Cylinder 316 Stainless Steel Design Specification: AS 1692 Tank Type: Process Container Name of Designer: Totara Engineering Capacity: 13,000 litres Safe fill level: 4120 mm | Name: Phosphoric acid (maximum 10% w/w) Classes: 6.1D, 8.1A, 8.2C, 8.3A Name: Sodium hydroxide aqueous solution (maximum 10% w/w) Classes: 6.1D, 8.1A, 8.2B, 8.3A | Protech Stainless Limited PO Box 10012, Te Rapa, Hamilton, 3241 40 Te Kowhai Road East, Burbush, Hamilton, 3288 | Construction verified. Satisfies Regulation part 17.91(2)(b)(ii) for Tank Construction | 2027-05-12
TNK20168 | 2022-07-06 | Fuel Storage Limited - Baz Burtt | FUEL STORAGE LIMITED PO Box 108, Te Awamutu, 3840 700 Bond Road, Te Awamutu, 3800 FAB0050 | AS 1692:2006 | Description: 490 litres above ground single skin octagonal stationary generator day tank Design Specification: AS1692: 2006 Tank Type: Service Tank Name of Designer: Fuel Storage Limited - Baz Burtt Capacity: 490 Litres Maximum Safe Fill Level: 465 litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | FUEL STORAGE LIMITED PO Box 108, Te Awamutu, 3840 700 Bond Road, Te Awamutu, 3800 | Approved For: The storage and transfer of diesel only, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved to supply an engine or burner. References: Compliant with AS 1692:2006, Category 3. 8818-1000, 490L Tank Design Statement – In accordance with AS 1692:2006, Load combinations: AS/NZS 1170.0:2002, Wind loading: AS/NZS 1170.2:2011 & Seismic loading: NZS 1170.5:2004, Joe Bain (CPEng 248672), Dated 03/03/2026. 6697-0001, 500L Tank Design Statement – In accordance with AS 1692:2006, Load combinations: AS/NZS 1170.0:2002, Wind loading: AS/NZS 1170.2:2011 & Seismic loading: NZS 1170.5:2004, seismic loading to NZSEE method, Joe Bain (CPEng 248672), Dated 6/7/2022. Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. QA inspection and documentation to be completed before installation of the tank/s. Must not be installed in non-fire resistant construction - Installation location stipulated in clause 17.63 of Heath and Safety at Work (Hazardous Substances) Regulations 2017. The following clauses from the Heath and Safety at Work (Hazardous Substances) Regulations 2017, are requirements to be met on installation for this stationary tank supplying an engine (generator): 17.6 (2), 17.25, 17.27, Part 17 Subpart 3, 11-13, 17.75, 17.78, 17.79, 17.80 & 17.81. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced Fuel Storage Limited drawings or applicable standards. | 2036-03-05 | FAB0050
TNK20169 | 2022-07-16 | NDA Engineering Trading as TIRA |  | AS1692: 2006 category 5 | Description: 304 S/S Vertical Cone Roof Cone bottom on skirt AS1692-Cat 5 Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: NDA Engineering Trading as TIRA Capacity: 20,000 Litres Compartments: 1 | Name: 2.5-5% Caustic Soda Class(es): 8.1A, 8.2C, 8.3A | NDA ENGINEERING LIMITED Private Bag 3018, Waikato Mail Centre, Te Rapa, Hamilton, 3240709 Te Rapa Road, Te Rapa, Hamilton, 3200 | NDA registered Tank design 22/6711406-01. This tank is for the OLAM Dairy Factory under construction in Tokoroa. OLAM designated Tank Number Q1TK0941 at 29 Bridge Street, Tokoroa 3420. | 2047-07-16 | N/A
TNK20170 | 2022-07-16 | NDA Engineering Trading as TIRA |  | AS1692: 2006 category 5 | Description: 304 S/S Vertical Insulated Cone Roof Cone bottom on skirt AS1692-Cat 5 Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: NDA Engineering Trading as TIRA Capacity: 20,000 Litres Compartments: 1 | Name: 10% Nitric Acid Class(es): 6.9B, 8.1A, 8.2C, 8.3A | NDA ENGINEERING LIMITED Private Bag 3018, Waikato Mail Centre, Te Rapa, Hamilton, 3240709 Te Rapa Road, Te Rapa, Hamilton, 3200 | NDA registered Tank design 22/6711403-01. This tank is for the OLAM Dairy Factory under construction in Tokoroa. OLAM designated Tank Number Q1TK0741 at 29 Bridge Street, Tokoroa 3420. | 2047-07-16 | N/A
TNK20171 | 2022-07-16 | NDA Engineering Trading as TIRA |  | AS1692: 2006 category 5 | Description: 304 S/S Vertical Insulated Cone Roof Cone bottom on skirt AS1692-Cat 5 Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: NDA Engineering Trading as TIRA Capacity: 20,000 Litres Compartments: 1 | Name: <5% Caustic Soda Class(es): 8.1A, 8.2C, 8.3A | NDA ENGINEERING LIMITED Private Bag 3018, Waikato Mail Centre, Te Rapa, Hamilton, 3240709 Te Rapa Road, Te Rapa, Hamilton, 3200 | NDA registered Tank design 22/6711405-01. This tank is for the OLAM Dairy Factory under construction in Tokoroa. OLAM designated Tank Number Q1TK0641 at 29 Bridge Street, Tokoroa 3420. | 2047-07-16 | N/A
TNK20172 | 2022-07-21 | Etech Engineering Services Ltd |  | API650, 13th Edition, Addendum 2020, Annex A & S. | Description: 304 S/S Vertical cone roof API650 App J & S, AS1692:2006 .Cat 5 Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Etech Engineering Services Ltd Capacity: 82,380 litres Compartments: 1 | Name: Monomer 2 Ethyl Hexyl Acrylate Class(es): 3.1D, 6.5B | ALLNEX NEW ZEALAND LIMITED PO Box 12841, Penrose, Auckland, 1642 715 Great South Road, Penrose, Auckland, 1061 | Tank installation at Allnex Industries 715 Great South Road, Penrose Auckland. | 2072-07-21
TNK20173 | 2022-08-04 | Fuel Storage Limited - Baz Burtt | FUEL STORAGE LIMITED PO Box 108, Te Awamutu, 3840 700 Bond Road, Te Awamutu, 3800 FAB0050 | AS 1692:2006, Category 3 | Description: 20,000 Litres above ground double skinned rectangular stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Fuel Storage Limited - Baz Burtt Capacity: 19,707 Litres Maximum Safe Fill Level: 18,639 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | FUEL STORAGE LIMITED PO Box 108, Te Awamutu, 3840 700 Bond Road, Te Awamutu, 3800 | 6643-1005, 20kL Tank Design Statement, Rev 00 Released, 02Aug22: – In accordance with AS 1692:2006, Load combinations: AS/NZS 1170.0:2002, Wind loading: AS/NZS 1170.2:2011 & Seismic loading: NZS 1170.5:2004, seismic loading to NZSEE method, Joe Bain (CPEng 248672), Dated 2/8/22. Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. QA inspection and documentation to be completed before installation of the tank/s. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced Fuel Storage Limited drawings or applicable standards. Brass Vent DataSheet_190_2021_rev4_eng 6643-1005, 20kL Tank Design Statement, Rev 00 Released, 02Aug22 6643-1002, 20,000L Tank Calculations, Rev 00, Draft 02, 01Aug22 6643-0002, AS 1692 Compliance Checklist (20kL) 6644-1000, Tank Volume Check | 2032-08-04 | FAB0050
TNK20174 | 2024-09-24 | Fuel Storage Limited - Baz Burtt | FUEL STORAGE LIMITED PO Box 108, Te Awamutu, 3840 700 Bond Road, Te Awamutu, 3800 FAB0050 | AS 1692:2006, Category 3 | Description: 1,800 Litres above ground double skinned rectangular stationary tank with and without cabinet Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Fuel Storage Limited - Baz Burtt Capacity: 1,815 Litres Maximum Safe Fill Level: 1,724 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B Name: Low Flash Diesel Class(es): 3.1C, 6.1E, 6.3B, 6.7B, 9.1B | FUEL STORAGE LIMITED PO Box 108, Te Awamutu, 3840 700 Bond Road, Te Awamutu, 3800 | Compliant with AS 1692:2006, Category 3. 8122-1001, 1.8kL Tank Design Statement, Rev 00, Released, 23Sep24: – In accordance with AS 1692:2006, Load combinations: AS/NZS 1170.0:2002,Wind loading: AS/NZS 1170.2:2011 & Seismic loading: NZS 1170.5:2004, seismic loading to NZSEE method, Joe Bain (CPEng 248672), Dated22/9/2024. Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. QA inspection and documentation to be completed before installation of the tank/s. Must not be installed in non-fire resistant construction - Installation location stipulated in clause 17.63 of Heath and Safety at Work (HazardousSubstances) Regulations 2017. The following clauses from the Heath and Safety at Work (Hazardous Substances) Regulations 2017, are requirements to be met on installation for this stationary tank supplying an engine (generator): 17.6 (2), 17.25, 17.27, Part 17 Subpart 3, 11-13, 17.75, 17.78, 17.79, 17.80 & 17.81. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced Fuel Storage Limited drawings or applicable standards. | 2035-11-21 | FAB0050 Design updated 24/09/2024 Design updated 21/11/2025
TNK20175 | 2024-09-24 | Fuel Storage Limited - Baz Burtt | FUEL STORAGE LIMITED PO Box 108, Te Awamutu, 3840 700 Bond Road, Te Awamutu, 3800 FAB0050 | AS 1692:2006, Category 3 | Description: 3,000 Litres above ground double skinned rectangular stationary tank with and without cabinet Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Fuel Storage Limited - Baz Burtt Capacity: 3,095 Litres Maximum Safe Fill Level: 2,943 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B Name: Low Flash Diesel Class(es): 3.1C, 6.1E, 6.3B, 6.7B, 9.1B | FUEL STORAGE LIMITED PO Box 108, Te Awamutu, 3840 700 Bond Road, Te Awamutu, 3800 | Compliant with AS 1692:2006, Category 3. 8122-1002, 3kL Tank Design Statement, Rev 00, Released, 23Sep24: – In accordance with AS 1692:2006, Load combinations: AS/NZS 1170.0:2002,Wind loading: AS/NZS 1170.2:2011 & Seismic loading: NZS 1170.5:2004, seismic loading to NZSEE method, Joe Bain (CPEng 248672), Dated22/9/2024. Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture, pressure testin kPa and safe fi ll level. All other markings to comply with the Hazardous Substances Regulations. QA inspection and documentation to be completed before installation of the tank/s. Must not be installed in non-fire resistant construction - Installation location stipulated in clause 17.63 of Heath and Safety at Work (HazardousSubstances) Regulations 2017. The following clauses from the Heath and Safety at Work (Hazardous Substances) Regulations 2017, are requirements to be met on installation forthis stationary tank supplying an engine (generator): 17.6 (2), 17.25, 17.27, Part 17 Subpart 3, 11-13, 17.75, 17.78, 17.79, 17.80 & 17.81. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced Fuel Storage Limited drawings or applicable standards. | 2035-11-21 | FAB0050 Design updated 24/09/2024 Design updated 21/11/2025
TNK20176 | 2022-07-19 | Mech Eng Limited |  | AS 2634-1983 | Description: #3240 FRP Vertical cylinder: 3215mm H x 2500mm DIA x 12mm WT Design Specification: AS 2634 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 15,000 litres Compartments: 1 | Name: Sulphuric acid 98% Class(es): 6.1B, 6.7A, 8.1A, 8.2B, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction Verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2027-07-19
TNK20177 | 2022-07-19 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: #3250 HDPE Secondary Contained 2743mm H x 2600mm DIA x 15/30mm WT Vertical cylinder Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 10,000 litres Compartments: 1 | Name: Hydrofluorosilicic Acid 1.22sg Class(es): 8.2C, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction Verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction Secondary Containment greater than 110% | 2027-07-19
TNK20178 | 2022-07-19 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: #3251 HDPE Secondary Contained Vertical cylinder, 3067mm H x 3000mm DIA x 20mmWT Design Specification: BS EN 12573 Thermoplastic Stationary Tanks Safe Work Instrument 2017 Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 15,000 litres Compartments: 1 | Name: Hydrofluorosilicic Acid 1.22sg Class(es): 8.2C, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction Verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction Secondary Containment greater than 110% | 2027-07-19
TNK20179 | 2022-07-21 | Carlyon Civil Construction Limited | Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | UL 142:2006 | Description: FHBITU30KL -5900mm LOA x 2750mm DIA horizontal cylinder single skin Design Specification: UL 142 Tank Type: Above Ground Stationary Tank Name of Designer: Carlyon Civil Construction Capacity: 30,000 L Compartments: 1 | Name: Bitumen, Cut-Back Bitumen Class(es): 3.1B, 3.1C, 3.1D | Carlyon Civil Construction Limited PO Box 10092, Te Rapa, Hamilton, 3241 3 Ellis Street, Frankton, Hamilton, 3204 |  | 2027-07-21 | FAB0083
TNK20180 | 2022-07-21 | Carlyon Civil Construction Limited | Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | UL 142:2006 | Description: FHBITU50KL -9300mm LOA x 2800mm DIA horizontal cylinder single skin Design Specification: UL 142 Tank Type: Above Ground Stationary Tank Name of Designer: Carlyon Civil Construction Capacity: 50,000 L Compartments: 1 | Name: Bitumen, Cut-Back Bitumen Class(es): 3.1B, 3.1C, 3.1D | Carlyon Civil Construction Limited PO Box 10092, Te Rapa, Hamilton, 3241 3 Ellis Street, Frankton, Hamilton, 3204 |  | 2027-07-21 | FAB0083
TNK20181 | 2022-07-21 | Carlyon Civil Construction Limited | Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | UL 142:2006 | Description: FHBITU80KL -14400mm LOA x 2800mm DIA horizontal cylinder single skin Design Specification: UL 142 Tank Type: Above Ground Stationary Tank Name of Designer: Carlyon Civil Construction Capacity: 80,000 L Compartments: 1 | Name: Bitumen, Cut-Back Bitumen Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Carlyon Civil Construction Limited PO Box 10092, Te Rapa, Hamilton, 3241 3 Ellis Street, Frankton, Hamilton, 3204 |  | 2027-07-21 | FAB0083
TNK20182 | 2022-07-27 | Maskell/Tank Reline NZ Limited |  | UL 1316:1994 | Description: KAP912: FRP Single skin 9000mm LOA x 2500mm DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Name of Designer: Maskell/Tank Reline NZ Limited Capacity: 40,000 L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Mobil Oil New Zealand Limited PO Box 1709, Shortland Street, Auckland, 1140 22 Amohia Street, Paraparaumu, 5032 |  | 2027-07-27
TNK20183 | 2022-07-27 | Maskell/Tank Reline NZ Limited |  | UL 1316:1994 | Description: KAP983: FRP Single skin 9000mm LOA x 2500mm DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Name of Designer: Maskell/Tank Reline NZ Limited Capacity: 40,000 L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Mobil Oil New Zealand Limited PO Box 1709, Shortland Street, Auckland, 1140 22 Amohia Street, Paraparaumu, 5032 |  | 2027-07-27
TNK20184 | 2022-07-27 | Maskell/Tank Reline NZ Limited |  | UL 1316:1994 | Description: KAPD4: FRP Single skin 9000mm LOA x 2500mm DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Name of Designer: Maskell/Tank Reline NZ Limited Capacity: 40,000 L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Mobil Oil New Zealand Limited PO Box 1709, Shortland Street, Auckland, 1140 22 Amohia Street, Paraparaumu, 5032 |  | 2027-07-27
TNK20185 | 2022-04-20 | Mech Eng Limited |  | BS EN 12573: 2000 Thermoplastic Stationary Tanks Safe Work Instrument 2017 | Description: #3216 1800mm D x 2614mm H x 12mm WT HDPE Design Specification: BS EN 12573 SWI Thermoplasic Tanks Tank Type: Above Ground Stationary Tank Name of Designer: Mech Eng Limited Capacity: 5000 litres Compartments: 1 | Name: Hydrofluorosilicic Acid 1.22sg Classes: 6.1A, 8.1A, 8.2C, 8.3A | Plastics Constructions Ltd 26 Fremlin Place, Avondale Auckland | Construction Verified Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2027-04-20
TNK20186 | 2022-08-11 | Stainless Engineering Co Ltd. |  | API Standard 650 | Description: T14164 - 316L Stainless Steel Vertical cylinder 1900mm DIA x 1400mm HOA x 3mm WT Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering 67-TK-11, Dwg: P894-001, ver 1 Name of Designer: Stainless Engineering Co. Ltd Capacity: 3200 Litres | Name: Hydrogen peroxide 50% w/w Class(es): 5.1.1B, 6.1C, 6.1D, 8.1A, 8.2C, 8.3A | STAINLESS ENGINEERING CO LIMITED 17 Neilpark Drive, East Tamaki, Auckland, 2013 |  | 2027-08-11
TNK20187 | 2022-08-16 | TRL Engineering Pty Ltd |  | UL 1316 | Description: Z-100307-T2 - Z Northcross Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-T2-104 Name of Designer: TRL Engineering Pty Ltd Capacity: 50,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 175 Roydvale Avenue, Burnside, Christchurch, 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2027-08-16
TNK20188 | 2022-08-15 | Mech Eng Limited |  | AS 2634 | Description: #3252 FRP Vertical cylinder Process Vessel 2050mm DIA x 2260mm HOA Design Specification: AS 2634 Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering TK-20-T3252, 5000 litre Chromate Tank Name of Designer: Mech Eng Limited Capacity: 5000 litres Compartments: 1 | Name: OKEMCOAT F1 (R) UN1755 Class(es): 5.1.1B, 6.1D, 6.5A, 6.6A, 6.7A, 6.8B, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland, 1026 | CONSTRUCTION VERIFIED Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2027-08-15
TNK20189 | 2022-09-02 | Mech Eng Limited |  | AS 2634 | Description: #3238 Primary Tank GRP Vertical cylinder 2200mm DIA x 3660mm HOA, Secondary Containment HDPE Design Specification: AS 2634 Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering 75-TK-61 shts 1, 2, & 3 of 3 Name of Designer: Mech Eng Limited Capacity: 12100 litres Compartments: 1 | Name: Sodium hypochlorite 10% w/w aqueous solution Class(es): 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland, 1026 | CONSTRUCTION VERIFIED Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2027-09-02
TNK20190 | 2022-09-02 | Mech Eng Limited |  | AS 2634 | Description: #3239 Primary Tank GRP Vertical cylinder 2200mm DIA x 3660mm HOA, Secondary Containment HDPE Design Specification: AS 2634 Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering 75-TK-62 shts 1 & 2, 75-TK-61 sht 3 of 3 Name of Designer: Mech Eng Limited Capacity: 12100 litres Compartments: 1 | Name: Sodium hypochlorite 10% w/w aqueous solution Class(es): 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland, 1026 | CONSTRUCTION VERIFIED Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2027-09-02
FAB0088 | 2023-09-08 |  | FIELDEN METALWORKS LIMITED 11-23 Columbia Avenue, Hornby South, Christchurch, 8042 11-23 Columbia Avenue, Hornby South, Christchurch, 8042 |  | Steel tanks in accordance with AS 1692-2006 Refer to individual TNK numbers: TNK20191 and TNK20192 | Class 3.1D hazardous substances | FIELDEN METALWORKS LIMITED 11-23 Columbia Avenue, Hornby South, Christchurch, 8042 11-23 Columbia Avenue, Hornby South, Christchurch, 8042 | Allocation of unique individual tank serial number to be stamped on each individual tank and recorded. Retention of individual tank fabrication, testing records and QA records for each tank. In addition to the conditions specified on Certificate 100241-6929-01, the following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the coompliance certifier who issued the certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2026-09-08 | Fabricator of: TNK20191 and TNK20192
TNK20191 | 2023-09-08 | Fielden Metalworks Limited | FIELDEN METALWORKS LIMITED 11-23 Columbia Avenue, Hornby South, Christchurch, 8042 11-23 Columbia Avenue, Hornby South, Christchurch, 8042 FAB0088 | AS1692: 2006 | Description: 477.36 Litres above ground single skin octagonal prismatic stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 480L Diesel Tank, drawn by JC, Rev F,Sheets 1 to 6, Date: 11/06/23 Name of Designer: Fielden Metalworks Limited - JC Capacity: 477.36 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | FIELDEN METALWORKS LIMITED 11-23 Columbia Avenue, Hornby South, Christchurch 8042 | The storage and transfer of Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved to supply an engine or burner and approved for residential and workplaces. If supplying an engine or burner approved for use with diesel only having a flash point greater than 60 degC but less than or equal to 93 deg C. Under the conditions of EPA - Hazardous Substances (Hazardous Property Controls) Notice 2017. Engineer’s report: 17112498_01. Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced Fielden Metalworks Limited drawings or applicable standard/s. | 2028-09-08 | FAB0088
TNK20192 | 8/0/2023 | Fielden Metalworks Limited | FIELDEN METALWORKS LIMITED 11-23 Columbia Avenue, Hornby South, Christchurch, 8042 11-23 Columbia Avenue, Hornby South, Christchurch, 8042 FAB0088 | AS1692: 2006 | Description: 998.69 Litres above ground single skin octagonal prismatic stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 980L Diesel Tank, drawn by JC, Rev E, Sheets 1 to 7, Date: 11/06/23 Name of Designer: Fielden Metalworks Limited - JC Capacity: 998.69 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | FIELDEN METALWORKS LIMITED 11-23 Columbia Avenue, Hornby South, Christchurch 8042 | The storage and transfer of Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved to supply an engine or burner and approved for residential and workplaces. If supplying an engine or burner approved for use with diesel only having a flash point greater than 60 degC but less than or equal to 93 deg C. Under the conditions of EPA - Hazardous Substances (Hazardous Property Controls) Notice 2017. Engineer’s report: 17112498_02. Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced Fielden Metalworks Limited drawings or applicable standard/s. | 2028-09-08 | FAB0088
TNK20193 | 2022-09-23 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplasic Tanks | Description: #3247 HDPE Vertical cylinder fixed cone roof, single skin, 2900mm DIA x 2954mm HOA x 25mm WT Design Specification: BS EN 12573 SWI Thermoplasic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Chemfeed 401957/01/01 rev-G Name of Designer: Mech Eng Limited Capacity: 15000 litres Compartments: 1 | Name: Poly Aluminium Chloride (PAC) aqueous solution 1.2sg Class(es): 6.1D, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place Avondale Auckland 1026 | CONSTRUCTION VERIFIED Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2027-09-23 | N/A
TNK20194 | 2022-09-22 | John Ho Etech Engineering Services | ETECH NZ LIMITED 130 Kaimanawa Street, Kelvin Grove, Palmerston North 4414 FAB0095 | BS EN 12285-1:2005 | Description: UST Double Skin ASTM SA240 304SS Design Specification: BS EN 12285:1 Tank Type: Below Ground Stationary Name of Designer: John Ho Etech Engineering Services Capacity: 50,273 litres Compartments: 1 | Name: Butyl Acrylate Class(es): 3.1C, 6.1C, 6.5B, 6.9B | ETECH ENGINEERING SERVICES LIMITED Unit 31 1st Floor 2 Bishop Dunn Place Flat Bush Auckland 2013 | Tank is destined for Allnex New Zealand, 14 Industry Road, Penrose, Auckland. 1061 | 2023-08-12 | FAB0095 (12/08/2023)
TNK20195 | 2022-09-22 | John Ho Etech Engineering Services | ETECH NZ LIMITED 130 Kaimanawa Street, Kelvin Grove, Palmerston North 4414 FAB0095 | BS EN 12285-1:2005 | Description: UST Double Skin ASTM SA240 304SS Design Specification: BS EN 12285:1 Tank Type: Below Ground Stationary Name of Designer: John Ho Etech Engineering Services Capacity: 50,273 litres Compartments: 1 | Name: Methyl Methacrylate Class(es): 3.1B, 6.7B, 6.8B, 6.9B | ETECH ENGINEERING SERVICES LIMITED Unit 31 2 Bishop Dunn Place Flat Bush Auckland 2013 | Tank is destined for Allnex New Zealand, 14 Industry Road, Penrose, Auckland. 1061 | 2072-09-22 | FAB0095 (12/08/2023)
TNK20196 | 2022-09-22 | John Ho Etech Engineering Services | ETECH NZ LIMITED 130 Kaimanawa Street, Kelvin Grove, Palmerston North 4414 FAB0095 | BS EN 12285-1:2005 | Description: UST Double Skin ASTM SA240 304SS Design Specification: BS EN 12285:1 Tank Type: Below Ground Stationary Name of Designer: John Ho Etech Engineering Services Capacity: 50,273 litres Compartments: 1 | Name: Styrene Class(es): 3.1C, 6.1D, 6.8B, 6.9A | ETECH ENGINEERING SERVICES LIMITED Unit 31 1st Floor 2 Bishop Dunn Place Flat Bush Auckland 2013 | Tank is destined for Allnex New Zealand, 14 Industry Road, Penrose, Auckland. 1061 | 2072-09-22 | FAB0095 (12/08/2023)
TNK20197 | 2022-09-20 | Sanjay Pandey |  | AS1692:2006 | Description: 316L SS Vertical Cone Roof. Design Specification: AS1692:2006 Category 5 Tank Type: Above Ground Stationary Tank Name of Designer: Sanjay Pandey Capacity: 10,000 litres Compartments: 1 | Name: Sulphuric Acid 98% Class(es): 6.1A, 6.7A, 6.9A, 8.1A, 8.2A, 8.3A | NDA ENGINEERING LIMITED Private Bag 3018, Waikato Mail Centre, Hamilton, 3240 709 Te Rapa Road, Te Rapa, Hamilton, 3200 | Tank designed for PanPac Forest Products 1161 State Highway 2, Wairoa Road, Napier 4182, Hawke’s Bay, New Zealand. | 2047-12-31 | N/A
TNK20198 | 2023-02-10 | Dairy Technology Services Limited | DAIRY TECHNOLOGY SERVICES LIMITED PO Box 85, Hawera, 4640 17 Wallscourt Place, Normanby, Hawera,4614 FAB0089 | AS1692: 2006, Category 1 | Description: 440L octagonal prismatic above ground single skin stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 2550-10-01, Rev 6, Sheets: 1 to 6, Title: Domestic 440L Tank Assembly, Date:14.12.22 Name of Designer: O.Kelly Capacity: 438 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | DAIRY TECHNOLOGY SERVICES LIMITED 17 Wallscourt Place, Normanby, Hawera 4614 | The storage and transfer of Diesel only having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved to supply an engine or burner and approved for residential and workplaces. If supplying an engine or burner approved for use with diesel only having a flash point greater than 60 deg C but less than or equal to 93 deg C. Compliant with AS 1692:2006, Category 1. Under the conditions of EPA - Hazardous Substances (Hazardous Property Controls) Notice 2017. Statement of Design Compliance - PS1 - 6992-0000, 440L Home Heating Tank Generic PS1, Rev B, Released, 21Dec22, CPEng: Joseph Bain, #248672. Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure testin kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced Dairy Technology Services Limited drawings or applicable standard/s. | 2028-02-09 | FAB0089 | N/A
FAB0089 | 2023-02-09 |  | DAIRY TECHNOLOGY SERVICES LIMITED PO Box 85, Hawera, 4640 17 Wallscourt Place, Normanby, Hawera,4614 | AS1692:2006 | Refer to individual TNK numbers: TNK20198 | Name: Diesel Class(es): 3.1D, 6.7B | DAIRY TECHNOLOGY SERVICES LIMITED PO Box 85, Hawera, 4640 17 Wallscourt Place, Normanby, Hawera,4614 | Allocation of unique individual tank serial number to be stamped on each individual tank and recorded. Retention of individual tank fabrication, testing records and QA records for each tank. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2026-02-09 | Fabricator of: TNK20198
TNK20199 | 2022-10-31 | Hendl & Murray Engineering Limited - Deon den Otter | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | API Standard 650 | Description: 23,248 Litres above ground, vertical,cylindrical, single skin, stationary tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Hendl & Murray Engineering Limited - Deon den Otter Capacity: 23,248 Litres Maximum Safe Fill Level: 21,000 Litres (3,200mm) Compartments: 1 | Name: Nitric Acid - Concentration 60-64% Class(es): 6.1D, 6.9B, 8.1A, 8.2A, 8.3A | HENDL & MURRAY ENGINEERING LIMITED PO Box 5492, Frankton, Hamilton, 3242 103 Tawa Street, Melville, Hamilton, 3206 | Design report: 221601, RP01, RevA, Ultrex 21m3 Nitric Acid Tank Design Report, dated: 19/07/2022, author: Tom Robert (CPEng No.: 1024350). PS1/Design Statement issued by Mech Eng Ltd, to Hendl & Murray Engineering Ltd, to be supplied to Matamata-Piako District Council, in respect of Utrex 21m3 Nitric Acid Tank, at Fonterra Waitoa, Corner of No.1 Road and State Highway 26, Waitoa 3380. Seismic design to NZS 1170.5:2004 and NZSEE SDST:2009, wind design to AS/NZS 1170.2:2011, tank design to API 650 13th Ed, ventilation to API 2000 5th Ed. Signed by Tom Roberts (CPEng No.: 1024350), dated: 10-Oct-22. If manufacturing of this tank is for a different site other than the one listed in the PS1 above a new producer statement (PS1) will need to be provided to confirm the compliance with the wind & seismic requirements in the Health and Safety at Work (Hazardous Substances) Regulations 2017, Clause 17.6(3). Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced Hendl & Murray Engineering Limited drawings or applicable standard/s. Supplied API 650 data sheet from Hendl & Murray Engineering Limited Hendl & Murray Engineering Limited – HSWA producer Statement – Dated 15-09-2022 221601, RP01, RevA, Ultrex 21m3 Nitric Acid Tank Design Report, dated: 19/07/2022, author: Tom Robert (CPEng No.: 1024350) PS1/Design Statement issued by Mech Eng Ltd, to Hendl & Murray Engineering Ltd, to be supplied to Matamata-Piako District Council, in respect of Utrex 21m3 Nitric Acid Tank, at Fonterra Waitoa, Corner of No.1 Road and State Highway 26, Waitoa 3380. Seismic design to NZS 1170.5:2004 and NZSEE SDST:2009, wind design to AS/NZS 1170.2:2011, tank design to API 650 13th Ed, ventilation to API 2000 5th Ed. Signed by Tom Roberts (CPEng No.: 1024350), dated: 10-Oct-22 Ixom Nitric Acid 60-64% SDS, Revision Number 6, Revision date: 20-Apr-2022 | 2027-10-31 | FAB0033
TNK20200 | 2022-10-31 | Hendl & Murray Engineering Limited - Deon den Otter | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | API Standard 650 | Description: 11,160 Litres above ground, vertical, cylindrical, single skin, fixed coned roof, stationary tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Hendl & Murray Engineering Limited - Deon den Otter Capacity: 11,160 Litres Maximum Safe Fill Level: 10,000 Litres (2,600mm) Compartments: 1 | Name: Sulphuric Acid - With concentration of more than 51% Class(es): 6.1D, 6.7A, 6.9A, 8.1A, 8.2B,8.3A, 9.1C. | HENDL & MURRAY ENGINEERING LIMITED PO Box 5492, Frankton, Hamilton, 3242 103 Tawa Street, Melville, Hamilton, 3206 | Design report: 221602, RP01, RevA, Ultrex 10m3 Sulphuric Acid Tank Design Report, dated: 13/07/2022, author: Tom Robert (CPEng No.: 1024350). PS1/Design Statement issued by Mech Eng Ltd, to Hendl & Murray Engineering Ltd, to be supplied to Matamata-Piako District Council, in respect of Utrex 10m3 Sulphuric Acid Tank, at Fonterra Waitoa, Corner of No.1 Road and State Highway 26, Waitoa 3380. Seismic design to NZS 1170.5:2004 and NZSEE SDST:2009, wind design to AS/NZS 1170.2:2011, tank design to API 650 13th Ed, ventilation to API 2000 5th Ed. Signed by Tom Roberts (CPEng No.: 1024350), dated: 10-Oct-22. If manufacturing of this tank is for a different site other than the one listed in the PS1 above a new producer statement (PS1) will need to be provided to confirm the compliance with the wind & seismic requirements in the Health and Safety at Work (Hazardous Substances) Regulations 2017, Clause 17.6(3). Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced Hendl & Murray Engineering Limited drawings or applicable standard/s. Supplied API 650 data sheet from Hendl & Murray Engineering Limited Hendl & Murray Engineering Limited – HSWA producer Statement – Dated 15-09-2022 221602, RP01, RevA, Ultrex 10m3 Sulphuric Acid Tank Design Report, dated: 13/07/2022, author: Tom Robert (CPEng No.: 1024350) PS1/Design Statement issued by Mech Eng Ltd, to Hendl & Murray Engineering Ltd, to be supplied to Matamata-Piako District Council, in respect of Utrex 10m3 Sulphuric Acid Tank, at Fonterra Waitoa, Corner of No.1 Road and State Highway 26, Waitoa 3380. Seismic design to NZS 1170.5:2004 and NZSEE SDST:2009, wind design to AS/NZS 1170.2:2011, tank design to API 650 13th Ed, ventilation to API 2000 5th Ed. Signed by Tom Roberts (CPEng No.: 1024350), dated: 10-Oct-22. Ixom Sulphuric Acid Safety Data Sheet, Version 6, Issued: 21/06/2019. | 2027-10-31 | FAB0033
TNK20201 | 2022-10-11 | Aurecon |  | API Standard 650 | Description: 304L SS Vertical Cone roof Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: 510116-0000-DRG-MM Sheets 0001 to 0014 Name of Designer: Aurecon Capacity: 346,400 Litres Compartments: 1 | Name: Pine Wood Spirits CSTXR Class(es): 3.1C, 6.5B | AURECON NEW ZEALAND LIMITED Level 8, 42-52 Willis Street, Wellington Central, Wellington 6011 | This certificate expiry is based on the design life of the tank. Lawter T141 Aurecon Design Package, dated 17th December 2021, signed by Jonathan Ault (API653 No.: 80301) and Sam Lawrence (API653 No.: 40459; CPEng No.: 1003542). Page Macrae Quality Assurance Pack, Lawter 141 PR 82834, dated September 2021. Aurecon – Design Calculations for PME Mount Maunganui Tank T141 – Date: 26/11/2021. API650 data sheet – Aurecon – T141 Lawter Mount Maunganui – Data sheet No.: 510116-0000-DS-0141-01, Rev 1, Date: 14-10-2022. Lawter – Pass-1 Stripped CST (CSTXR) – Safety Data sheet – Version #: 1.2, Revision Date: 27-March-2019, Issue Date: 21-March-2019 | 2072-10-11 | N/A
TNK20202 | 2022-10-11 | Aurecon |  | API Standard 650 | Description: 304L SS Vertical Cone roof Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Aurecon Capacity: 126,700 litres Compartments: 1 | Name: Pinechem 600 Class(es): 3.1C, 6.5B | AURECON NEW ZEALAND LIMITED Level 8, 42-52 Willis Street, Wellington Central, Wellington 6011 | This Certificates expiry is based on the design life of the tank. Design statement/letter for T149 tank, design in accordance with API650 13th Edition, 2020, Appen. L, E, F, S, M & V. Seismic design to NZS1170.5:2004, wind design to NZS1170.2:2011. Venting in accordance with API2000:2014. Signed by Sam Lawrance (CPEng No.: 1003542). Page Macrae Quality Assurance Pack, Lawter Tank Compliance Upgrade, Stage 1, Tank T149, dated November 2020. Aurecon – Design Calculations for PME Mount Maunganui Tank T149 – Date: 7/12/2020. API650 data sheet – Aurecon – T149 Tank Datasheet – Data sheet No.: 510116-0000-DS-0149, Rev 1, Date: 14-10-2022. Lawter – Pinechem 600 – Safety Data sheet – Version #: 2.3, Revision Date: 01-April- 2019, Issue Date: 27-February-2019 | 2072-10-11 | N/A
TNK20203 | 2022-10-13 | TRL Engineering Pty Ltd |  | UL 1316 | Description: Z-104083-T1 - Z Massey North GRP Double Skinned permanently monitored 9.3m LOA x 2.5m DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-104083-T1-95-F105/F106 Name of Designer: TRL Engineering Pty Ltd Capacity: 40,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED, 175 Roydvale Avenue, Burnside, Christchurch 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2027-10-13 | N/A
TNK20204 | 2022-10-13 | TRL Engineering Pty Ltd |  | UL 1316 | Description: Z-104083-T3 - Z Massey North GRP Double Skinned permanently monitored 11.7m LOA x 2.5m DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-104083-T3-D-F109/F110 Name of Designer: TRL Engineering Pty Ltd Capacity: 50,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED, 175 Roydvale Avenue, Burnside, Christchurch 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2027-10-13 | N/A | N/A
TNK20205 | 2022-10-17 | TRL Engineering Pty Ltd |  | UL 1316 | Description: Z-100632-T3- Z Hunters Corner GRP Double-Skinned permanently monitored 7.0m L x 2.4m DIA, SFL28000 Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-100632-T3-D-F305/306 Name of Designer: TRL Engineering Pty Ltd Capacity: 30,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED, 175 Roydvale Avenue, Burnside, Christchurch 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2027-10-17 | N/A | N/A
TNK20206 | 2022-10-17 | TRL Engineering Pty Ltd |  | UL 1316 | Description: Z-100632-T1- Z Hunters Corner GRP Double Skinned permanently monitored 9.4m LOA x 2.4m DIA, SFL38000 Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-100632-T1-95-F301/302 Name of Designer: TRL Engineering Pty Ltd Capacity: 40,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED, 175 Roydvale Avenue, Burnside, Christchurch 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2027-10-17 | N/A | N/A
TNK20207 | 2022-10-13 | TRL Engineering Pty Ltd |  | UL 1316 | Description: Z-104083-T2 - Z Massey North GRP Double Skinned permanently monitored 9.4m LOA x 2.5m DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-104083-T2-91-F107/F108 Name of Designer: TRL Engineering Pty Ltd Capacity: 40,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED, 175 Roydvale Avenue, Burnside, Christchurch 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2027-10-13 | N/A | N/A
TNK20208 | 2022-10-19 | Fuelchief Limited, 5 Tanya Street, Bromley Christchurch 8062 | Fuelchief Limited, 5 Tanya Street, Bromley Christchurch 8062, FAB0076 As of 19/03/2023 FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | SWRI 95-03 | Description: SVR10000/SVR10000S Design Specification: SWRI 95-03 Tank Type: Above Ground Stationary Tank Drawing Numbers: SVR-10000-GA & SVR10000S GA Name of Designer: Fuelchief Capacity: 10000 Compartments: 1 | Name: Flammable liquids Class(es): 3.1A, 3.1B, 3.1C or 3.1D Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D Name: Waste Oil Re-refined Class(es): 3.1 D | Fuelchief Limited, 5 Tanya Street, Bromley Christchurch 8062 | Additional product classifications 6.1E, 6.3B, 9.1B | 2027-10-19 | FAB0076 As of 19/03/2023 FAB0093
TNK20209 | 2022-10-17 | TRL Engineering Pty Ltd |  | UL 1316 | Description: Z-100632-T2- Z Hunters Corner GRP Double-Skinned permanently monitored 11.6m L x 2.4m DIA, SFL48000 Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-100632-T2-91-F303/304 Name of Designer: TRL Engineering Pty Ltd Capacity: 50,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED, 175 Roydvale Avenue, Burnside, Christchurch 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2027-10-17 | N/A | N/A
TNK20210 | 2022-11-18 | Hendl & Murray Engineering Limited - Deon den Otter | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 FAB0033 | API Standard 650 | Description: 15,280 Litres above ground, vertical, cylindrical, flat bottom, fixed cone roof stationary tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Hendl & Murray Engineering Limited - Deon den Otter Capacity: 15,280 Litres Maximum Safe Fill Level: 12,000 Litres (2,450mm) Compartments: 1 | Name: Sulphuric Acid - 98% concentration Class(es): 6.1D, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A | HENDL & MURRAY ENGINEERING LIMITED 103 Tawa Street, Melville, Hamilton 3206 | Design report: 221851 RP01 RevA, Apex Water 12m³ Sulphuric Acid Tank Design Report, dated 10/10/22, author: Tom Roberts (CPEng No.: 1024350). 221851 PS1 & Design Statement issued by: Tom Roberts, to: Hendl and Murray Engineering Ltd, to be supplied to: South Waikato District Council, in respect of: Apex Water 12m3 Sulphuric Acid Tank, at: Olam Dairy, 90 Browning Street, Tokoroa. Seismic design to NZS 1170.5:2004, wind design to AS/NZS 1170.2:2011, tank design to API 650 13th Ed, ventilation to API 2000 5th Ed. Signed by Tom Roberts (CPEng No.: 1024350), dated: 14-Nov-22. If manufacturing of this tank is for a different site other than the one listed in the PS1 above a new producer statement (PS1) will need to be provided to confirm the compliance with the wind & seismic requirements in the Health and Safety at Work (Hazardous Substances) Regulations 2017, Clause 17.6(3). Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced Hendl & Murray Engineering Limited drawings or applicable standard/s. Supplied API 650 data sheet from Hendl & Murray Engineering Limited Hendl & Murray Engineering Limited – HSWA producer Statement – Dated 17-10-2022 221851 RP01 RevA, Apex Water 12m³ Sulphuric Acid Tank Design Report, dated 10/10/22, author: Tom Roberts (CPEng No.: 1024350) 221851 PS1 & Design Statement issued by: Tom Roberts, to: Hendl and Murray Engineering Ltd, to be supplied to: South Waikato District Council, in respect of: Apex Water 12m3 Sulphuric Acid Tank, at: Olam Dairy, 90 Browning Street, Tokoroa. Seismic design to NZS 1170.5:2004, wind design to AS/NZS 1170.2:2011, tank design to API 650 13th Ed, ventilation to API 2000 5th Ed. Signed by Tom Roberts (CPEng No.: 1024350), dated: 14-Nov-22 Ixom Sulphuric Acid Safety Data Sheet, Version 6, Issued: 21/06/2019. | 2027-11-18 | FAB0033 | N/A
TNK20211 | 2022-10-12 | NDA Engineering Trading as TIRA |  | AS1692:2006 | Description: Vertical Cone roof A240 304 S/S Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Drawing Numbers: 6771-702-G01 Name of Designer: NDA Engineering Trading as TIRA Capacity: 22,110 litres Compartments: 1 | Name: Covestro Desmodour T80 Class(es): 6.1A, 6.5A, 6.5B, 6.7B, 6.9A | NDA NEW ZEALAND LIMITED, 709 Te Rapa Road, Te Rapa, Hamilton 3200 | Tank is destined for Sleepyhead 58 Lumsden Road Ohinewai. Expiry is based on the Tank's design life | 2072-10-12 | N/A | N/A
TNK20212 | 2022-10-12 | NDA Engineering Trading as TIRA |  | AS1692:2006 | Description: Vertical Cone roof A240 304 S/S Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank NDA Engineering Trading as TIRA Capacity: 13,170 litres Compartments: 1 | Name: Huntsman Suprasec 7050 Class(es): 6.1B, 6.5A, 6.5B, 6.7B, 6.9A | NDA NEW ZEALAND LIMITED, 709 Te Rapa Road, Te Rapa, Hamilton 3200 | Tank is destined for Sleepyhead 58 Lumsden Road Ohinewai. Expiry is based on the Tank's design life | 2072-10-12 | N/A | N/A
TNK20213 | 2022-10-12 | NDA Engineering Trading as TIRA |  | AS1692:2006 | Description: Vertical Cone roof A240 304 S/S Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: NDA Engineering Trading as TIRA Capacity: 13,170 litres Compartments: 1 | Name: Wannate PM 8228 Class(es): 6.5A, 6.5B, 6.7B, 6.9A | NDA NEW ZEALAND LIMITED, 709 Te Rapa Road, Te Rapa, Hamilton 3200 | Tank is destined for Sleepyhead 58 Lumsden Road Ohinewai. Expiry is based on the Tank's design life | 2072-10-12 | N/A | N/A
TNK20214 | 2022-10-12 | NDA Engineering Trading as TIRA |  | AS1692:2006 | Description: Vertical Cone roof A240 304 S/S Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: NDA Engineering Trading as TIRA Capacity: 22,110 litres Compartments: 1 | Name: Voranate T80 Class(es): 6.1A, 6.5A, 6.5B, 6.7B, 6.9A | NDA NEW ZEALAND LIMITED, 709 Te Rapa Road, Te Rapa, Hamilton 3200 | Tank is destined for Sleepyhead 58 Lumsden Road Ohinewai. Expiry is based on the Tank's design life | 2072-10-12 | N/A | N/A
TNK20215 | 2022-11-10 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplasic Tanks | Description: T #3144 Primary Tank HDPE 2980mm DIA x 3363mm HOA Design Specification: BS EN 12573 SWI Thermoplasic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Chemfeed 402100/02/01 Name of Designer: Mech Eng Limited Capacity: 11000 litres Compartments: 1 | Name: Sodium hydroxide aqueous solution 50%w/w Class(es): 6.1B, 6.1D, 6.7A, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED, 26 Fremlin Place, Avondale, Auckland, 1026 | Re-engineered tank with reduced height overflow at 2120mm to 12100 litres. SFL 1893mm, satisfies seismic design requirements for sg 1.5 per Mech Eng Report 201201/C. Integral secondary containment greater than 110%. | 2027-11-10 | N/A | N/A
TNK20216 | 2022-11-17 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplasic Tanks | Description: T #3272 Self bunded HDPE, vertical cylinder 1800mm HOA x 2474mm DIA; Design Specification: BS EN 12573 SWI Thermoplasic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering DWG-P976-001 Name of Designer: Mech Eng Limited Capacity: 5000 litres Compartments: 1 | Name: Sodium hydroxide aqueous solution 50%w/w Class(es): 6.1B, 6.1D, 6.7A, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED, 26 Fremlin Place, Avondale, Auckland, 1026 | Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction Self bunding to 120% primary tank volume | 2027-11-17 | N/A | N/A
TNK20217 | 2022-11-22 | Tankreline NZ Limited |  | UL 1316 | Description: Z-104077-T2 - Z Royal Oak GRP Double Skinned 9.4m LOA x 2.4m DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-104077-T2-91-F303; Z-104077-T2-91- F304 Name of Designer: Tankreline NZ Limited Capacity: 40,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED, 175 Roydvale Avenue, Burnside, Christchurch, 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2027-11-22 | N/A | N/A
TNK20218 | 2022-11-22 | Tankreline NZ Limited |  | UL 1316 | Description: Z-104077-T3 - Z Royal Oak GRP Double Skinned 9.4m LOA x 2.4m DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-104077-T3-D-F305; Z-104077-T2-D-F306 Name of Designer: Tankreline NZ Limited Capacity: 40,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED, 175 Roydvale Avenue, Burnside, Christchurch, 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2027-11-22 | N/A | N/A
TNK20219 | 2022-11-22 | Tankreline NZ Limited |  | UL 1316 | Description: Z-104077-T1 - Z Royal Oak GRP Double Skinned 9.4m LOA x 2.4m DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-104077-T1-95-F301; Z-104077-T1-95- F302 Name of Designer: Tankreline NZ Limited Capacity: 40,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED, 175 Roydvale Avenue, Burnside, Christchurch, 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2027-11-22 | N/A | N/A
TNK20220 | 2022-11-28 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplasic Tanks | Description: T#3257 Primary Tank HDPE 2500 mm DIAID x 2822mm HOA Design Specification: BS EN 12573 SWI Thermoplasic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Chemfeed 401593/01/01 rev J Name of Designer: Mech Eng Limited Capacity: 10000 litres Compartments: 1 | Name: Sodium hydroxide aqueous solution 50%w/w Class(es): 6.1D, 6.7A, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED, 26 Fremlin Place, Avondale, Auckland, 1026 | Integral secondary containment greater than 110%. CONSTRUCTION VERIFIED Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2027-11-28 | N/A | N/A
TNK20221 | 2022-11-28 | Mech Eng Limited |  | AS 2634 | Description: T#3256 Primary Tank UPVC/GRP 2300 mm DIA-ID x 2614mm HOA Design Specification: AS 2634 Tank Type: Above Ground Stationary Tank Drawing Numbers: Chemfeed 401593/02/03 rev D ; 401593/02/01 rev F Name of Designer: Mech Eng Limited Capacity: 10000 litres Compartments: 1 | Name: Nitric acid 67% Class(es): 5.1.1C, 6.1D, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED, 26 Fremlin Place, Avondale, Auckland, 1026 | Integral secondary containment greater than 110%. CONSTRUCTION VERIFIED Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2022-11-28 | N/A | N/A
TNK20222 | 2022-12-02 | Etech Engineering Services Ltd |  | AS 1692:2006 Category 5 FAB0091 | Description: 316L SS Vertical cone bottom shell and bottom steam jacketed Design Specification: AS 1692 Tank Type: Process Container Name of Designer: Etech Engineering Services Ltd Capacity: 8,500 litres Compartments: 1 | Name and Class(es): Caustic Soda 50% 6.1D, 8.1A, 8.2B, 8.3A Cholic Acid 6.5B CRUDE DEOXYCHOLIC ACID 6.1D, 6.5B Mother Liquor 8.1A, 8.2A, 8.3A Toluene 3.1B, 6.1D, 6.8B, 6.9B | ETECH ENGINEERING SERVICES LIMITED 130 Kaimanawa Street, Kelvin Grove, Palmerston North, 4414 | Process Tank to be built for NZ Pharmaceuticals 68 Weld Street, RD 2 Palmerston North 4472. The dimpled steam jacket is designed under Pressure Equipment Cranes and Ropeways Act. The jacket design is 10 Bar saturated steam and is not part of this design certiﬁcate. | 2072-12-02 | FAB0091(13/12/2022)
TNK20223 | 2022-12-09 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplasic Tanks | Description: #3229 HDPE 1800mm D x 2641mm H x 12mm WT Design Specification: BS EN 12573 SWI Thermoplasic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Chemfeed 209/04 Name of Designer: Mech Eng Limited Capacity: 4750 litres Compartments: 1 | Name: Sulphuric acid 78% Class(es): 6.1D, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED, 26 Fremlin Place, Avondale, Auckland, 1026 | Integral Secondary containment >110% CONSTRUCTION VERIFIED Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2022-12-09 | N/A | N/A
TNK20224 | 2022-11-20 | Culham Engineering |  | API650 | Description: Vertical Cone roof Single skin MS Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Culham Engineering Capacity: 8,100 cubic meters Compartments: 1 | Name: VLSFO Class(es): 3.1D, 6.1D, 6.7A, 6.8B, 6.9B | CULHAM ENGINEERING COMPANY LIMITED PO Box 660, Whangarei, 0140 15-17 Hewlett Street, Port Whangarei | Tank ID MN20 is to be constructed on-site at Stolthaven 156 Hewletts Road, Mount Maunganui. | 2077-11-20 | N/A
TNK20225 | 2022-11-20 | Culham Engineering |  | API650 | Description: Vertical Cone roof Single skin MS Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Culham Engineering Capacity: 8,100 cubic meters Compartments: 1 | Name: VLSFO Class(es): 3.1D, 6.1D, 6.7A, 6.8B, 6.9B | CULHAM ENGINEERING COMPANY LIMITED PO Box 660, Whangarei, 0140 15-17 Hewlett Street, Port Whangarei | Tank ID MN21 is to be constructed on-site at Stolthaven, 156 Hewletts Road, Mount Maunganui. | 2077-11-20 | N/A
TNK20226 | 2023-02-10 | Palmers Mechanical Limited / Epsilon Engineering - P.Griffin | PALMERS MECHANICAL LIMITED 2 Neptune Street, Dunedin Central, Dunedin, 9016 FAB0090 | AS1692: 2006, Category 1 | Description: 428 Litres above ground single skin octagonal prismatic stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Palmers Mechanical Limited / Epsilon Engineering - P.Griffin Capacity: 428 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | PALMERS MECHANICAL LIMITED 2 Neptune Street, Dunedin Central, Dunedin, 9016 | Approved to supply an engine or burner and approved for residential and workplaces. If supplying an engine or burner approved for use with diesel only having a flash point greater than 60 deg C but less than or equal to 93 deg C. Compliant with AS 1692:2006, Category 1, EPA Notice - Hazardous Substances (Hazardous Property Controls) Notice 2017. Design Statement - 7204-1000 - Signed by: Joseph Bain (CPEng 248672), Date: 5/12/2022. Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure testin kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabricati on and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced Palmers Mechanical Limited drawings or applicable standard/s. | 2028-02-10 | FAB0090 | N/A
FAB0090 | 2023-02-10 |  | PALMERS MECHANICAL LIMITED 2 Neptune Street, Dunedin Central, Dunedin, 9016 FAB0090 | AS1692:2006 | Refer to individual TNK numbers: TNK20226 | Name: Diesel Class(es): 3.1D, 6.7B | PALMERS MECHANICAL LIMITED 2 Neptune Street, Dunedin Central, Dunedin, 9016 | Allocation of unique individual tank serial number to be stamped on each individual tank and recorded. Retention of individual tank fabrication, testing records and QA records for each tank. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2026-02-10 | Fabricator of: TNK20226 | N/A
TNK20227 | 2022-12-20 | Protank Industries Ltd | Prior to 17/10/2023: Protank Industries Limited PO Box 10125, Phillipstown, Christchurch, 8145 84b Armstrong Street, Roslyn, Palmerston North, 4414 FAB0085 As of 17/10/2023: PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 FAB0096 | AS 1692:2006, Category 4 | Description: 9,738 Litres above ground cylindrical horizontal double skinned stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Name of Designer: Protank Industries Ltd - Daniel Thomas Capacity: 9,738 Litres Maximum Safe Fill Level: 9,450 Litres (1,748mm) Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | PROTANK INDUSTRIES LIMITED PO Box 10125, Phillpstown, Christchurch,8145 84b Armstrong Street, Roslyn, PalmerstonNorth, 4414 | 9,738 Litres above ground cylindrical horizontal double skinned stationary tank achieves 110% secondary containment. Flat ends stiffened in accordance with AS1210 - 6986-0001, 10kL Tank General PS1, Rev 01, Signed by Joe Bain, CPEng number 248672, Date: 16/12/22. Producer Statement – PS1 Design – Building Code Clause(s): B1, Issued By: Motovated Design and Analysis LTD, To: Protank NZ, Supplied to: As Applicable, In Respect of: Wind and Seismic Assessment of Duel Storage Tank, At: Various Locations (refer to design parameters) - 6986-0001, 10kL Tank General PS1, Rev 01, Signed by Joe Bain, CPEng number 248672, Date: 16/12/22. Allocation of unique serial number for each tank and retention of individual tank fabrication and testing records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Manufacturer to retain individual tank fabrication and test records. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced Protank Industries Limited drawings or applicable standard/s. Approved for supplying an engine or burner. If supplying an engine or burner approved for use with diesel only having a flash point greater than 60 deg C but less than or equal to 93 deg C. | 2027-12-20 | Prior to 17/10/2023: FAB0085 As of 17/10/2023: FAB0096
TNK20228 | 2022-12-09 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplasic Tanks | Description: T#3277 HDPE Vertical cylinder 2800mm DIA x 3286mm HOA x 20mm WT Design Specification: BS EN 12573 SWI Thermoplasic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: MASONS 19-052-SHT-01 Rev E Name of Designer: Mech Eng Limited Capacity: 15000 litres Compartments: 1 | Name: Caustic soda 30% w/w aqueous solution Class(es): 6.1D, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED, 26 Fremlin Place, Avondale, Auckland, 1026 | CONSTRUCTION VERIFIED Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2027-12-09 | N/A | N/A
TNK20229 | 2022-12-15 | Transtank / Qingdao Jinhuanghai Container |  | AS1692: 2006 | Description: T30-TNTK-402906-4 CONTAINERISED DOUBLE SKINNED >110% SECONDARY CONTAINMENT Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: JHC-T-C30-GA01 Name of Designer: Transtank / Qingdao Jinhuanghai Container Co Capacity: 31400 litres; 28000 litres SFL Compartments: 1 | Name: Diesel & Combustible liquids AS1940 C1/C2 Class(es): 3.1D | AGGREKO (NZ) LIMITED, 1048-1050 Great South Road, Mount Wellington, Auckland, 1060 | DOM 2012 | 2027-12-15 | N/A | N/A
TNK20230 | 2022-12-16 | Carlyon Civil Construction | Carlyon Civil Construction Ltd PO Box 10092 Te Rapa, Hamilton, 3241 12 - 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | SWRI 95-03 | Description: FR-MC-DS-20-110KL Tank Range Design Specification: SWRI 95-03 Tank Type: Above Ground Stationary Tank Drawing Numbers: Carlyon FR-MC-DS Tank Assembly Name of Designer: Carlyon Civil Construction Capacity: 20,000 - 110,000 litres Compartments: 5 | Name: Flammable Liquids, Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | CARLYON CIVIL CONSTRUCTION LIMITED, 3 Ellis Street, Frankton, Hamilton, 3204 | Number of compartments varies per table in FR-MC-DC-Tank Assembly Drawing | 2027-12-16 | FAB0083
TNK20231 | 2022-12-19 | Maskell/Tank Reline NZ Limited |  | UL 1316 | Description: HOS911: FRP Single skin 8750mm LOA x 2500mm DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Mobil Hospital rev 1; 300-01; 300-02; 300- 03; 300-04; Maskell E40000 Name of Designer: Maskell/Tank Reline NZ Limited Capacity: 40000 Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED, 351 Featherston Street, Palmerston North, 4414 | Satisfies Regulation 17.91 (2)(b)(ii) & 17.91(2)(b)(iii) | 2027-12-19 | N/A | N/A
TNK20232 | 2022-12-19 | Maskell/Tank Reline NZ Limited |  | UL 1316 | Description: HOS912: FRP Single skin 8750mm LOA x 2500mm DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Mobil Hospital rev 1; 300-01; 300-02; 300- 03; 300-04; Maskell E40000 Name of Designer: Maskell/Tank Reline NZ Limited Capacity: 40000 Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED, 351 Featherston Street, Palmerston North, 4414 | Satisfies Regulation 17.91 (2)(b)(ii) & 17.91(2)(b)(iii) | 2027-12-19 | N/A | N/A
TNK20233 | 2022-12-19 | Maskell/Tank Reline NZ Limited |  | UL 1316 | Description: HOS983: FRP Single skin 8750mm LOA x 2500mm DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Mobil Hospital rev 1; 300-01; 300-02; 300- 03; 300-04; Maskell E40000 Name of Designer: Maskell/Tank Reline NZ Limited Capacity: 40000 Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED, 351 Featherston Street, Palmerston North, 4414 | Satisfies Regulation 17.91 (2)(b)(ii) & 17.91(2)(b)(iii) | 2027-12-19 | N/A | N/A
TNK20234 | 2022-12-19 | Maskell/Tank Reline NZ Limited |  | UL 1316 | Description: HOSD4: FRP Single skin 8750mm LOA x 2500mm DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Mobil Hospital rev 1; 300-01; 300-02; 300- 03; 300-04; Maskell E40000 Name of Designer: Maskell/Tank Reline NZ Limited Capacity: 40000 Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED, 351 Featherston Street, Palmerston North, 4414 | Satisfies Regulation 17.91 (2)(b)(ii) & 17.91(2)(b)(iii) | 2027-12-19 | N/A | N/A
TNK20235 | 2022-12-16 | Carlyon Civil Construction |  | SWRI 95-03 | Description: FR-DS-SC-1.2KL-110KL Tank Range Design Specification: SWRI 95-03 Tank Type: Above Ground Stationary Tank Drawing Numbers: Carlyon FIRE RATED-DS-SC-PED Tank Assembly Name of Designer: Carlyon Civil Construction Capacity: 1,200 - 110,000 litres Compartments: 1 | Name: Petroleum Products & Flammable Liquids Class(es): 3.1A, 3.1B, 3.1C, 3.1D | CARLYON CIVIL CONSTRUCTION LIMITED, 3 Ellis Street, Frankton, Hamilton, 3204 | Tank Dimensions vary per table in FR-DS-SC-PED-Tank Assembly Drawing | 2027-12-19 | N/A | N/A
FAB0091 | 2022-12-13 |  | ETECH NZ LIMITED 130 Kaimanawa Street, Kelvin Grove, Palmerston North 4414 | AS 1692: 2006 Category 5 | Tank Serial Number: 37T30 Tank Type: Process Container Maximum Quantity: 8,500 Litres Year of Manufacture: 2022 Tank Details: 316L SS Vertical cone bottom, shell and bottom steam jacketed Design Specifications: AS 1692: 2006 (Category 5) Reference: TNK20222 | Caustic soda 50% 6.1D, 8.1A, 8.2B, 8.3A Cholic Acid 6.5B Crude Deoxycholic acid 6.1D, 6.5B Mother Liquor 8.1A, 8.2A, 8.3A Toluene 3.1B, 6.1D, 6.8B, 6.9B | ETECH NZ LIMITED 130 Kaimanawa Street, Kelvin Grove, Palmerston North 4414 | Process tank to be fabricated for NZ Pharmaceuticals 68 weld street, RD2 Palmerston North. The dimpled jacket is designed under PECPR (pressure equipment Cranes and Ropeways Act) the jacket is 10 bar saturated steam. Must be fabricated as per the original drawings EES-NZP-37T30-001,/-002,/-003,/-004,/-005,/-006,/-007,/-008,/-009 rev 1 | 2023-12-13 | TNK20222
TNK20236 | 2023-01-10 | Tankreline NZ Limited |  | UL 1316 | Description: Z-103757-T1 - Z Whangaparoa GRP Double Skinned 6.9m LOA x 2.4m DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-103757-T1-95-F301; Z-103757-T1-95- F302 Name of Designer: Tankreline NZ Limited Capacity: 27,800 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 175 Roydvale Avenue, Burnside, Christchurch, 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2028-01-10 | N/A | N/A
TNK20237 | 2023-01-10 | Tankreline NZ Limited |  | UL 1316 | Description: Z-103757-T2 - Z Whangaparoa GRP Double Skinned 11.8m LOA x 2.4m DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-103757-T2-91-F303; Z-103757-T2-91-F304 Name of Designer: Tankreline NZ Limited Capacity: 48,500 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 175 Roydvale Avenue, Burnside, Christchurch, 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2028-01-10 | N/A | N/A
TNK20238 | 2023-01-10 | Tankreline NZ Limited |  | UL 1316 | Description: Z-103757-T3 - Z Whangaparoa GRP Double Skinned 9.4m LOA x 2.4m DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-103757-T3-D-F305; Z-103757-T3-D-F306 Name of Designer: Tankreline NZ Limited Capacity: 38,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 175 Roydvale Avenue, Burnside, Christchurch, 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2028-01-10 | N/A | N/A
TNK20239 | 2022-03-04 | TRL Engineering Pty Ltd |  | UL 1316:1994 (2nd Edition) | Description: Z-101189-T1 - Z Awakeri Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-101189-T1-95-F104; Z-101189-T1-95-F105 Name of Designer: TRL Engineering Pty Ltd Capacity: 14,000 litres | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 175 Roydvale Avenue, Burnside, Christchurch, 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2027-03-04 | Tank capacity does not match drawing, amendment requested 12/01/2023, received 06/06/2023 Correct documentation received 25/06/2026 | N/A
TNK20240 | 2022-03-04 | TRL Engineering Pty Ltd |  | UL 1316:1994 (2nd Edition) | Description: Z-101189-T2 - Z Awakeri Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: DWG-Z-101189-T2-91-F106; DWG-Z-101189-T2-91-F107 Name of Designer: TRL Engineering Pty Ltd Capacity: 45,000 litres | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 175 Roydvale Avenue, Burnside, Christchurch, 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2027-03-04 | Certificate missing, requested 12/01/2023, received 06/06/2023 with error, amendment requested 06/06/2023. Correct documentation received 25/06/2026 | N/A
TNK20241 | 2022-03-04 | TRL Engineering Pty Ltd |  | UL 1316:1994 (2nd Edition) | Description: Z-101189-T3 -Z Awakeri Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-101189-T3-D-108; Z101189-T3-D-F109 Name of Designer: TRL Engineering Pty Ltd Capacity: 50,000 litres | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 175 Roydvale Avenue, Burnside, Christchurch, 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2027-03-04 | Correct documentation received 25/06/2026 | N/A
TNK20242 | 2023-02-03 | Plaspoke Limited / Mech Eng Limited | PLASPOKE LIMITED 35 Saleyards Road, Ōtāhuhu, Auckland, 1062 FAB0094 | BS EN 12573 SWI Thermoplasic Tanks | Description: Self Bunded HDPE Chemical Tanks SB-01 Range Design Specification: BS EN 12573 SWI Thermoplasic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: PLAS-SB-01 (sheets 1-7 Name of Designer: Plaspoke Limited / Mech Eng Limited Capacity: 2500-20000 Compartments: 1 | Name: Various (See Details Section) Class(es): 6.1A, 6.1B, 6.1C, 6.1D, 6.5A, 6.5B, 6.6A, 6.6B, 6.7A, 6.7B, 6.8A, 6.8B, 6.8C, 6.9A, 6.9B, 8.1A, 8.2A, 8.2B, 8.2C, 8.3A | Plaspoke Limited, 95 St Annes Crescent, Wattle Downs, Auckland 2103 | Approved Substances for this range of HDPE Tanks is limited as follows: Any hazardous substance with a flammable liquid classification is excluded. Hydrocarbons without flammable liquid classification but carry solvent properties incompatible with HDPE are excluded. Exclusions to use for hazardous substances and the various concentrations listed by BS EN 12573 and the Thermoplastic Stationary Tank SWI 2017 Section 12. Manufacturer to provide confirmation of chemical compatibility for specific products to the purchaser of each tank. | 2028-02-03 | FAB0094 | N/A
TNK20243 | 2023-02-10 | Hendl & Murray Engineering Limited |  | API Standard 650 | Description: 316L SS Vertical Cone Roof Insulated Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Hendl & Murray Engineering Limited Capacity: 103,000 Litres Safe Fill Level: 90,000 Litres Compartments: 1 | Name: 98% Sulfuric Acid Class(es): 6.1D, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A | Hendl & Murray Engineering Ltd PO Box 5492, Frankton, Hamilton, 3242 103 Tawa Street, Melville, Hamilton, 3206 | The Design is valid for the Tauhara Steam Field Waikato, off SH1 3378. Design report issued by: MechEng Ltd, to: Hendl & Murray Engineering Ltd, with title 221951 RP01 RevC, Contact Energy 903 Sulphuric Acid Tank Design Report, referencing design codes: AS 3990:1990, NZS 1170.5:2004, NZSEE, EOTA TR 029 and EOTA TR 045, AS1210:2010, API 650, 13th Ed & & Appendix S., NZS 1170.0: 2002, NZS 1170.2: 2021, NZS 1170.3: 2003, API 2000:1998, dated: 02/02/2023, author: Tom Roberts. | 2073-02-10
TNK20244 | 2023-03-16 | Carlyon Civil Construction | Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | UL 142:2009 | Description: 1800L_DS-OG Pre-Heat Tank Design Specification: UL 142:2009 Tank Type: Above Ground Stationary Tank Drawing Numbers: Carlyon FH44275-DAP-PHT Name of Designer: Carlyon Civil Construction Capacity: 1800 Compartments: 1 | Name: Diesel / Refined Waste Oil Class(es): 3.1D | CARLYON CIVIL CONSTRUCTION LIMITED 3 Ellis Street, Frankton, Hamilton 3204 |  | 2028-03-16 | FAB0083 | N/A
FAB0092 | 2023-03-27 |  | A W TRINDER LIMITED PO Box 3143, Richmond, 7050 2 Poutama Street, Richmond, 7020 |  | Steel tanks up to 60,000 litres capacity in accordance with AS 1692-2006 Refer to individual TNK numbers: TNK18045, TNK18046, TNK18047,TNK18048, TNK18049, TNK18050 | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | A W TRINDER LIMITED PO Box 3143, Richmond, 7050 2 Poutama Street, Richmond, 7020 | Allocation of unique individual tank serial number to be stamped on each individual tank and recorded. Retention of individual tank fabricati on, testing records and QA records for each tank. In addition to the conditions specified on Certificate 100241-6813-02, the following conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the coompliance certifier who issued the certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2026-03-27 | Fabricator of: TNK18045, TNK18046, TNK18047,TNK18048, TNK18049, TNK18050
TNK20245 | 2023-02-24 | ACME Engineering |  | API Standard 650 | Description: Vertical Cone roof AS3678-250, Weld efficiency=70%. Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: ACME Engineering Capacity: 385 m3 Compartments: 1 | Name: Acetone Class(es): 3.1B Name: Mineral Turpentine Class(es): 3.1C, 6.7B, 6.9B | ACME Engineering Limited 11-29 Hutt Road, Petone, Lower Hutt, 5012 | Designed for Stolthaven NZ Limited, 156 Hewletts Road, Mount Maunganui, 3116. Bay of Plenty | 2073-02-24
FAB0093 | 2023-03-19 |  | FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS1692 and UL142 above-ground tanks UL2085 rated to SwRI 95-03 | Up to 19/03/2026: Design approved for AS1692, and UL142 above-ground tanks UL2085 rated to SwRI 95-03 up to 110,000 litres. Reference: TNK13011, TNK13013, TNK13014, TNK13015, TNK13017, TNK15001, TNK16017, TNK17021, TNK17024, TNK18013, TNK20019, TNK20020, TNK20023, TNK20032, TNK20075, TNK20076, TNK20077, TNK20208, TNK20324, TNK20336, TNK20357, TNK20437, TNK20440, TNK20443, TNK20553 As of 02/04/2026: Designs approved for AS1692, UL142, UL2085 rated to SwRI 95-03 up to 110,000 Litres for which TNK's: TNK13011, TNK13013, TNK13015, TNK13017, TNK15001, TNK17021, TNK17024, TNK18013, TNK18016, TNK20019, TNK20020, TNK20075, TNK20076, TNK20077, TNK20208, TNK20324, TNK20336, TNK20357, TNK20437, TNK20440, TNK20443, TNK20476, TNK20535, TNK20547, TNK20564 | Class 3 and Class 6 hazardous substances | FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | Up to 19/03/2026: Replaces the previous Certificate, FAB0076 issued to Fuelchief of the factory at 5 Tanya Street, Bromley, Christchurch, 8062. SwRI tanks are licensed by SwRI (Southwest Research Institute) and Fuelchief procedures and QC are subject to periodic validation by SwRI. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the test certifier who issued the test certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. As of 02/04/2026: Approved to fabricate tanks in accordance with the provisions of AS1692, UL142, UL2085, SwRI 93-01, SwRI 95-03 and the requirements of the Health and Safety at Work (Hazardous Substances) Regulations 2017 up to a capacity of 110,000 litres, for which TNK numbers have been registered with WorkSafe New Zealand. Licensed by Southwest Research Institute (SwRI) to manufacture tanks tested in accordance with SwRI 93-01, 95-03 Testing Procedures. Fabrication, inspection and testing in accordance with the specified tank design and fabrication code, approved tank design drawings and approved for construction drawings. The SwRI tanks are licensed by SwRI (Southwest Research Institute) and Fuelchief procedures and QC are subject to periodic validation by SwRI. Allocation of unique individual tank serial number to be stamped on each individual tank and recorded. Retention of individual tank fabrication, testing records and QA records for each tank. | 2029-04-02 | Up to 19/03/2026: Fabricator of: TNK13011, TNK13013, TNK13014, TNK13015, TNK13017, TNK15001, TNK16017, TNK17021, TNK17024, TNK18013, TNK20019, TNK20020, TNK20023, TNK20032, TNK20075, TNK20076, TNK20077, TNK20208, TNK20324, TNK20336, TNK20357, TNK20437, TNK20440, TNK20443, TNK20553 As of 02/04/2026: Fabricator of: TNK13011, TNK13013, TNK13015, TNK13017, TNK15001, TNK17021, TNK17024, TNK18013, TNK18016, TNK20019, TNK20020, TNK20075, TNK20076, TNK20077, TNK20208, TNK20324, TNK20336, TNK20357, TNK20437, TNK20440, TNK20443, TNK20476, TNK20535, TNK20547, TNK20564
TNK20246 | 2023-03-28 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3275 Primary Tank HDPE 2500 mm DIAID x 2819mm HOA Design Specification: BS EN 12573 SWI Thermoplasic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Chemfeed 402777-01-01 rev E, Name of Designer: Mech Eng Limited Capacity: 10000 litres Compartments: 1 | Name: Sodium hydroxide (Caustic soda) 50% w/w aqueous solution Class(es): 6.1D, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Integral secondary containment greater than 110%. CONSTRUCTION VERIFIED Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2028-03-28
TNK20247 | 2023-03-28 | Mech Eng Limited |  | AS 2634 | Description: T#3274 Primary Tank GRP 2500 mm DIA-IDx 2614mm HOA Design Specification: AS 2634 Tank Type: Above Ground Stationary Tank Drawing Numbers: Chemfeed 402777-02-01 rev E, 402777-02-02 rev B, 402777-02-03 rev D Name of Designer: Mech Eng Limited Capacity: 10000 litres Compartments: 1 | Name: Sulphuric acid 98% Class(es): 6.1D, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Integral secondary containment greater than 110%. CONSTRUCTION VERIFIED Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction | 2027-03-28
TNK20248 | 2023-03-29 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3284 Primary Tank HDPE 2700 mm DIAID x 2819mm HOA Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plastics Construction CTX-001 rev C2 Name of Designer: Mech Eng Limited Capacity: 10000 litres Compartments: 1 | Name: Poly Aluminium Chloride (PAC) aqueous solution Class(es): 6.1D, 6.9B | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Integral secondary containment greater than 110%. CONSTRUCTION VERIFIED Satisfies Regulation 17.91(2)(b)(ii) for Tank Construction Includes Classifications 6.3A, 6.4A on PAC SDS | 2028-03-29
TNK20249 | 2023-02-03 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: 400017-T1 GRP Double skin 8750mm LOA x 2500mm DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Mobil Papatoetoe XPP-400017-T1 Name of Designer: Tankreline NZ Limited Capacity: 40000 L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 73 East Tamaki Road, Papatoetoe, Auckland, 2025 | Satisfies Regulation 17.91 (2)(b)(ii) & 17.91(2)(b)(iii) Permanent Hydro-guard interstice monitor | 2028-02-03
TNK20250 | 2023-02-03 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: 400017-T3 GRP Double skin 8750mm LOA x 2500mm DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Mobil Papatoetoe XPP-400017-T3 Name of Designer: Tankreline NZ Limited Capacity: 40000 L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 73 East Tamaki Road, Papatoetoe, Auckland, 2025 | Satisfies Regulation 17.91 (2)(b)(ii) & 17.91(2)(b)(iii) Permanent Hydro-guard interstice monitor | 2028-02-03
TNK20251 | 2023-04-04 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: 400017-T2 GRP Double skin 8750mm LOA x 2500mm DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Mobil Papatoetoe XPP-400017-T2 Name of Designer: Tankreline NZ Limited Capacity: 40000 L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 73 East Tamaki Road, Papatoetoe, Auckland, 2025 | Satisfies Regulation 17.91 (2)(b)(ii) & 17.91(2)(b)(iii) Permanent Hydro-guard interstice monitor | 2028-04-04
TNK20252 | 2023-04-04 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: 400017-T4 GRP Double skin 8750mm LOA x 2500mm DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Mobil Papatoetoe XPP-400017-T4 Name of Designer: Tankreline NZ Limited Capacity: 40000 L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 73 East Tamaki Road, Papatoetoe, Auckland, 2025 | Satisfies Regulation 17.91 (2)(b)(ii) & 17.91(2)(b)(iii) Permanent Hydro-guard interstice monitor | 2028-04-04
TNK20253 | 2023-04-27 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplasic Tanks | Description: T#3280 Single Skin HDPE 1800mm DIA x 2611mm HOA x 12/24 mm WT Design Specification: BS EN 12573 SWI Thermoplasic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Chemfeed 402244-01-30 rev D Name of Designer: Mech Eng Limited Capacity: 5000 litres Compartments: 1 | Name: HYDROFLUOROSILICIC ACID 1.15sg Class(es): 8.2C, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 | 2028-04-27
FAB0094 | 2023-08-11 |  | PLASPOKE LIMITED 35 Saleyards Road, Ōtāhuhu, Auckland, 1062 |  | Welded thermoplastic tanks designed and constructed to to BS EN 12573, with a maximum capacity of 15,000L. Reference: TNK20242, TNK20118, TNK20298, TNK20486 | Class 6, 8 & 9 hazardous liquids | PLASPOKE LIMITED 35 Saleyards Road, Ōtāhuhu, Auckland, 1062 | The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the compliance certifier who issued the compliance certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2026-08-11 | Fabricator of: TNK20242 TNK20118 TNK20298 TNK20486
TNK20254 | 2023-06-15 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: Z-103709-T1 - Z Te Atatu GRP Double Skinned 6.9m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-103709-T1-95-F301 Name of Designer: Tankreline NZ Limited Capacity: 28,993 litres; SFL 27,500 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 175 Roydvale Avenue, Burnside, Christchurch 8053 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-06-15
TNK20255 | 2023-06-15 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: Z-103709-T2 - Z Te Atatu GRP Double Skinned 11.8m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-103709-T2-91-F302 Name of Designer: Tankreline NZ Limited Capacity: 51,289 litres; SFL 48,500 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 175 Roydvale Avenue, Burnside, Christchurch 8053 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-06-15
TNK20256 | 2023-06-15 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: Z-103709-T3 - Z Te Atatu GRP Double Skinned 9.4m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-103709-T3-D-F303 Name of Designer: Tankreline NZ Limited Capacity: 39,507 litres; SFL 37,500 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 175 Roydvale Avenue, Burnside, Christchurch 8053 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-06-15
TNK20257 | 2023-07-04 | MechEng Tom Roberts reviewed |  | AS 1692: 2006 | Description: 304 SS Vertical Dome roof and bottom on legs: SN:DTS-CT-T1301-011 Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: MechEng Tom Roberts reviewed. Capacity: 5,690 litres Compartments: 1 | Name: Heptane Class(es): 3.1B | DAIRY TECHNICAL SERVICES LIMITED (DTS) PO Box 85, Te Rapa Park, Hawera, 4640 17 Wallscourt Place, Normanby, Hāwera, 4614 | The tank is to be installed at Reswax, 214 Sandhills Road Awanui 0483. | 2073-07-04
TNK20258 | 2023-07-04 | Danie Ippel |  | AS 1692: 2006 | Description: 304 SS Vertical Dome Top Cone Bottom on legs. SN:DTS-CT-T1401-011 Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Danie Ippel Capacity: 5,690 litres Compartments: 1 | Name: Methanol Class(es): 3.1B, 6.1D, 6.8B, 6.9A | DAIRY TECHNICAL SERVICES LIMITED (DTS) PO Box 85, Te Rapa Park, Hawera, 4640 17 Wallscourt Place, Normanby, Hāwera, 4614 | The tank is to be installed at Reswax, 214 Sandhills Road Awanui 0483. | 2073-07-04
TNK20259 | 2023-07-04 | Danie Ippel |  | AS 1692: 2006 | Description: 304 SS Vertical Dome Top Cone Bottom on legs. SN:DTS-CT-T1501-011 Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Danie Ippel Capacity: 5,690 litres Compartments: 1 | Name: n-Butyl Acetate Class(es): 3.1B, 6.1D | DAIRY TECHNICAL SERVICES LIMITED (DTS) PO Box 85, Te Rapa Park, Hawera, 4640 17 Wallscourt Place, Normanby, Hāwera, 4614 | The tank is to be installed at Reswax, 214 Sandhills Road Awanui 0483. | 2073-07-04
TNK20260 | 2023-07-04 | TIRA NDA |  | AS 1692: 2006 | Description: T304 SS Vertical Cone roof. & Bottom on legs. SN: 23/6947001 Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: TIRA NDA Capacity: 44,064 Litres Compartments: 1 | Name: Ethanol Class(es): 3.1B | CROWN SHEETMETAL LIMITED 32 Spey Street, West Invercargill, Invercargill, 9810 32 Spey Street, West Invercargill, Invercargill, 9810 | The tank is to be installed at The Gin Company TA Scapegrace Distillery, Bendigo Cromwell. | 2073-07-04
TNK20261 | 2023-07-31 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3335 Single Skin HDPE 2200mm DIA x 2400mm HOA x 12/24 mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plastics Construction WW-79-TK-01 GA Name of Designer: Mech Eng Limited Capacity: 7500 litres Compartments: 1 | Name: Acetic acid 49% Class(es): 6.1D, 6.9B, 8.1A, 8.2C, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland, 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 | 2028-07-31
TNK20262 | 2023-07-31 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3332 Single Skin HDPE 1800mm DIA x 2400mm HOA x 12/24 mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plastics Construction W-81-TK-01 GA Name of Designer: Mech Eng Limited Capacity: 5000 litres Compartments: 1 | Name: Sulphuric acid 20% sg 1.14 Class(es): 8.1A, 8.2A, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland, 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 | 2028-07-31
TNK20263 | 2023-07-31 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3334 Single Skin HDPE 2200mm DIA x 2400mm HOA x 12/24 mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plastics Construction WW-74-TK-01 GA Name of Designer: Mech Eng Limited Capacity: 7500 litres Compartments: 1 | Name: Sodium hydroxide (Caustic soda) 30% w/w aqueous solution Class(es): 6.1D, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland, 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 | 2028-07-31
TNK20264 | 2023-07-31 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3333 Single Skin HDPE 1800mm DIA x 2400mm HOA x 12/24 mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plastics Construction W-75-TK-31 GA Name of Designer: Mech Eng Limited Capacity: 5000 litres Compartments: 1 | Name: Sodium hypochlorite 10% w/w aqueous solution Class(es): 8.2A, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland, 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 | 2028-07-31
TNK20265 | 2023-08-07 | Carlyon Civil Construction | Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | UL 2085 :1997 UL 142: 2006 | Description: 2HR-FR-SC-PED Tank Range Design Specification: UL 2085: 1997, UL 142: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: Carlyon 2HR-FR-SC-PED Tank Assembly sheets 1-3 Name of Designer: Carlyon Civil Construction Capacity: 1200-110000 litres Compartments: 1 | Name: Petroleum Products, Flammable Liquids Class(es): 3.1A, 3.1B, 3.1C, 3.1D | CARLYON CIVIL CONSTRUCTION LIMITED 3 Ellis Street, Frankton, Hamilton, 3204 | All tank variations are constructed to UL142: 2006 Tank design verified 2 hour fire rated to UL2085: 1997 Dimensions and nozzles of variants are according to Carlyon Civil Construction Drawings 2HR-FR-SC-PED Tank Assembly sheets 1-3 | 2028-08-07 | FAB0083
TNK20266 | 2023-08-16 | MHM Automation |  | AS1692: 2006 | Description: 55,730 Litres above ground single skinned vertical cylindrical stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 30164-01-00, Date: 13/07/203, Rev 8 &30164-02-00, Date: 9/08/2023, Rev 3 Name of Designer: MHM Automation - R.Brewitt Capacity: 55,730 Litres Compartments: 1 | Name: Dilute CCA 1-6% Class(es): 6.1D, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 6.9B, 8.3A | MHM AUTOMATION LIMITED (MERCERSTAINLESS LIMITED) 53 Lunns Road, Middleton, Christchurch 8024 | Compliant with As 1692:2006, Category 5. Producer statement - In respect of seismic design of new tanks (excluding foundations), issued by Kotahi Studio Limited, Job No.: S2002359, signed by Adam Walker (CPEng No.: 1003749), dated 17/07/2023. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2028-08-16 | FAB0077
TNK20267 | 2023-08-14 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: Z-100677-T1 - Z Takanini GRP Double Skinned 6.1m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-100677-T1-95-F105; Z-100677-T1-95-F106 Name of Designer: Tankreline NZ Limited Capacity: 28,641 litres; SFL 27,000itres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 166-168 Great South Road, Conifer Grove, Takanini 2112 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-08-14
TNK20268 | 2023-08-14 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: Z-100677-T2 - Z Takanini GRP Double Skinned 11.6m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-100677-T2-91-F101; Z-100677-T2-91-F102 Name of Designer: Tankreline NZ Limited Capacity: 49,439 litres; SFL 47,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 166-168 Great South Road, Conifer Grove, Takanini 2112 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-08-14
TNK20269 | 2023-08-14 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: Z-100677-T3 - Z Takanini GRP Double Skinned 9.3m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-100677-T3-ADO-F103; Z-100677-T3-ADO-F104 Name of Designer: Tankreline NZ Limited Capacity: 39,977 litres; SFL 38,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 166-168 Great South Road, Conifer Grove, Takanini 2112 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-08-14
TNK20270 | 2023-08-14 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: NPD-Brightwater-T1 GRP Double Skinned 3.2m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: NPD-T1-95-F101; NPD-T1-95-F102; NPDTK-107 Name of Designer: Tankreline NZ Limited Capacity: 14,126 litres; SFL 13,400 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Nelson Petroleum Distributors Limited 34 Ellis Street, Conifer Grove, Brightwater 7022 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-08-14
TNK20271 | 2023-08-14 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: NPD-Brightwater-T2 GRP Double Skinned 4.1m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: NPD-T2-91-F103; NPD-T2-91-F104; NPDTK-107 Name of Designer: Tankreline NZ Limited Capacity: 18,737 litres; SFL 17,800 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Nelson Petroleum Distributors Limited 34 Ellis Street, Conifer Grove, Brightwater 7022 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-08-14
TNK20272 | 2023-08-14 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: NPD-Brightwater-T3 GRP Double Skinned 4.7m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: NPD-T3-ADO-F105; NPD-T3-ADO-F106; NPD-TK-107 Name of Designer: Tankreline NZ Limited Capacity: 20,872 litres; SFL 19,800 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Nelson Petroleum Distributors Limited 34 Ellis Street, Conifer Grove, Brightwater 7022 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2023-08-14
TNK20273 | 2023-08-17 | Carlyon Civil Construction | Carlyon Civil Construction Ltd PO Box 10092 Te Rapa, Hamilton, 3241 12 - 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692:2006 SWI Reduced Secondary Containment for Tanks | Description: DS-DC-PED-OG Tank Range Design Specification: AS 1692:2006 SWI Reduced Secondary Containment for Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Carlyon DS-DC-PED-OG Tank Assembly sheets 1-4 Name of Designer: Carlyon Civil Construction Capacity: 1200-110000 litres Compartments: 2 | Name: Flammable Liquids Class(es): 3.1A, 3.1B, 3.1C, 3.1D | CARLYON CIVIL CONSTRUCTION LIMITED 3 Ellis Street, Frankton, Hamilton, 3204 | Dimensions and nozzles of variants are according to Carlyon Civil Construction Drawings DS-DC-PED-OG Tank Assembly sheets 1-4 | 2028-08-17 | FAB0083
TNK20274 | 2023-08-25 | Maskell Productions |  | AS 2634: 1983 | Description: 49-02-TK-2023/76: FRP (D411 VE Resin/BPO Cure) 4m Dia x 6.775m High x (10.5mm / 8 mm) WT Design Specification: AS 2634: 1983 Tank Type: Above Ground Stationary Tank Drawing Numbers: Maskell 2350-70-00 rev-1 Name of Designer: Maskell Productions Capacity: 74141 L | Name: Sodium hypochlorite 15% aqueous solution Class(es): 8.2C, 8.3A | MASKELL PRODUCTIONS LIMITED 24 Bowden Road, Mount Wellington, Auckland, 1060 | Tank Design Parameters in accordance with Maskell Design Report J21848 Tank to be constructed in accordance with Maskell Productions Limited ISO9001 Quality Systems Manual. Maximum density 1.23 s.g. Free venting 150mm NB satisfies API2000 for flow rates of 24 m3/hr Atmospheric pressure Minimum Temperature 5C Maximum Temperature 50C | 2028-08-25
TNK20275 | 2023-08-25 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3260 Single Skin HDPE 3500mm DIA x 3942mm HOA x 45/25 mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: CHEMFEED 402582/01/01 rev H Name of Designer: Mech Eng Limited Capacity: 30000 litres Compartments: 1 | Name: Poly Aluminium Chloride (PAC) aqueous solution Class(es): 6.1D | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design in accordance with Mech Eng 221901-RP01- rev0 | 2028-08-25
TNK20276 | 2023-08-25 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3261 Single Skin HDPE 3500mm DIA x 3942mm HOA x 45/25 mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: CHEMFEED 402582/01/02 rev H Name of Designer: Mech Eng Limited Capacity: 30000 litres Compartments: 1 | Name: Poly Aluminium Chloride (PAC) aqueous solution Class(es): 6.1D | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design in accordance with Mech Eng 221901-RP01- rev0 | 2028-08-25
TNK20277 | 2023-12-21 | Contract Mechanical Services Limited | CONTRACT MECHANICAL SERVICES LIMITED 11 Harvard Way, Mount Maunganui, 3116 FAB0097 |  | Description: Sulphuric Acid Tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Name of Designer: Contract Mechanical Services Limited Capacity: Nominal volume up to 45m3 Maximum fill level: 4.185m | Name: 98% sulphuric acid Class(es): 6.1D, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A | CONTRACT MECHANICAL SERVICES LIMITED 11 Harvard Way, Mount Maunganui, 3116 |  | 2033-12-21 | FAB0097
TNK20278 | 2023-09-06 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3315 Bunded HDPE 2500mm DIA x 2812mm HOA x 15 mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: CHEMFEED 403842/02/200 rev D Name of Designer: Mech Eng Limited Capacity: 10000 litres Compartments: 1 | Name: Aluminium sulphate aqueous solution 1.33 s.g. Class(es): 6.1D, 8.1A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design in accordance with Mech Eng 231651-RP01- revA | 2028-09-06
TNK20279 | 2023-09-06 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3316 Bunded HDPE 2200mm DIA x 2565mm HOA x 24/12 mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: CHEMFEED 403842/01/200 rev E Name of Designer: Mech Eng Limited Capacity: 7000 litres Compartments: 1 | Name: Acetic acid 49% s.g. 1.025 Class(es): 6.1D, 6.9B, 8.1A, 8.2C, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design in accordance with Mech Eng 231653-RP01- rev B | 2023-09-06
TNK20280 | 2023-09-13 | Martin Engineering (PN) Limited | Martin Engineering (Palmerston North) Ltd. PO Box 5295, Terrace End, Palmerston North, 4441 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 FAB0045 | AS1692: 2006 FAB0045 | Description: 18,430 Litres above ground single skinned vertical cylindrical stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 0580-000, 15k Concentrate, Rev Draft 01,Date: 03/07/2023 Name of Designer: Martin Engineering (PN) Limited Capacity: 18,430 Litres Compartments: 1 | Name: MCA or CCA (1-6%) Class(es): 6.1A, 6.1B, 6.1C, 6.1D, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 6.8B, 6.9A, 6.9B, 8.1A, 8.2B, 8.3A | MARTIN ENGINEERING (PN) LIMITED 891 Tremaine Avenue, Roslyn, Palmerston North 4414 | Approved for drawings: - Dwg No.: 0539-910, Foot ASM – VertTank, Rev 01, Date: 20/06/2022 – Corrected 5/07/2023 - Dwg No.: 0539-920, Lift Lug ASM – VertTank, Rev 02, Date: 24/01/2023 - Dwg No.: 0539-930, Manway ø600, Rev 01, Date: 9/01/2023 - Dwg No.: 0539-930a, Manway Portal ASM ø600, Rev 01, Date: 7/07/2022 - Dwg No.: 0539-930b, Manway Lid ASM ø600, Rev 01, Date: 21/06/2022 - Dwg: Nameplate Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2028-09-13 | FAB0045
TNK20281 | 13/09/2023 29/01/2025 (renewed) | Martin Engineering (PN) Limited | Martin Engineering (Palmerston North) Ltd. PO Box 5295, Terrace End, Palmerston North, 4441 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 FAB0045 | AS1692: 2006 FAB0045 | Description: 24,321 Litres above ground single skinned vertical cylindrical stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers:0553-100, Sheet 1 & 2, Micthpine 20,000ltr Tank, Rev Draft 06, Date:20/06/2022 – Corrected 5/07/23 Name of Designer: Martin Engineering (PN) Limited Capacity: 24,321 Litres Compartments: 1 | Prior to 29/01/2025 Name: MCA or CCA (1-6%) Class(es): 6.1A, 6.1B, 6.1C, 6.1D, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 6.8B, 6.9A, 6.9B, 8.1A, 8.2B, 8.3A As of 29/01/2025: Name: MCA or CCA (1-6%) Class(es): 6.1A, 6.1B, 6.1C, 6.1D, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 6.8B, 6.9A, 6.9B, 8.1A, 8.2B, 8.3A Name: Tanalith C Oxide Class(es): 6.1B, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 8.1A, 8.2B, 8.3A | MARTIN ENGINEERING (PN) LIMITED 891 Tremaine Avenue, Roslyn, Palmerston North 4414 | Approved for the storage and transfer of MCA or CCA 1-6% or Tanalith C Oxide, having a hazard classification of 6.1A, 6.1B, 6.1C, 6.1D, 6.3A, 6.5A, 6.5B, 6.6A, 6.7A,6.8A, 6.8B, 6.9A, 6.9B, 8.1A, 8.2B, 8.3A, 9.1A, 9.1B, 9.1C, 9.2B, 9.2C, 9.3A, 9.3C, 9.4C. Compliant with AS1692:2006, Category 5. Design statement – 7513-1005 – In Respect Of: 20kL Chemical Tank, Issued To: Martin Engineering, Signed by: Joseph Bain (CPEng No.: 248672),Dated: 23/01/2025. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2028-09-13 | FAB0045
TNK20282 | 2023-09-11 | Martin Engineering | Martin Engineering (Palmerston North) Ltd. PO Box 5295, Terrace End, Palmerston North, 4441 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 FAB0045 | AS1692: 2006 FAB0045 | Description: 3 x Vertical Cone Roof C.S. single skin tanks for =<1.85 S.G. Design Specification: AS 1692:2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 0542-000-Sht1/Sht2/Sht3; 0539-000; 0539-910; 0539-920;/-930;/-930a;/-930b; 0539-936; 0539-100 Name of Designer: Martin Engineering Capacity: 61,072 litres, 48,858 litres, 36,643 litres Compartments: 1 | Name: MCA & CCA (Tanalith C Oxide) Class(es): 6.1B, 6.1C, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 6.9A, 8.1A, 8.2B, 8.3A | MARTIN ENGINEERING (PN) LIMITED 891 Tremaine Avenue, Roslyn, Palmerston North 4414 | This Design Certificate is for 3 tanks all 3.600 mtrs in diameter with varied heights primarily designed for timber treatment products of S.G up to 1.8. The design may be used for other chemical products of equal or lesser SG provided the chemical characteristics are compatible with Carbon Steel. | 2073-09-11 | FAB0045
TNK20283 | 2021-11-22 | TRL Engineering Pty Ltd |  | UL 1316:1994 (2nd Edition) | Description: Z-103705-T1 - Z Te Rapa, Pukete Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-103705-T1 Name of Designer: TRL Engineering Pty Ltd Capacity: 30,000 litres | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 175 Roydvale Avenue, Burnside, Christchurch 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2026-11-22
TNK20284 | 2021-11-22 | TRL Engineering Pty Ltd |  | UL 1316:1994 (2nd Edition) | Description: Z-103705-T2 - Z Te Rapa, Pukete Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-103705-T2 Name of Designer: TRL Engineering Pty Ltd Capacity: 50,000 litres | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 175 Roydvale Avenue, Burnside, Christchurch 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2026-11-22
TNK20285 | 2021-11-22 | TRL Engineering Pty Ltd |  | UL 1316:1994 (2nd Edition) | Description: Z-103705-T3 - Z Te Rapa, Pukete Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-103705-T3 Name of Designer: TRL Engineering Pty Ltd Capacity: 40,000 litres | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 175 Roydvale Avenue, Burnside, Christchurch 8053 | FIELD CONSTRUCTED TANK; CONSTRUCTION VERIFIED; Satisfies requirements of Regulation 17.91(2)(b)(i), 17.91(2)(b)(ii) & 17.91(2)(b)(iii) DOUBLE SKIN GRP, CONTINUOUS INTERSTITIAL MONITORING | 2026-11-22
FAB0095 | 2023-08-12 |  | ETECH NZ LIMITED 130 Kaimanawa Street, Kelvin Grove, Palmerston North 4414 |  | Approved for the shop fabrication of steel tanks in accordance with BS EN 12285.3 2019 for Classes 3.1B, 3.1C hazardous substances for which TNK numbers (TNK20194, TNK20195, TNK20196) have been registered with WorkSafe New Zealand. Allocation of unique individual tank serial number to be stamped on each individual tank and recorded. Retention of individual tank fabrication, testing records and QA records for each tank. Capacity: 50,273 Litres | Butyl Acrylate Class(es): 3.1C, 6.1C, 6.5B, 6.9B Methyl Methacrylate Class(es): 3.1B, 6.7B, 6.8B, 6.9B Styrene Class(es): 3.1C, 6.1D, 6.8B, 6.9A | ETECH NZ LIMITED 130 Kaimanawa Street, Kelvin Grove, Palmerston North 4414 | The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the compliance certifier who issued the compliance certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2026-08-12 | Fabricator of: TNK20194, TNK20195, TNK20196
TNK20286 | 2023-09-18 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: 400418-T3: GRP Double skin 8750mm LOA x 2480mm DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: TRL-DRW-XMH-T3-91 Name of Designer: Tankreline NZ Limited Capacity: 39600 L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 481 Featherston Street, Palmerston North 4414 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-09-18
TNK20287 | 2023-10-15 | Robin King Engineers Ltd. |  | API Standard 650 | Description: 45 kL boron concentrate tank 1. Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: S015-S-002 144 Rev 03. Name of Designer: Robin King Engineers Ltd. Capacity: 45,000 L Compartments: 1 | Name: Frame Pro timber treatment HSR 000907. Class(es): 6.1D, 8.3A | CONTRACT MECHANICAL SERVICES LIMITED 11 Harvard Way, Mt Maunganui, Tauranga 3116 | Tank serial number Tank 1 CMS201, 4BO-TNK-0016. 45,000 Litre 304L grade stainless steel tank to API650 Annex S and Annex J. Contract Mechanical Services QA Pack Boron concentrate tank 4BO-TNK-0016 DATED June 2022 : Rev 1. Design temperature -10 to +40 deg C. O.D. 3.8m x 4.515m high x 5mm strakes. Joint efficiency 0.7 (no radiography). Safe fill height 3.983m. High level alarm 4.155m. Hi hi level alarm 4.327m. Roof pitch 10 degrees. Top curb channel 50x50x6 mm. Design life 50 years. Location Red Stag Timber, State Mill Road, Waipa, Rotorua. Wind and seismic design to NZS 1170.2 and NZS1170.5, NZSEE:2009 Robin King Engineers Ltd report dated 1 Nov 2021. Seismic zone 0.24. Maximum specific gravity 1.232, tank designed for specific gravity 1.6.Sp = 1.0. Site subsoil Class D. Tank design pressure 3 kPa. Design vacuum - 0.25 kPa. Venting to API2000, AS1940. Maximum fill rate 500 litres / minute. Maximum pump out rate 500 litres / minute. 100 NB Sch 10 gooseneck natural vent fitted with drip collection plate with 15 NB condensate drip return pipe. Anchoring 8 M24 anchors on 3.92 m PCD. 190 mm minimum embedment with Ramset Epcon C6 grout. Minimum concrete thickness at anchors 242 mm. Minimum edge distance 150 mm. Concrete strength 32 MPa. | 2028-10-15
TNK20288 | 2023-10-15 | Robin King Engineers Ltd |  | API Standard 650 | Description: 45 kL process tank 4BO-TNK-0017 Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: S015-S-002145 Rev 03 Name of Designer: Robin King Engineers Ltd Capacity: 45,000 L Compartments: 1 | Name: Frame Pro timber treatment HSR 000907. Class(es): 6.1D, 8.3A | CONTRACT MECHANICAL SERVICES LIMITED 11 Harvard Way, Mt Maunganui, Tauranga 3116 | Tank serial number Tank 2 CMS202, 4BO-TNK-0017. 45,000 Litre 304L grade stainless steel tank to API650 Annex S and Annex J. Contract Mechanical Services QA Pack Boron concentrate tank 4BO-TNK-0016 DATED June 2022 : Rev 1. Design temperature -10 to +40 deg C. O.D. 3.8m x 4.515m high x 5mm strakes. Joint efficiency 0.7 (no radiography). Safe fill height 3.983m. High level alarm 4.155m. Hi hi level alarm 4.327m. Roof pitch 10 degrees. Top curb channel 50x50x6 mm. Design life 50 years. Location Red Stag Timber, State Mill Road, Waipa, Rotorua. Wind and seismic design to NZS 1170.2 and NZS1170.5, NZSEE:2009 Robin King Engineers Ltd report dated 3 Nov 2021. Seismic zone 0.24. Maximum specific gravity 1.232, tank designed for specific gravity 1.6. Sp = 1.0. Site subsoil Class D. Tank design pressure 3 kPa. Design vacuum - 0.25 kPa. Venting to API2000, AS1940. Maximum fill rate 500 litres / minute. Maximum pump out rate 500 litres / minute. 100 NB Sch 10 gooseneck natural vent fitted with 15 NB condensate drip return pipe. Anchoring 8 M24 anchors on 3.92 m PCD. 190 mm minimum embedment with Ramset Epcon C6 grout. Minimum concrete thickness at anchors 242 mm. Minimum edge distance 150 mm. Concrete strength 32 MPa. | 2028-10-15
TNK20289 | 2023-10-15 | Robin King Engineers Ltd. |  | API Standard 650 | Description: 45 kL recirculating process tank 3 4BO-TNK-0018. Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: S015-S-002146 Rev 03. Name of Designer: Robin King Engineers Ltd. Capacity: 45,000 L. Compartments: 1 | Name: Frame Pro timber treatment HSR 000907 Class(es): 6.1D, 8.3A | CONTRACT MECHANICAL SERVICES LIMITED 11 Harvard Way, Mt Maunganui, Tauranga 3116 | Tank serial number Tank 3 CMS203, 4BO-TNK-0018. 45,000 Litre 304L grade stainless steel tank to API650 Annex S and Annex J. Contract Mechanical Services QA Pack Recirculating Process Tank 4BO-TNK-0018 DATED June 2022 : Rev 1. Design temperature -10 to +40 deg C. O.D. 3.8m x 4.515m high x 5mm strakes. Joint efficiency 0.7 (no radiography). Safe fill height 3.983m. High level alarm 4.155m. Hi hi level alarm 4.327m. Roof pitch 10 degrees. Top curb channel 50x50x6 mm. Design life 50 years. Location Red Stag Timber, State Mill Road, Waipa, Rotorua. Wind and seismic design to NZS 1170.2 and NZS1170.5, NZSEE:2009 Robin King Engineers Ltd report dated 10 Nov 2021. Seismic zone 0.24. Maximum specific gravity 1.232, tank designed for specific gravity 1.6. Sp = 1.0. Site subsoil Class D. Tank design pressure 3 kPa. Design vacuum - 0.25 kPa. Venting to API2000, AS1940. Maximum fill rate 500 litres / minute. Maximum pump out rate 500 litres / minute. 100 NB Sch 10 gooseneck natural vent fitted with drip collection plate with 15 NB condensate drip return pipe. Anchoring 8 M24 anchors on 3.92 m PCD. 190 mm minimum embedment with Ramset Epcon C6 grout. Minimum concrete thickness at anchors 242 mm. Minimum edge distance 150 mm. Concrete strength 32 MPa. | 2028-10-15
TNK20290 | 2023-09-25 | Plaspoke Limited / Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: 0113-PLASCT-01 Self Bunded HDPE Chemical Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: 0113-PLASCT-01(HYPO TANK) Sheets 1-5 Name of Designer: Plaspoke Limited / Mech Eng Limited Capacity: 7000 litres Compartments: 1 | Name: Sodium hypochlorite 15% aqueous solution Class(es): 8.2B, 8.3A | Plaspoke Limited 35 Saleyards Road, Otahuhu, Auckland 1062 | To be manufactured in accordance with Plaspoke QA Documents QA-0113-PLASCT-01 | 2028-09-25
TNK20291 | 2023-09-26 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: Z-104056-T1 - Z Lakewood Court GRP Double Skinned 9.4m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-104056-T1-95-F101; Z-104056-T1-95-F102 Name of Designer: Tankreline NZ Limited Capacity: 40,951 litres; SFL 38,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 742 Great South Road, Manukau, Auckland 2104 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-09-26
TNK20292 | 2023-09-26 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: Z-104056-T3 - Z Lakewood Court GRP Double Skinned 9.4m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-104056-T3-ADO-F103; Z-104056-T3-ADO-F104 Name of Designer: Tankreline NZ Limited Capacity: 40,141 litres; SFL 38,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 742 Great South Road, Manukau, Auckland 2104 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-09-26
TNK20293 | 2023-10-03 | Plaspoke Limited / Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: 5000L-HFA-IL3- HDPE 2044mm HOA x 1900mm DIA x 12mm WT Design Specification: BS EN 12573 SWI Thermoplasic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: 5000L HFA Tank (IL3) Sheets 1-5 Rev B Name of Designer: Plaspoke Limited / Mech Eng Limited Capacity: 5000 L Compartments: 1 | Name: HYDROFLUOROSILICIC ACID 1.22sg Class(es): 8.2C, 8.3A | Plaspoke Limited 35 Saleyards Road, Otahuhu, Auckland 1062 | To be manufactured in accordance with Plaspoke QA Documents QA-PLASCT-IL3 | 2028-10-03
TNK20294 | 2023-10-06 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3344 Single Skin HDPE 1800mm DIA x 2850mm HOA x 24/12 mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering 3288-013 Name of Designer: Mech Eng Limited Capacity: 5,827 L total, 5547 L SFL Compartments: 1 | Name: Citric acid 50% aqueous solution 1.25 s.g. Class(es): 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design in accordance with Mech Eng Report 231892-RP01-RevA 13.06.2025 Certificate amended as follows - 5000 litres changed to 5827 litres maximum, 5547 litres SFL | 2028-10-06
TNK20295 | 2023-10-12 | Carlyon Civil Construction | Carlyon Civil Construction Ltd 12 & 15 Manchester Place Te Rapa Hamilton 3200 FAB0083 | AS 1692 SWI Reduced Secondary Containment for Tanks | Description: DS-MC-PED-AG Tank Range Design Specification: AS 1692 SWI Reduced Secondary Containment for Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Carlyon DS-MC-PED-AG Tank Assembly sheets 1-4 Name of Designer: Carlyon Civil Construction Capacity: 1200-110000 litres Compartments: 5 | Name: Diesel & Combustible liquids AS1940 C1/C2 Flammable Liquids Class(es): 3.1D 3.1A, 3.1B, 3.1C | CARLYON CIVIL CONSTRUCTION LIMITED 3 Ellis Street, Frankton, Hamilton, 3204 | Dimensions, nozzles, and compartments of variants are according to Carlyon Civil Construction Drawings DS-MC-PED-AG Tank Assembly sheets 1-4 | 2028-10-12 | FAB0083
FAB0096 | 2023-10-17 |  | PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 |  | Tank design code: AS1692-2006 Tank details: Steel tanks up to maximum capacity of 60,000 litres Reference: TNK12005, TNK12006, TNK12007, TNK12008, TNK12009, TNK12010, TNK13023, TNK13027, TNK13057, TNK13078, TNK15004, TNK16009, TNK16015, TNK16016, TNK17000, TNK18003, TNK18004, TNK18036, TNK20007, TNK20082 & TNK20227 | Class 3.1A, B, C or D hazardous substances | PROTANK INDUSTRIES LIMITED 291 Tremaine Avenue, Highbury, Palmerston North, 4412 PO Box 10125 Phillipstown Christchurch 8145 | Fabrication, inspection and testing in accordance with the specified tank design and fabrication code, approved tank design drawings and approved for construction drawings. Allocation of unique individual tank serial number to be stamped on each individual tank and recorded. Retention of individual tank fabrication, testing records and QA records for each tank. WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the compliance certifier who issued the compliance certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2026-10-17 | Fabricator of: TNK12005, TNK12006, TNK12007,TNK12008, TNK12009, TNK12010,TNK13023, TNK13027, TNK13057,TNK13078, TNK15004, TNK16009,TNK16015, TNK16016, TNK17000,TNK18003, TNK18004, TNK18036,TNK20007, TNK20082, TNK20227.
TNK20296 | 2023-10-17 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3313 Self=bunded HDPE 3100mm DIA x 3375mm HOA x 15/30mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Chemfeed DWG 404050/01/01-revA Name of Designer: Mech Eng Limited Capacity: 19000 litres Compartments: 1 | Name: Aluminium sulphate aqueous solution 1.33 s.g. Class(es): 6.1D, 8.1A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design in accordance with Mech Eng Report231641-RP01-RevA | 2028-10-17
TNK20297 | 2023-10-20 | Maskell Productions |  | UL 1316:1994 (2nd Edition) | Description: Model100KL-PNT: GRP Double-skinned 3.0m DIA x 14.85m LOA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Maskell 1037.100.70 rev 2 Name of Designer: Maskell Productions Capacity: 100,000 litres | Name: Cyclo-pentane Class(es): 3.1B Name: Flammable liquids compatible with the GRP resin Class(es): 3.1A, 3.1B, 3.1C, 3.1D Name: Petroleum fractions with vapour pressure not exceeding 45kPa(a) @ 20C Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MASKELL PRODUCTIONS LIMITED 24 Bowden Road, Mount Wellington, Auckland 1060 | Tank fitted with permanent Hydra-guard interstitial monitor Tank to be installed in accordance with UPSS Sections 12.8, 12.9, & 16 Tank to be manufactured by a UL1316 Approved Fabricator Tank manufactured to UL1316:2013 (3rd Edition) deemed to comply with UL1316:1994 (2nd Edition) For products with vapour pressure exceeding 35kPa(a) tank to be fitted with two independent 4" (100mm NB) Pressure Vacuum vents | 2028-10-20
TNK20298 | 2023-10-18 | Plaspoke Limited / Mech Eng Limited | Plaspoke Limited 35 Saleyards Road, Otahuhu, Auckland 1062 FAB0094 | BS EN 12573 SWI Thermoplastic Tanks | Description: PLASCT-V2-01 HDPE Chemical Tank Range Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: PLASCT-V2-01 (HDPE Chemical Tanks) (Sheets 1-6) Rev D Name of Designer: Plaspoke Limited / Mech Eng Limited Capacity: 5000-20000 L Compartments: 1 | Name: Chemicals Range Maximum product density 1.660 sg. Class(es): 6.1A, 6.1B, 6.1C, 6.1D, 6.5A, 6.5B, 6.6A, 6.6B, 6.7A, 6.7B, 6.8A, 6.8B, 6.8C, 6.9A, 6.9B, 8.1A, 8.2A, 8.2B, 8.2C, 8.3A | Plaspoke Limited 35 Saleyards Road, Otahuhu, Auckland 1062 | Design in accordance with Mech Eng Limited Design Report 231970-RP01-RevA incorporating Reports 231971, 231972, 231973, 231974, 231975, & 231976 Variation of dimensions and volumes is according to table "Tank Design Size Guide" on page 4 of the drawing set Chemical compatibility must be demonstrated for any specific application according to the limits imposed by BS-EN-12573 SWI-2017 Thermoplastic Tanks | 2028-10-18 | FAB0094
TNK20299 | 2023-10-25 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: 1000798-T1 GRP Double Skinned 11.7m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: 1000798-T1-91-F101; 1000798-T1-91-F102 Name of Designer: Tankreline NZ Limited Capacity: 51727 litres; SFL 49,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | WAIKAWA MARINA HOLDINGS LIMITED 80 Beach Road, Waikawa, Picton 7220 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-10-25
TNK20300 | 2023-10-25 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: Z-104056-T2 - Z Lakewood Court GRP Double Skinned 9.6m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-104056-T2-91-F105; Z-104056-T2-91- F106 Name of Designer: Tankreline NZ Limited Capacity: 40,090 litres; SFL 38,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 742 Great South Road, Manukau, Auckland 2104 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-10-25
TNK20301 | 2023-10-26 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: Z-101359-T2 - Z Gisborne GRP Double Skinned 9.6m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-101359-T2-91-F101; Z-1010359-T2-91- F102 Name of Designer: Tankreline NZ Limited Capacity: 40,090 litres; SFL 38,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 300 Gladstone Road, Manukau, Gisborne 4010 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has permanent hydroguard interstitial monitoring.. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-10-26
TNK20302 | 2023-10-26 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: Z-101359-T3 - Z Gisborne GRP Double Skinned 9.24m LOA x 2.37m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-101359-T3-ADO-F103; Z-1010359-T3- ADO-F104 Name of Designer: Tankreline NZ Limited Capacity: 39257 litres; SFL 37,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 300 Gladstone Road, Manukau, Gisborne 4010 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has permanent hydroguard interstitial monitoring.. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-10-26
TNK20303 | 2023-10-26 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: 400418-T1: GRP Double skin 8680mm LOA x 2480mm DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: TRL-DRW-XMH-T1-98 Name of Designer: Tankreline NZ Limited Capacity: 39800 L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 481 Featherston Street, Palmerston North 4414 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has Hydroguard permanent interstitial monitoring system Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-10-26
TNK20304 | 2023-10-26 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: 400418-T2: GRP Double skin 8660mm LOA x 2480mm DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: TRL-DRW-XMH-T2-91 Name of Designer: Tankreline NZ Limited Capacity: 39600 L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 481 Featherston Street, Palmerston North 4414 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has Hydroguard permanent interstitial monitoring system Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-10-26
TNK20305 | 2013-11-13 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3342 Single Skin HDPE 2500mm DIA x 3710mm HOA x 40/20 mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering-DWG 4894-002 rev C Name of Designer: Mech Eng Limited Capacity: 17843 litres 17,000 litres SFL Compartments: 1 | Name: HYDROFLUOROSILICIC ACID 1.22sg Class(es): 8.2C, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 | 2028-11-13
TNK20306 | 2023-11-20 | AZELIS NEW ZEALAND LIMITED (TIMTECH CHEMICALS LIMITED) | Nymic Engineering Limited FAB0023 | AS1692: 2006 | Description: 6,805 litres above ground single skinned vertical cylindrical stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 6805-01, Sheets 1 to 7, Rev A, CCA conc tank, Date: 15/11/2023 Name of Designer: AZELIS NEW ZEALAND LIMITED (TIMTECH CHEMICALS LIMITED) - Luke Spring Capacity: 6,805 L Compartments: 1 | Name: TimTech CX Oxide Concentrate Class(es): 6.1B, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 6.9A, 8.1A, 8.2B, 8.3A | AZELIS NEW ZEALAND LIMITED (TIMTECH CHEMICALS LIMITED) 106G Carmen Road, Hornby, Christchurch 8545 | Approved for Nymic Engineering Limited to serially produce this tank design under their FAB No.: FAB0023. The storage and transfer of TimTech CX Oxide Concentrate, having a hazard classification of 6.1B, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 6.9A, 8.1A, 8.2B, 8.3A, 9.1A, 9.2B, 9.3A, 9.4C. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2033-11-20 | FAB0023
TNK20307 | 2023-11-16 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: 400418-T4: GRP Double skin 8680mm LOA x 2480mm DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: TRL-DRW-XMH-T4-D Name of Designer: Tankreline NZ Limited Capacity: 39800 litres / 37,800 litres SFL Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 481 Featherston Street, Palmerston North 4414 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has Hydroguard permanent interstitial monitoring system Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-11-16
TNK20308 | 2023-12-04 | MHM Automation | Mercer Stainless Limited 53 Lunns Road, Middleton Christchurch 8024 and 5 Tanya Street, Bromley, Christchurch 8062 FAB0077 | AS1692: 2006 | Description: 22,714 litres vertical cylindrical single skin jacketed flat bottom & cone roof above ground tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 30169-10-00, SHT 1 to 2, Rev 9, 20m3 Caustic Soda Storage tank, General Arrangement, Date: 27/09/23 Name of Designer: MHM Automation - S.Coldicott Capacity: 22,714 litres Compartments: 1 | Name: Caustic Soda Class(es): 6.1D, 8.1A, 8.2B, 8.3A | MHM AUTOMATION LIMITED (MERCER STAINLESS LIMITED) 53 Lunns Road, Middleton, Christchurch 8024 | Maximum Safe Fill Level = 19,518 litres. Approved For: The storage and transfer of Caustic Soda, having a hazard classification of 6.1D, 8.1A, 8.2B, 8.3A, 9.1D Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2033-12-04 | FAB0077
TNK20309 | 2023-12-04 | MHM Automation | Mercer Stainless Limited 53 Lunns Road, Middleton Christchurch 8024 and 5 Tanya Street, Bromley, Christchurch 8062 FAB0077 | AS1692: 2006 | Description: 17,805 litres vertical cylindrical single skin flat bottom & cone roof above ground stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 30169-30-00, SHT 1 & 2, Rev 9, 15m3 Sulphuric Acid Storage tank, Genera lArrangement, Date: 26/09/23 Name of Designer: MHM Automation - S.Coldicott Capacity: 17,805 litres Compartments: 1 | Name: Sulphuric Acid Class(es): 6.1D, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A | MHM AUTOMATION LIMITED (MERCER STAINLESS LIMITED) 53 Lunns Road, Middleton, Christchurch 8024 | Maximum Safe Fill Level = 15,089 litres Approved For: The storage and transfer of Sulphuric Acid, having a hazard classification of 6.1D, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A, 9.1C. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2033-12-04 | FAB0077
TNK20310 | 2023-12-04 | MHM Automation | Mercer Stainless Limited 53 Lunns Road, Middleton Christchurch 8024 and 5 Tanya Street, Bromley, Christchurch 8062 FAB0077 | AS1692: 2006 | Description: 22,714 litres vertical cylindrical single skin flat bottom & cone roof above ground stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 30169-20-00, SHT 1 to 2, Rev 9, 20m3 Nitric Acid Storage tank, General Arrangement, Date: 27/09/23 Name of Designer: MHM Automation - S.Coldicott Capacity: 22,714 litres Compartments: 1 | Name: Nitric Acid Class(es): 6.1D, 6.9B, 8.1A, 8.2B, 8.3A | MHM AUTOMATION LIMITED (MERCER STAINLESS LIMITED) 53 Lunns Road, Middleton, Christchurch 8024 | Maximum Safe Fill Level = 19,518 litres Approved For: The storage and transfer of Nitric Acid, having a hazard classification of 6.1D, 6.9B, 8.1A, 8.2B, 8.3A. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure testin kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2033-12-04 | FAB0077
FAB0097 | 2023-12-18 |  | CONTRACT MECHANICAL SERVICES LIMITED 11 Harvard Way, Mount Maunganui, 3116 |  | Above ground single skin tank, carbon or stainless steel up to 60,000 L for which a TNK number has been issued. Reference: TNK20277 |  | CONTRACT MECHANICAL SERVICES LIMITED 11 Harvard Way, Mount Maunganui, 3116 | The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the compliance certifier who issued the compliance certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2026-12-18 | Fabricator of: TNK20277
TNK20311 | 2023-12-15 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: 1000798-T2 GRP Double Skinned 4.58m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: 1000798-T2-95-F103 1000798-T2-95-F104 Name of Designer: Tankreline NZ Limited Capacity: 19,446 litres; SFL 18,400 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | PORT MARLBOROUGH NEW ZEALAND LIMITED 14 Auckland Street, Picton 7250 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-12-15
TNK20312 | 2023-12-18 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: Z-101359-T4 - Z Gisborne GRP Double Skinned 6.9m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-101359-T4-91-F107; Z-101359-T4-91- F108 Name of Designer: Tankreline NZ Limited Capacity: 28,718 litres; SFL 27,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 300 Gladstone Road, Manukau, Gisborne 4010 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has permanent hydroguard interstitial monitoring. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-12-18
TNK20313 | 2023-12-18 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: Z-101359-T1 - Z Gisborne GRP Double Skinned 6.8m LOA x 2.4m DIA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-101359-T1-95-F105; Z-101359-T1-95- F106 Name of Designer: Tankreline NZ Limited Capacity: 28,983 litres; SFL 27,500 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 300 Gladstone Road, Manukau, Gisborne 4010 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has permanent hydroguard interstitial monitoring. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-12-18
TNK20314 | 2023-12-19 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3262 Single Skin HDPE 3500mm DIA, 3942mm HOA, 25/45mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: CHEMFEED-DWG 402582/02/01 Rev J Name of Designer: Mech Eng Limited Capacity: 33,000 litres 30,000 litres SFL Compartments: 1 | Name: Aluminium sulphate aqueous solution 1.33 s.g. maximum Class(es): 6.1D, 8.1A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation Manual April 2023 - Production reference T-3262 | 2028-12-19
TNK20315 | 2023-12-19 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3263 Single Skin HDPE 3500mm DIA, 3942mm HOA, 25/45mm WT Design Specification:BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: CHEMFEED-DWG 402582/02/02 Rev J Name of Designer: Mech Eng Limited Capacity: 33,000 litres 30,000 litres SFL Compartments: 1 | Name: Aluminium sulphate aqueous solution 1.33 s.g. maximum Class(es): 6.1D, 8.1A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation Manual April 2023 - Production reference T-3263 | 2028-12-19
TNK20316 | 2023-12-19 | Maskell Productions |  | AS 2634: 1983 | Description: OR08-801TK; 3000mm DIA x 3500mm HOA x 6.9mm WT GRP 411 VE Resin Design Specification: AS 2634: 1983 Tank Type: Above Ground Stationary Tank Drawing Numbers: Maskell 2370-27-00 rev 5 Name of Designer: Maskell Productions Capacity: 27,000 litres | Name: Sodium hypochlorite 15% aqueous solution 1.4s.g. max. Class(es): 8.2C, 8.3A | MASKELL PRODUCTIONS LIMITED 24 Bowden Road, Mount Wellington, Auckland 1060 | Tank Data Plate to be attached to the tank Manufactured to Maskell Productions QA Record J21874 | 2028-12-19
TNK20317 | 2024-01-18 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3346 HDPE Single Skinned insulated. 3800 mm DIA x 3695 mm HOA x 25/45 mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering 3228-011 Name of Designer: Mech Eng Limited Capacity: 33,683 litres; SFL 32,072 litres Compartments: 1 | Name: Sodium hydroxide (Caustic soda) 50% w/w aqueous solution Class(es): 6.1D, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation Manual April 2023 - Production reference T-3346 13.06.2025 Certificate amended as follows - SFL 30,000 litres changed to SFL 32,072 litres (ASC). | 2029-01-18
TNK20318 | 2024-01-18 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3345 Single Skin HDPE 3200mm DIA, 3415mm HOA, 20/40mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering 3228-014 Name of Designer: Mech Eng Limited Capacity: 22,599 litres; SFL 21,521 litres Compartments: 1 | Name: Acetic acid 49% Class(es): 6.1D, 6.9A, 8.1A, 8.2C, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation Manual April 2023 - Production reference T-3345 13.06.2025 Certificate amended as follows - 22,499 litres; SFL 20,000 litres changed to 22,599 litres; SFL 21,521 litres. | 2029-01-18
TNK20319 | 2024-01-18 | Crown Iron Works / Tom Roberts |  | Design Verified to AS3990 and AS1210 | Description: Horizontal Solvent Extractor Model B3243, 304 S/S, 11785 mm LOA x 1999 mm H x 533 mm W x 5mm WT Design Specification: Design Verified to AS3990 and AS1210 Tank Type: Process Container Drawing Numbers: Crown Iron Works B3243-000 rev 1 Name of Designer: Crown Iron Works / Tom Roberts Capacity: 3500 litres 3286 litres SFL | Name: n-Butyl acetate Class(es): 3.1B, 3.1C, 6.1D | RESIN & WAX HOLDINGS LIMITED 214 Sandhills Road, Awanui 0483 | Engineering Design Verification by Tom Roberts of Mech Eng Limited Certificate 232011 Design Verified to AS3990 and AS1210. Crown Iron Works Design Report 2023/08/30 ver. 1 | 2029-01-18
TNK20320 | 2024-02-07 | Maskell Productions Limited |  | UL 1316:1994 (2nd Edition) | Description: D55-24023545: GRP Double-skinned 2.5m DIA x 11.8m LOA Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Maskell 2380-55-00 rev 2 Name of Designer: Maskell Productions Capacity: 55,000 L | Name: Cyclo-pentane Class(es): 3.1B Name:Flammable liquids compatible with the GRP resin Class(es):3.1A, 3.1B, 3.1C, 3.1D Name: Petroleum fractions with vapour pressure not exceeding 45kPa(a) @ 20C Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MASKELL PRODUCTIONS LIMITED 24 Bowden Road, Mount Wellington, Auckland 1060 | Tank fitted with permanent Hydra-guard interstitial monitor Tank to be installed in accordance with UPSS Sections 12.8, 12.9, & 16 Tank to be manufactured by a UL1316 Approved Fabricator Tank manufactured to UL1316:2013 (3rd Edition) deemed to comply with UL1316:1994 (2nd Edition) For products with vapour pressure exceeding 35kPa(a) tank to be fitted with two independent 4" (100mm NB) Pressure Vacuum vents | 2029-02-07 | N/A
TNK20321 | 2024-02-07 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3357 Single Skin HDPE 1700mm DIA x 2315mm HOA x 1500 WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering 5517-011 ver. 1 Name of Designer: Mech Eng Limited Capacity: 5027 L Compartments: 1 | Name: Sodium hypochlorite 15% w/w aqueous solution Class(es): 8.2A, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Tom Robert, Mech Eng Limited Report 232321-RP01-revA | 2029-02-07 | N/A
TNK20322 | 2024-02-07 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3358 Single Skin HDPE 1700mm DIA x 2315mm HOA x 1500 WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering 5517-012 ver. 1 Name of Designer: Mech Eng Limited Capacity: 5027 L Compartments: 1 | Name: Sodium hypochlorite 15% w/w aqueous solution Class(es): 8.2A, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Tom Roberts, Mech Eng Limited Report 232321-RP01-revA | 2029-02-07 | N/A
TNK20323 | 2024-02-22 | Mt Maunganui Engineering Limited |  | API Standard 650 | Description: CS Vertical Cone Roof flat bottom Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: J2023-358 M10; J2023-358 M11; J2023-358 M12 Name of Designer: Mt Maunganui Engineering, Design Calculations by 2E Consulting Tauranga. Capacity: 22,500 L Compartments: 1 | Name: 50% Caustic Soda Class(es): 6.1D, 8.1A, 8.2B, 8.3A | MOUNT MAUNGANUI ENGINEERING LIMITED 1 Mangatawa Link Road, Kairua, Papamoa 3175 | Tank is built as a one-off by Mount Maunganui Engineering for Oceana Gold Waihi. Tank site at Moresby Avenue Waihi, Tank designation is Tank 60-TNK-07. This tank replaces the previous Tank 0023. | 2074-01-31 | N/A
TNK20324 | 2024-02-28 | Fuelchief Limited | FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS1692: 2006 FAB0093 | Description: 10,688 Litres above ground single skin vertical cylindrical dome top flat bottom stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 10,000 Litre Vertical Tank, Rev B, Sheet: 1, Drawn: DL, Date: 23/02/2024 Name of Designer: Fuelchief Limited - DL Capacity: 10,688 Litres Compartments: 1 | Name: Tanalith C Oxide Class(es): 6.1B, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 8.1A, 8.2B, 8.3A | FUELCHIEF LIMITED Innovation Park Lot 15/185 Kirk Road, Templeton, Christchurch 7675 | Design statement number: 7835-1000, 10kL CCA Tank for 194 Ranzau Road, Hope, Nelson, In Respect Of: 10kL CCA Tank, Issued To: Fuelchief LTD,Drawing: 10,000 Litre Vertical Tank GA Rev 0 MDA Markup 24Jan24, Signed: Joseph Bain (CPEng 248672), Date: 26/1/2024. Tank Location: 194 Ranzau Road, Hope, Nelson. Unique serial number to be allocated for tank. Tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2034-02-28 | FAB0093
TNK20325 | 2024-02-27 | TransTank International |  | AS1692: 2006 | Description: TNTK402838-7-WADY012001-2 CONTAINERISED DOUBLE SKINNED >110% SECONDARY CONTAINMENT Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: TransTank A000436-T12 GA Name of Designer: TransTank International Capacity: 12000 litres; SFL 11020 litres Compartments: 1 | Name: Diesel & Combustible liquids AS1940 C1/C2 Class(es): 3.1D | AGGREKO (NZ) LIMITED, 1048-1050 Great South Road, Mount Wellington, Auckland, 1060 |  | 2029-02-27 | DOM 2012
TNK20326 | 2024-02-27 | Design Engineering | Zhangjiagang Fuel Equipment System Co. Ltd. 3 Haixin North Road, Nanfeng, Zhangjiagang, Jiangsu, China | AS 1692: 2006 SWI Reduced Secondary Containment for Tanks 2017 FAB0087 | From 27/02/2024: Description: GO-INDUSTRIAL STORE SERIES Design Specification: AS 1692 SWI Reduced Secondary Containment for Tanks 2017 Tank Type: Above Ground Stationary Tank Drawing Numbers: GOSTORE-2023NOV-Series, Drawing Numbers in Details Name of Designer: DESIGN ENGINEERING Capacity: 2,500 litres, 5,500 litres; 11,000 litres, 16,000 litres From 13/02/2025: Description: GO-INDUSTRIAL STORE SERIES Design Specification: AS 1692 SWI Reduced Secondary Containment for Tanks 2017 Tank Type: Above Ground Stationary Tank Drawing Numbers: GOSTORE-2023/2024 NOV-Series, Drawing Numbers in Details Name of Designer: DESIGN ENGINEERING Capacity: 2,500 litres, 4,950 litres; 5,500 litres; 11,000 litres, 16,000 litres | Name: Diesel & Combustible liquids AS1940 C1/C2 Class(es): 3.1D | GO INDUSTRIAL PTY LTD Suite 15229 17B Farnham Street Parnell Auckland 1052 New Zealand | From 27/02/2024: FAB0087: Zhangjiagang Fuel Equipment System Co. Ltd. 3 Haixin North Road, Nanfeng, Zhangjiagang, Jiangsu, China. Safe Fill Levels per individual tank drawings From 13/02/2025: FAB0087: Zhangjiagang Fuel Equipment System Co. Ltd. 3 Haixin North Road, Nanfeng, Zhangjiagang, Jiangsu, China. TNK20326 Safe Fill Levels per individual tank drawings. Specific Tank Drawing Numbers: GOSTORE-2023NOV-2500 sheets 1-4; GOSTORE-2024NOV-4950 sheets 1-4; GOSTORE-2023NOV-5500 sheets 1-4; GOSTORE-2023NOV-11000 sheets 1-5; GOSTORE-2023NOV-16000 sheets 1-5. | 2030-02-13 | FAB0087
TNK20327 | 2024-02-27 | Design Engineering | Zhangjiagang Fuel Equipment System Co. Ltd. 3 Haixin North Road, Nanfeng, Zhangjiagang, Jiangsu, China | AS 1692: 2006 FAB0087 | Description: GO-INDUSTRIAL CONTAINER SERIES Design Specification: AS 1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: GOCON-2023SEPT-Series: 12; 18; 30; 38; 69; 75; 80; 90; 110 - shts 1-2 Name of Designer: DESIGN ENGINEERING Capacity: 12,000; 18,000, 30,000; 38,000; 69,000; 75,000; 80,000; 90,000; 110,000 L | Name: Diesel & Combustible liquids AS1940 C1/C2 Class(es): 3.1D | GO INDUSTRIAL PTY LTD Suite 15229 17B Farnham Street Parnell Auckland 1052 New Zealand | FAB0087: Zhangjiagang Fuel Equipment System Co. Ltd. 3 Haixin North Road, Nanfeng, Zhangjiagang, Jiangsu, China. Safe Fill Levels per individual tank drawings. GO Container Series all have greater than 110% Secondary Containment | 2029-02-27 | FAB0087
TNK20328 | 2024-02-27 | Carlyon Civil Construction | Carlyon Civil Construction Ltd PO Box 10092 Te Rapa, Hamilton, 3241 12 Manchester Place, Te Rapa, Hamilton 3200 FAB0083 | SWRI 95-03 FAB0083 | Description: 4HR-FFS-Series Design Specification: SWRI 95-03 Tank Type: Above Ground Stationary Tank Drawing Numbers: Carlyon: Tank Asm; Fire Resistant Tanks 08/02/2024 Rev A sheets 1 & 2 Name of Designer: Carlyon Civil Construction Capacity: 850 - 10,000 litres Compartments: 1 | Name: Diesel / Refined Waste Oil Class(es): 3.1D Name: Petroleum Products & Flammable Liquids Class(es): 3.1A, 3.1B, 3.1C, 3.1D | CARLYON CIVIL CONSTRUCTION LIMITED 12 Manchester Place, Te Rapa, Hamilton 3200 | Tank series dimensions, vents and nozzles per Carlyon tank drawing tables sheets 1 & 2. SwRI Report 01.28312.01.001 FAB0083 | 2029-02-27 | FAB0083
TNK20329 | 2024-03-01 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3361 Double contained >110% Secondary Containment: HDPE 2450mm DIA x 3000mm HOA x 20mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plastic Construction HFA-001-Rev A2 Name of Designer: Mech Eng Limited Capacity: 13,671 litres Compartments: 1 | Name: HYDROFLUOROSILICIC ACID 1.22sg Class(es): 8.2C, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Tom Robert, Mech Eng Limited Report 241031-RP01-revA | 2029-03-01
TNK20330 | 2024-02-23 | TIRA NDA |  | AS 1692: 2006 | Description: Vertical 316 SS cone roof and bottom on legs Design Specification: AS 1692:2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 7103214-G01; 7103214-A01; 7103214-A02 Name of Designer: TIRA NDA Capacity: 40,000 litres Compartments: 1 | Name: Caustic Soda 2% Class(es): 8.1A, 8.2C, 8.3A | TIRA COMPANY LIMITED 10 Seafair Close, Cloudy Bay Business Park, Blenheim 7274 | This tank is designated for Caustic storage at Westlands Dairy Factory 56 Livingstone Street Hokitika. | 2074-02-28
TNK20331 | 2024-03-06 | TIRA NDA |  | AS 1692: 2006 | Description: Vertical 316 SS cone roof and bottom on legs Design Specification: AS 1692:2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 7103210-G01; 7103210-A01; 7103210-A02 Name of Designer: TIRA NDA Capacity: 33,350 Ltrs Compartments: 1 | Name: Caustic 2-5% Class(es): 8.1A, 8.2C, 8.3A | TIRA COMPANY LIMITED 10 Seafair Close, Cloudy Bay Business Park, Blenheim 7274 | This tank is designated for Caustic Storage at Westlands Dairy Factory, 56 Livingstone Street, Hokitika. | 2074-03-06
TNK20332 | 2024-03-06 | TIRA NDA |  | AS 1692: 2006 | Description: Vertical 316 SS cone roof and bottom on legs Design Specification: AS 1692:2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 7103211-G01; 7103211-A01; 7103211-A02 Name of Designer: TIRA NDA Capacity: 43,063 litres Compartments: 1 | Name: Nitric Acid 2% Class(es): 6.9B, 8.1A, 8.2C, 8.3A | TIRA COMPANY LIMITED 10 Seafair Close, Cloudy Bay Business Park, Blenheim 7274 | This tank is designated for Westlands Dairy Factory, 56 Livingstone Street, Hokitika. | 2074-03-06
TNK20333 | 2024-03-08 | Hendl & Murray Engineering Limited | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 | AS1692: 2006 FAB0033 | Description: 38,820 Litres aboveground, single skin, vertical, cylindrical, cone top, flat bottom stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 23137-00, Rev B, 35m3 Flammable Liquid Tank, Drawn: M.Singh, Date: 16/01/24 Name of Designer: Hendl & Murray Engineering Limited and Tom Roberts Capacity: 38,820 Litres Compartments: 1 | Name: Hydrocarbons Liquid Waste Class(es): 3.1B, 6.1C, 6.7B, 6.8A, 6.9A, 8.3A | HENDL & MURRAY ENGINEERING LIMITED 103 Tawa Street, Melville, Hamilton 3206 | Tank Location: 30 Neales Road, East Tāmaki, Auckland. Unique serial number to be allocated for tank. Tank fabrication and testing records to be retained. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2034-03-08 | FAB0033
TNK20334 | 2024-04-05 | Fuel Storage Limited | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu 3840 FAB0050 | AS1692: 2006 FAB0050 | Tank / Container Details: Description: 15,270 Litres above ground, double skinned, rectangular stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: FSL-DS15000-01-01 to 05, Rev A, TANK SIZE15,000L, Drawn: BAZ, Date: 20/03/2024 Name of Designer: Fuel Storage Limited - Baz Capacity: 15,270 L Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | FUEL STORAGE LIMITED 700 Bond Road, Te Awamutu 3800 | Maximum Safe Fill Level = 14,500 Litres (1947mm). Approved For: The storage and transfer of Diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2034-04-05 | FAB0050
TNK20335 | 2024-03-07 | Martin Engineering | Martin Engineering (Palmerston North) Ltd. PO Box 5295, Terrace End, Palmerston North 4441 891 Tremaine Avenue, Roslyn, Palmerston North 4414 | AS1692: 2006 FAB0045 | Description: 107KL-DS; 6mm Mild Steel, Category 4, 19.4m LOA x 2.8m DIA. Double skinned. Design Specification: AS 1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: Martin Engineering 107KL Tank GA Drawing - Rev A sheets 1-4 Name of Designer: Martin Engineering Capacity: 106206 L; 101650 L SFL | Name: Diesel & Combustible liquids AS1940 C1/C2 Class(es): 3.1D | MARTIN ENGINEERING (PN) LIMITED 891 Tremaine Avenue, Roslyn, Palmerston North 4414 | FAB0045; Secondary containment is greater than 110% of Primary Tank. | 2029-03-07 | FAB0045
TNK20336 | 2024-03-20 | Fuelchief Limited | FUELCHIEF LIMITED Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS 1692: 2006 SWI Reduced Secondary Containment for Tanks FAB0093 | Description: 10,000 Litres above ground, double skin ,horizontal, cylindrical stationary tank Design Specification: AS 1692:2006, SWI Reduced Secondary Containment for Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: VG3- 10,000, Sheet 1 of 1, Drawn: DL, Date: 08/11/2022 & 7870-1001 to 4, Rev01, Date: 14.3.24 Name of Designer: Fuelchief Limited - DL Capacity: 10,000 Litres Compartments: 1 | Name: Tanalith C Oxide Class(es): 6.1B, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 6.9A, 8.1A, 8.2B, 8.3A | FUELCHIEF LIMITED Innovation Park Lot 15/185 Kirk Road, Templeton, Christchurch 7675 | Approved For: The storage and transfer of Tanalith C Oxide, having a hazard classification of 6.1B, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 6.9A, 8.1A, 8.2B, 8.3A, 9.1A, 9.2B, 9.3A, 9.4C. Tank Location: 25 Yukon Place, Hornby South, Christchurch 8042. Unique serial number to be allocated for tank. Tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank name plate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2034-03-20 | FAB0093
TNK20337 | 2024-03-15 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3286: HDPE Single Skinned Vertical cylinder: 1800 mm DIA x 2605 mm HOA x 12/24mm WT, 5500 MAX Vo Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: CHEMFEED 402583/05/20 rev G Name of Designer: Mech Eng Limited Capacity: 5500 litres, 5000 litres SFL Compartments: 1 | Name: Citric acid 50% aqueous solution 1.25 s.g. Class(es): 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Tom Robert, Mech Eng Limited Report 231136-RP01-revB | 2029-03-15
TNK20338 | 2024-03-15 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3287: HDPE Single Skinned Vertical cylinder: 1800 mm DIA x 2605 mm HOA x 12/24mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: CHEMFEED 402583/05/10 rev H Name of Designer: Mech Eng Limited Capacity: 5500 litres; 5000 litres SFL Compartments: 1 | Name: Sodium hypochlorite 15% w/w aqueous solution Class(es): 8.2C | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Tom Robert, Mech Eng Limited Report 231134-RP01-revA | 2029-03-15
TNK20339 | 2024-03-15 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3289: HDPE Single Skinned Vertical cylinder: 2300 mm DIA x 2489 mm HOA x 15/27mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: CHEMFEED 402583/08/30 rev H Name of Designer: Mech Eng Limited Capacity: 8800 litres; 8000 litres SFL Compartments: 1 | Name: Sodium hydroxide (Caustic soda) 30% w/w aqueous solution sg 1.3 Class(es): 6.1D, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Tom Robert, Mech Eng Limited Report 231137-RP01-revA | 2029-03-14
TNK20340 | 2024-03-15 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3288: HDPE Single Skinned 2300 mm DIA x 2239mm HOA x 15/27 mm WT, Max 7700 litres; SFL 7000 litres Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: CHEMFEED 402583/07/10 rev G Name of Designer: Mech Eng Limited Capacity: 7700 litres; 7000 litres SFL Compartments: 1 | Name: Poly Aluminium chloride solution (Profloc A23) Class(es): 6.1D | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Tom Robert, Mech Eng Limited Report 231137-RP01-revA | 2029-03-15
TNK20341 | 2024-03-28 | Amir Pakroo |  | AS1692: 2006 | Description: Vertical 316 SS cone roof flat bottom Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 26675-TANK 01-A01 Sht's 1, 2 & 3 Name of Designer: Amir Pakroo Capacity: 16,349 liters Compartments: 1 | Name: 98% Sulphuric Acid Class(es): 6.1D, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A | LONGVELD LIMITED 153-157 Ellis Street, Frankton, Hamilton 3204 | This tank is designed for TetraPak Hautapu, Cambridge. Design life of the tank is 50 years. | 2074-12-31
TNK20342 | 2024-03-28 | Amir Pakroo |  | AS1692: 2006 | Description: 316L SS Vertical Cone Roof flat bottom Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 26675-TANK 02-A01 Sht's 1, 2 & 3 Name of Designer: Amir Pakroo Capacity: 11,265 Liters Compartments: 1 | Name: 50% Potassium Hydroxide KOH Class(es): 6.1D, 8.1A, 8.2A, 8.3A | LONGVELD LIMITED 153-157 Ellis Street, Frankton, Hamilton 3204 | This tank is designed for Tetrapak Hautapu, Cambridge. Design life is based on 50 years. | 2074-12-31
TNK20343 | 2024-04-15 | Matheson Fabrication Limited |  | Design verified to NZS 1170.5, NZSEE’s “Seismic Design of Storage Tanks” and NZS 3404 by Worley New Zealand Limited | Description: Vertical 316 SS flat roof and slope bottom load cells Design Specification: Design verified to NZS 1170.5, NZSEE’s “Seismic Design of Storage Tanks” and NZS 3404 by Worley New Zealand Limited Tank Type: Process Container Drawing Numbers: ISO-5K-CMT; SECT-5K-CMT; SWD-5K-CMT Name of Designer: Matheson Fabrication Limited Capacity: 5000 Ltrs Compartments: 1 | Name: >=51% Sulphuric Acid Class(es): 6.1D, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A Name: >5%-<50% Caustic Soda aqueous Class(es): 8.1A, 8.2A, 8.3A Name: 64% Nitric Acid Class(es): 6.1D, 8.1A, 8.2B, 8.3A | MATHESON FABRICATION LIMITED Site 29 Whakatu Industrial Park, Johnston Way, Hastings 4102 | This Process Vessel design has been approved by Worley NZ. Tank is destined for an Auckland site. Basis of design: standards used were NZS 1170.5 and NZSEE’s “Seismic Design of Storage Tanks” and the material design standard was NZS 3404 | 2074-04-15
TNK20344 | 2024-03-26 | TRL Engineering Pty Ltd |  | UL 1316:1994 (2nd Edition) | Description: Z-103707-T3 - Z Harris Road, Double skinned GRP; 11.672 m LOA 2.376 m DIA. Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-103707-T3-ADO-F101; Z-103707-T3-ADO-F102 Name of Designer: TRL Engineering Pty Ltd Capacity: 50,080 litres; SFL 48,500 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 142 Harris Road, East Tāmaki, Auckland 2013 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has permanent hydroguard interstitial monitoring.. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992 | 2029-03-26
TNK20345 | 2024-04-30 | Visa S.p.a. | Visa S.p.a. Via I° Maggio, 55 Fontanelle (TV) Italia | AS1692: 2006 FAB0061 | Description: 822 Litres above ground, single skin, rectangular generator base stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 103000005000-000-03, Sheets 1 to 9, Rev03, Serbatoio 800LT x GV151/00/00, Date:13/02/2023 Name of Designer: VISA S.P.A. - Angelo Claut Capacity: 822 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | QUALITY POWER LIMITED 212 Crawford Street, Central Dunedin, Dunedin 9016 | Maximum Safe Fill Level = 800 Litres. Approved For: The storage and transfer of Diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved for supplying an engine or burner. If supplying an engine or burner approved for use with diesel only having a flash point greater than 60 deg C but less than or equal to 93 deg C. 800L Product presentation rev 02, Date: 24/04/2024. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2034-04-30 | FAB0061
TNK20346 | 2024-05-01 | Mech Eng Limited |  | AS 2634: 1983 | Description: T-3347- PVC-GRP Single Skin, 1800mm DIA x 2820mm HOA x 12mm WT Design Specification: AS 2634: 1983 Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering 3288-012-Rev C Name of Designer: Mech Eng Limited Capacity: 5903 litres max / 5621 litres SFL Compartments: 1 | Name: Sodium hypochlorite 1.2 s.g. aqueous solution Class(es): 8.2C, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Tom Robert, Mech Eng Limited Report 231891-RP01-revB | 2029-05-01
TNK23047 | 2024-06-18 | CT Engineering Services Limited |  | API Standard 650 | Description: TNK23047 4.8m ID x 6 m high Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: C20040D-T170PM1793 Rev 2 Sheets 1-8 Name of Designer: CT Engineering Services Limited Capacity: 100,000 L Compartments: 1 | Name: Dilute CCA 1-6% UN3082 Class(es): 6.5A, 6.5B | CT ENGINEERING SERVICES LIMITED 10A Gateway Park Drive, Pokeno 2402 | Tank serial number T170PM1793. SG 1.0 @ 20 deg C. Design SG 1.1 @ 20 deg C. Seismic design to NZS1170.5. CMK Engineering Pty Ltd design report C20040-T170PM1793 Rev 2. Z factor Taupo 0.28. Sub soil class D. Near fault 1.0. Site location Permapine Ltd, 33 White Road, Broadlands, Taupo. No wind loading to NZS1170.2 required as tank installed indoors. Design specification API650 12th edition : 2013 inc Addendum 1 & 2. Joint efficiency 0.7 (no radiography). Corrosion allowance 2 mm. Seismic anchoring required, 8 number equi spaced M24 Gr 8.8 bolts. Hydrostatic pressure test carried out 9 May 2024. Safe fill height 5.25m (95 kL), High level alarm 5.425m (98.16 kL0), High high level alarm 5.525m (99.97 kL). Slosh wave height 456mm above product design height. Venting to API2000. Maximum inflow 20,000 litres/min. Maximum outflow 20,000 litres/min. 2 No. 200 NB goose neck vents fitted. | 2029-06-18 | Non-sequential TNK number.
TNK23048 | 2024-06-18 | CT Engineering Services Limited |  | API Standard 650 | Description: TNK23048 4.8m ID x 6m high Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: C20040D-T171PM1793 Rev 1 Name of Designer: CT Engineering Limited Capacity: 100,000 L Compartments: 1 | Name: Dilute CCA 1-6% UN3082 Class(es): 6.5A, 6.5B | CT ENGINEERING SERVICES LIMITED 10A Gateway Park Drive, Pokeno 2402 | Tank serial number T171PM1793. SG 1.0 @ 20 deg C. Design SG 1.1 @ 20 deg C. Seismic design to NZS1170.5. CMK Engineering Pty Ltd design report C20040-T170PM1793 Rev 2. Z factor Taupo 0.28. Sub soil class D. Near fault 1.0. Site location Permapine Ltd, 33 White Road, Broadlands, Taupo. No wind loading to NZS1170.2 required as tank installed indoors. Design specification API650 12th edition : 2013 inc Addendum 1 & 2. Joint efficiency 0.7 (no radiography). Corrosion allowance 2 mm. Seismic anchoring required, 8 number equi spaced M24 Gr 8.8 bolts. Hydrostatic pressure test carried out 9 May 2024. Safe fill height 5.25m (95 kL), High level alarm 5.425m (98.16 kL0), High high level alarm 5.525m (99.97 kL). Slosh wave height 456mm above product design height. Venting to API2000. Maximum inflow 20,000 litres/min. Maximum outflow 20,000 litres/min. 2 No. 200 NB goose neck vents fitted. | 2029-06-18 | Non-sequential TNK number.
TNK23049 | 2024-06-18 | CT Engineering Services Limited |  | API Standard 650 | Description: TNK23049, 4.8m ID x 6m high. Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: C20040D-T172PM1793 Rev 1. Name of Designer: CT Engineering Services Limited Capacity: 100,000 L Compartments: 1 | Name: Dilute CCA 1-6% UN3082 Class(es): 6.5A, 6.5B | CT ENGINEERING SERVICES LIMITED 10A Gateway Park Drive, Pokeno 2402 | Tank serial number T172PM1793. SG 1.0 @ 20 deg C. Design SG 1.1 @ 20 deg C. Seismic design to NZS1170.5. CMK Engineering Pty Ltd design report C20040-T170PM1793 Rev 2. Z factor Taupo 0.28. Sub soil class D. Near fault 1.0. Site location Permapine Ltd, 33 White Road, Broadlands, Taupo. No wind loading to NZS1170.2 required as tank installed indoors. Design specification API650 12th edition : 2013 inc Addendum 1 & 2. Joint efficiency 0.7 (no radiography). Corrosion allowance 2 mm. Seismic anchoring required, 8 number equi spaced M24 Gr 8.8 bolts. Hydrostatic pressure test carried out 9 May 2024. Safe fill height 5.25m (95 kL), High level alarm 5.425m (98.16 kL), High high level alarm 5.525m (99.97 kL). Slosh wave height 456mm above product design height. Venting to API2000. Maximum inflow 20,000 litres/min. Maximum outflow 20,000 litres/min. 2 No. 200 NB goose neck vents fitted. | 2029-06-18 | Non-sequential TNK number.
TNK23050 | 2024-06-25 | CT Engineering Services Limited |  | API Standard 650 | Description: TNK 23050 2.8 m ID x 4.29 m high 23.38 kL bulk storage tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: C21019D-T173PM1793 Rev 1 Name of Designer: CT Engineering Services Limited Capacity: 24,300 L Compartments: 1 | Name: Tanalith C Oxide UN2922. Class(es): 6.1B, 6.5A, 6.5B, 6.6A, 8.1A, 8.2B, 8.3A | CT ENGINEERING SERVICES LIMITED 10A Gateway Park Drive, Pokeno 2402 | Tank serial number T173PM1793. Design SG 2.0. Seismic design to NZS 1170.5 CMK Engineering Pty Ltd design report C2019-T173PM1793 Rev 1. Z Factor 0.28 Taupo. Soil class D. Near fault 1.0 Site location Permapine Ltd, 33 White Road, Broadlands, Taupo. No wind assessment to NZS1170.2 required as tank installed inside building. Design specification API650 12th edition: 2013 inc Addendum 1 & 2. Joint efficiency 0.7 (no radiography). Corrosion allowance 2 mm. Seismic anchoring required 6 number equispaced 24 mm dia bolts, PCD 2.94 m. Hydrostatic pressure test and pneumatic pressure testing of all tank compensating plates carried out 9/5/2024. Hydrotest to 7.58 m above tank floor. (74.33 kPa). Safe fill height 3.79 m, ("3.38 kL). High level alarm 3.84 m (23.68 kL). High high level alarm 3.89 m (23.99 kL). Slosh wave height 348 mm. Venting to API2000. Max inflow 1000 L/min. Max outflow 1000L/min. Vent pipe 65mm NB. | 2029-06-25 | Non-sequential TNK number.
TNK23051 | 2024-06-25 | CT Engineering Services Limited |  | API Standard 650 | Description: TNK23051 3.6m ID x 4.8 m high Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: C21084D-T175PM1793 Rev 1 Sheets 1-8 Name of Designer: CT Engineering Services Limited Capacity: 45,000 L Compartments: 1 | Name: Dilute CCA 1-6% UN3083 Class(es): 6.5A, 6.5B | CT ENGINEERING SERVICES LIMITED 10A Gateway Park Drive, Pokeno 2402 | Tank serial number T175PM1793. SG 1.1. Design SG 2.0. Seismic design to NZS 1170.5. CMK Engineering Pty Ltd design report C21084-T175PM1793 . Z Factor 0.28 Taupo. Soil class D. Near fault 1.0 Site location Permapine Ltd, 33 White Road, Broadlands, Taupo. No wind assessment to NZS1170.2 required as tank installed inside building. Design specification API650 12th edition: 2013 inc Addendum 1 & 2. Joint efficiency 0.7 (no radiography). Corrosion allowance 2 mm. Seismic anchoring required 5 number equispaced M24 mm GR 8.8 dia bolts. Hydrostatic pressure test and pneumatic pressure testing of all tank compensating plates carried out 9/5/2024. Hydrotest to 50 mm above corner joint. (47.12 kPa). Safe fill height 4.25 m, (43.25 kL). High level alarm 4.3 m (43.76 kL). High high level alarm 4.4 m (44.78 kL). Slosh wave height 395 mm. Venting to API2000. Max inflow 480 cu m/hr. Max outflow 480 cu m/hr. 2 number Vent pipes 200 mm NB. | 2029-06-25 | Non-sequential TNK number.
TNK20352 | 2024-04-26 | Plaspoke Limited / Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: 3008-TK01- HDPE Double skinned 2320mm IDIA, 3059mm HOA x 15/27mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plaspoke 0122-PLASCT-01-Rev-C shts 1-6 Name of Designer: Plaspoke Limited / Mech Eng Limited Capacity: 10707 litres / 10,000 litres SFL Compartments: 1 | Name: Waste Sulphuric acid 20% sg 1.14 Class(es): 6.1D, 6.9A, 6.9B, 8.1A, 8.2B, 8.3A | Plaspoke Limited 35 Saleyards Road, Otahuhu, Auckland 1062 | Design in accordance with Mech Eng Limited Design Report 241351-RP01-RevA | 2029-04-26 | N/A
TNK20353 | 2024-05-01 | TRL Engineering Pty Ltd |  | UL 1316:1994 (2nd Edition) | Description: Z-103707-T2 - Z Harris Road, Double skinned GRP; 11.5 m LOA 2.4 m DIA. Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-103707-T2-91-F103; Z-103707-T2-91-F104 Name of Designer: TRL Engineering Pty Ltd Capacity: 48,554 litres; SFL 46,000 litres Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 142 Harris Road, East Tāmaki, Auckland 2013 | This tank is constructed as a one-off field constructed tank. Tank has permanent hydroguard interstitial monitoring. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2029-05-01 | N/A
TNK20354 | 2024-05-02 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: XMG-400099-T1: GRP Double skinned 6.8m LOA x 2.5m DIA x 13mm WT Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: TRL-DRW-XMG-T1-98-103; TRL-DRW-XMGT1-98-104 Name of Designer: Tankreline NZ Limited Capacity: 30,109 litres / 27,000 litres SFL Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 560 Glenfield Road, Glenfield, Auckland 0629 | This tank is constructed as a one-off field constructed tank. Tank has Hydroguard permanent interstitial monitoring system. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2029-05-02 | N/A
TNK20355 | 2024-05-02 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: XMG-400099-T2: GRP Double skin 10.8m LOA x 2.5m DIA x 13mm WT Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: TRL-DRW-XMG-T2-91-101; TRL-DRW-XMGT2-91-102 Name of Designer: Tankreline NZ Limited Capacity: 47,222 litres / 42,500 litres SFL Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 560 Glenfield Road, Glenfield, Auckland 0629 | This tank is constructed as a one-off field constructed tank. Tank has Hydroguard permanent interstitial monitoring system. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2029-05-02 | N/A
TNK20356 | 2024-05-02 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: XMG-400099-T3: GRP Double skin 10.8m LOA x 2.5m DIA x 13m WT Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: TRL-DRW-XMG-T3-ADO-105; TRL-DRWXMG-T3-ADO-106 Name of Designer: Tankreline NZ Limited Capacity: 48,132 litres / 43,300 SFL Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 560 Glenfield Road, Glenfield, Auckland 0629 | This tank is constructed as a one-off field constructed tank. Tank has Hydroguard permanent interstitial monitoring system. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2029-05-02 | N/A
TNK20357 | 2024-06-07 | Fuelchief Limited | FUELCHIEF LIMITED Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS1692: 2006 FAB0093 | Description: 23,999 Litres above ground, single skin, cylindrical, horizontal stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: PX4-24,000, Rev C, Sheet 1 & 2, Date:30/05/2024 Name of Designer: Fuelchief Limited - DL Capacity: 23,999 Litres Compartments: 1 | Name: SOLBERG agent only RE-HEALING FOAM RF3 3% Class(es): 6.5B, 6.9B | FUELCHIEF LIMITED Innovation Park Lot 15, 185 Kirk Road, Templeton, Christchurch 7675 | Manufacturer's Tank Serial No.: 30034. Maximum Safe Fill Level = 23,279 Litres (2552mm). Approved For: The storage and transfer of SOLBERG agent only RE-HEALING FOAM RF3 3%, having a hazard classification of 6.1E, 6.3B, 6.4A, 6.5B, 6.9B. Unique serial number to be allocated for tank. Tank fabrication and testing records to be retained. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2034-06-07 | FAB0093
TNK20358 | 2024-06-05 | TRL Engineering Pty Ltd |  | UL 1316:1994 (2nd Edition) | Description: Z-103707-T1 - Z Harris Road, Double skinned GRP; 9.3 m LOA 2.4 m DIA. Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-103707-T1-95-F105; Z-103707-T1-95-F106 Name of Designer: TRL Engineering Pty Ltd Capacity: 39,413 litres; SFL 37,500 litres Compartments:1 | Name: Petroleum Products Class(es):3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED Postal Address: PO Box 2091, Wellington, 6140 Physical Address: 142 Harris Road, East Tāmaki, Auckland, 2013 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has permanent hydroguard interstitial monitoring.. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2029-05-23 | N/A
TNK20359 | 2024-06-10 | Plaspoke Limited / Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: 7.5KL-IL4-PLASCT-01 - Single skinned 2290mm IDIA, 2221mm HOA x 20mm WT Design Specification: BS EN 12573 SWI Thermoplasic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plaspoke 7.5KL-IL4-PLASCT-01-Rev-D shts 1-7 Name of Designer: Plaspoke Limited / Mech Eng Limited Capacity: 8266 litres / 7809 litres SFL Compartments: 1 | Name: HDPE Chemically compatible substances maximum density Classes: 1.13, 6.1A, 6.1B, 6.1C, 6.1D, 6.5A, 6.5B, 6.6A, 6.6B, 6.7A, 6.7B, 6.8A, 6.8B, 6.8C, 6.9A, 6.9B, 8.1A, 8.2A, 8.2B, 8.2C, 8.3A | Plaspoke Limited 35 Saleyards Road, Otahuhu, Auckland, 1062 | Design in accordance with Mech Eng Limited Design Report 241482-RP01-Rev-A PCBU to insure storage/use duty of the tank complies with material compatibility of HDPE. PCBU to insure the hazardous substance is within the specified classification and concentration limits of BS EN 12573 SWI Thermoplastic Stationary Tanks 2017. PCBU to insure tank is installed in accordance with Mech Eng Limited design report for seismic requirements of NZS1170.5 and wind loading requirements of NZS1170.2. | 2029-05-30 | N/A
TNK20360 | 2024-06-10 | Martin Engineering | Martin Engineering (Palmerston North) Ltd. PO Box 5295, Terrace End, Palmerston North, 4441 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 | AS1692: 2006 FAB0045 | Description: 107KL-DS-110SC; 6mm Mild Steel, Category 4, 20.5m LOA x 2.8m DIA. Double skinned. Design Specification: AS 1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: Martin Engineering 107KL-DS-110SC Tank GA Drawing - Rev E sheets 1-4 Name of Designer: Martin Engineering Capacity: 113277 litres; 107350 litres SFL. | Name: Diesel & Combustible liquids AS1940 C1/C2 Class(es): 3.1D | MARTIN ENGINEERING (PN) LIMITED 891 Tremaine Avenue, Roslyn, Palmerston North 4414 | FAB0045; Secondary containment is greater than 110% of Primary Tank. | 2029-06-10 | FAB0045
TNK20361 | 2024-06-14 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: XRH-400016-T1: GRP Double skin 10.9m LOA x 2.5m DIA x 13m WT Design Specification: UL 1316:1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: TRL-DRW-XRH-T1-98-101;TRL-DRW-XRH-T1-98-102 Name of Designer: Tankreline NZ Limited Capacity: 48,560 litres 46,100 SFL Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 130 Royal Road, Massey, Auckland 0614 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has Hydroguard permanent interstitial monitoring system Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. Tank Owner (PCBU) requested operational SFL reduction to 43,700 litres. | 2029-06-14 | N/A
TNK20362 | 2024-06-19 | Maskell Productions |  | AS 2634: 1983 | Description: TEA-1244- GRP- Vertical cylinder 3000 mm DIA x 4030 mm HOA x 6.5mm WT Design Specification: AS 2634: 1983 Tank Type: Above Ground Stationary Tank Drawing Numbers: Maskell 2370-20-00 rev 5 Name of Designer: Maskell Productions Capacity: 23,700 L max; 20,000 L SFL | Name: Sodium hypochlorite 15% aqueous solution 1.4 sg maximum Class(es): 8.2C, 8.3A | MASKELL PRODUCTIONS LIMITED 24 Bowden Road, Mount Wellington, Auckland 1060 | Design Report John Milton Clark Engineers, Inc. - 24MASK081 -ver. 1.0. | 2029-06-19 | N/A
TNK20363 | 2024-06-21 | Armatec Environmental Limited |  | ASME RTP-1 | Description: Vertical Scrubber Tower Vinyl Ester V66 resin Design Specification: ASME RTP-1 Tank Type: Process Container Drawing Numbers: 4064-60-0816 Name of Designer: Armatec Environmental Limited Capacity: 9,450 litres Compartments: 1 | Name: Hexafluorosilicic Acid Class(es): 8.2C, 8.3A | ARMATEC ENVIRONMENTAL LIMITED 42 Egmont Road, Waiwhakaiho, New Plymouth 4312 | Vessel Nbr: FT-100. This scrubber tower is destined for Ravensdown Fertiliser Works Awatoto Napier. | 2074-06-21 | N/A
TNK20364 | 2024-06-21 | Armatec Environmental Limited |  | ASME RTP-1 | Description: Vertical Scrubber Tower Vinyl Ester V66 Design Specification: ASME RTP-1 Tank Type: Process Container Drawing Numbers: 4064-60-0817 Name of Designer: Armatec Environmental Limited Capacity: 10,955 litres Compartments: 1 | Name: Hexafluorosilicic Acid Class(es): 8.2C, 8.3A | ARMATEC ENVIRONMENTAL LIMITED 42 Egmont Road, Waiwhakaiho, New Plymouth 4312 | Vessel Nbr: FT-200. This Scrubber tower is destined for Ravensdown Fertiliser Works, Awatoto Napier. | 2074-06-21 | N/A
TNK20365 | 2024-06-21 | Armatec Environmental Limited |  | ASME RTP-1 | Description: Vertical Scrubber Tower Vinyl Ester V66 resin Design Specification: ASME RTP-1 Tank Type: Process Container Drawing Numbers: 4064-60-0818 Name of Designer: Armatec Environmental Capacity: 11,700 litres Compartments: 1 | Name: Hexafluorosilicic Acid Class(es): 8.2C, 8.3A | ARMATEC ENVIRONMENTAL LIMITED 42 Egmont Road, Waiwhakaiho, New Plymouth 4312 | Vessel Nbr: FT-300. This Scrubber tower is destined for Ravensdown Fertiliser Works, Awatoto Napier. | 2074-06-21 | N/A
TNK20366 | 2024-06-21 | Armatec Environmental Limited |  | ASME RTP-1 | Description: Vertical Scrubber Tower Vinyl Ester V66 resin Design Specification: ASME RTP-1 Tank Type: Process Container Drawing Numbers: 4064-60-0819 Name of Designer: Armatec Environmental Capacity: 12,400 litres Compartments: 1 | Name: Hexafluorosilicic Acid Class(es): 8.2C, 8.3A | ARMATEC ENVIRONMENTAL LIMITED 42 Egmont Road, Waiwhakaiho, New Plymouth 4312 | Vessel Nbr: FT-400. This scrubber tower is destined for Ravensdown Fertiliser Works, Awatoto, Napier. | 2074-06-21 | N/A
TNK20367 | 2024-06-19 | PLASTICS CONSTRUCTIONS LIMITED |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T-3371-HDPE Double contained, vertical cylinder, 2700mm IDIA x 3000mm H x 25/40mm WT. Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plastics Constructions ACE-001 Rev A4 Name of Designer: Mech Eng Limited Capacity: 16375 litres MAX; 15000 litres SFL Compartments: 1 | Name: Acetic acid 49% aqueous concentration Class(es): 8.1A, 8.2B | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland, 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Tom Robert, Mech Eng Limited Report 241512-RP01-rev-A | 2029-06-19 | N/A
TNK20368 | 2024-06-19 | PLASTICS CONSTRUCTIONS LIMITED |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T-3372-HDPE Double contained, vertical cylinder, 3100mm IDIA x 3000mm H x 20/35mm WT. Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plastics Constructions ALU-001 Rev A4 Name of Designer: Mech Eng Limited Capacity: 21,586 litres MAX; 20,000 litres SFL Compartments: 1 | Name: Aluminium sulphate aqueous solution 1.33 s.g. maximum Class(es): 8.1A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland, 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Tom Robert, Mech Eng Limited Report 241511-RP01-rev-A | 2029-06-19 | N/A
TNK20369 | 2024-07-15 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3366 Single skin HDPE, 3400mm IDIA x 2840mm HOA x 20mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering 5667-005 issue 3 Name of Designer: Mech Eng Limited Capacity: 21,245 litres max; 20,228 litres SFL Compartments: 1 | Name: Sodium hydroxide (Caustic soda) 30% w/w aqueous solution Class(es): 6.1D, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Mech Eng Limited 241691-RP01-Rev A | 2029-07-15
TNK20370 | 2024-07-15 | Tankreline NZ Limited |  | UL 1316:1994 (2nd Edition) | Description: XRH-400016-T2: GRP Double skin 10.9mLOA x 2.5m DIA x 13m WT Design Specification: UL 1316: 1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: TRL-DRW-XRH-T2-91-103;TRL-DRW-XRHT2-91-104 Name of Designer: Tankreline NZ Limited Capacity: 48,728 L MAX - 46,290 L SFL Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 130 Royal Road, Massey, Auckland 0614 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has Hydroguard permanent interstitial monitoring system Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. Tank Owner (PCBU) requested operational SFL reduction to 43,700 litres. | 2029-07-15
TNK20371 | 2024-07-24 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3380 - Self bunded HDPE, 1900mm DIA x 2573mm HOA x 12/24mm WT, SC >110% Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: CHEMFEED 405752/20/01 rev B Name of Designer: Mech Eng Limited Capacity: 5500 litres Max; 5000 litres SFL Compartments: 1 | Name: Sodium hydroxide (Caustic soda) 33% w/w aqueous solution max sg 1.35 Class(es): 6.1D, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Mech Eng 241632-RP01-Rev-A | 2029-07-24
TNK20372 | 2024-07-24 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3384 - Self bunded HDPE, 3300mm DIA x 3286mm HOA x 20/35mm WT, SC >110% Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: PROMINENT 406115/10/01 rev D Name of Designer: Mech Eng Limited Capacity: 20,000 litres Max; 19,000 litres SFL Compartments: 1 | Name: Sodium hydroxide (Caustic soda) 50% w/w aqueous solution max sg 1.52 Class(es): 6.1D, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Mech Eng 241611-RP01-Rev-A | 2029-07-24
TNK20373 | 2025-07-29 | TRL Engineering Pty Ltd |  | UL 1316 | Description: Z-104086-T1 / Z Ti Rakau Drive, Double skinned GRP 6.9m LOA 2.4 m DIA. Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-104086-T1-95-F101; Z-104086-T1-95- F102 Name of Designer: TRL Engineering Pty Ltd Capacity: 29419 litres / 27900 litres SFL Compartments: 1 | Name:Petroleum Products Class(es) 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 284 Ti Rakau Drive, Burswood, Auckland, 2013 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has permanent hydroguard interstitial monitoring. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2029-07-29
TNK20374 | 2025-07-29 | TRL Engineering Pty Ltd |  | UL 1316 | Description: Z-104086-T2 / Z Ti Rakau Drive, Double skinned GRP 11.8m LOA 2.4 m DIA. Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-104086-T2-91-F103; Z-104086-T2-91-F104 Name of Designer: TRL Engineering Pty Ltd Capacity: 50,611 litres / 48,000 SFL litres Compartments: 1 | Name:Petroleum Products Class(es) 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 284 Ti Rakau Drive, Burswood, Auckland, 2013 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has permanent hydroguard interstitial monitoring. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2029-07-29
TNK20375 | 2025-07-29 | TRL Engineering Pty Ltd |  | UL 1316 | Description: Z-104086-T3 / Z Ti Rakau Drive, Double skinned GRP; 9.3 m LOA 2.4 m DIA. Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-104086-T3-ADO-F105; Z-104086-T3-ADO-F106 Name of Designer: TRL Engineering Pty Ltd Capacity: 39902 litres; SFL 37,900 litres Compartments: 1 | Name:Petroleum Products Class(es) 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 284 Ti Rakau Drive, Burswood, Auckland, 2013 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has permanent hydroguard interstitial monitoring. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2029-07-29
TNK20376 | 2025-07-29 | Plaspoke Limited / Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: 7.5KL-IL4-HR-PLASCT-02 - Single skinned 2190mm IDIA, 2602mm HOA x 20mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plaspoke 7.5KL-IL4-HR-PLASCT-02-Rev-F shts 1, 2, 4-8, PLaspoke 7.5KL-IL4-PLASCT- 01 sht 3 Name of Designer: Plaspoke Limited / Mech Eng Limited Capacity: 8266 litres / 7809 litres SFL Compartments: 1 | Name: HDPE Chemically compatible substances maximum density 1.13 Class(es): 6.1A, 6.1B, 6.1C, 6.1D, 6.5A, 6.5B, 6.6A, 6.6B, 6.7A, 6.7B, 6.8A, 6.8B, 6.8C, 6.9A, 6.9B, 8.1A, 8.2A, 8.2B, 8.2C, 8.3A | Plaspoke Limited 35 Saleyards Road, Otahuhu, Auckland, 1062 | Design in accordance with Mech Eng Limited Design Report 241651-RP01-Rev-A PCBU to insure storage/use duty of the tank complies with material compatibility of HDPE. PCBU to insure the hazardous substance is within the specified classification and concentration limits of BS EN 12573 SWI Thermoplastic Stationary Tanks 2017. PCBU to insure tank is installed in accordance with Mech Eng Limited design report for seismic requirements of NZS1170.5 and wind loading requirements of NZS1170.2. | 2029-07-29
TNK20377 | 2024-07-26 | Vitor Egito de Castro |  | AS1692: 2006 | Description: Vertical 316 SS cone roof and bottom on legs Design Specification: AS 1692: 2006 Tank Type: Process Container Drawing Numbers: 27433-TANK-01_A01-01 Name of Designer: Vitor Egito de Castro Capacity: 10,504 ltrs Compartments: 1 | Name: Iron Sulfate Class(es): 6.1D Name: Silicic Acid Class(es): 6.5B, 6.7A, 6.9A Name: Sodium Bi-Sulfate Class(es): 8.2C, 8.3A Name: Sulfuric Acid 98% Class(es): 6.9A, 8.1A, 8.2A, 8.3A | LONGVELD LIMITED 153 - 157 Ellis Street, Frankton, Hamilton 3204 | Certificate expiry is based on the mechanical design life of 25 yrs of cyclic use. Tank is destined for Aspiring Materials Addington Christchurch. | 2049-07-26
TNK20378 | 2024-07-26 | Vitor Egito de Castro |  | AS1692: 2006 | Description: Vertical 316 SS open top, cone bottom on legs. Design Specification: AS 1692: 2006 Tank Type: Process Container Drawing Numbers: 27433-TANK06-A01 Name of Designer: Vitor Egito de Castro Capacity: 1,854 Ltrs Compartments: 1 | Name: Iron Sulfate Class(es): 6.1D Name: Silicic Acid Class(es): 6.5B, 6.7A, 6.9A Name: Sodium Bi-Sulfate Class(es): 8.2C, 8.3A | LONGVELD LIMITED 153 - 157 Ellis Street, Frankton, Hamilton 3204 | Certificate expiry is based on the mechanical design life of 25 yrs of cyclic use. The tank is destined for Aspiring Materials Addington Christchurch. | 2049-07-26
TNK20379 | 2024-07-26 | Vitor Egito de Castro |  | AS1692: 2006 | Description: Vertical 316 SS cone roof and bottom on legs. CAT-5 Design Specification: AS 1692:2006 Tank Type: Process Container Drawing Numbers: 27433-TANK 03-A01 Name of Designer: Vitor Egito de Castro Capacity: 2,285 Ltrs Compartments: 1 | Name: Iron Sulfate Class(es): 6.1D Name: Silicic Acid Class(es): 6.5B, 6.7A, 6.9A Name: Sodium Bi-Sulfate Class(es): 8.2C, 8.3A Name: Sulfuric Acid 98% Class(es): 6.9A, 8.1A, 8.2A, 8.3A | LONGVELD LIMITED 153 - 157 Ellis Street, Frankton, Hamilton 3204 | Certificate expiry is based on the mechanical design life of 25 yrs of cyclic use. Tank is destined for Aspiring Materials Addington Christchurch. | 2049-07-26
TNK20380 | 2024-07-26 | Vitor Egito de Castro |  | AS1692: 2006 | Description: Vertical 316 SS cone roof and bottom on legs Design Specification: AS 1692: 2006 Tank Type: Process Container Drawing Numbers: 27433- TANK04 -A01 Name of Designer: Vitor Egito de Castro Capacity: 10,725 Ltrs Compartments: 1 | Name: Iron Sulfate Class(es): 6.1D Name: Silicic Acid Class(es): 6.5B, 6.7A, 6.9A Name: Sodium Bi-Sulfate Class(es): 8.2C, 8.3A Name: Sulfuric Acid 98% Class(es): 6.9A, 8.1A, 8.2A, 8.3A | LONGVELD LIMITED 153 - 157 Ellis Street, Frankton, Hamilton 3204 | Certificate expiry is based on the mechanical design life of 25 yrs of cyclic use. Tank is destined for Aspiring Materials Addington Christchurch. | 2049-07-26
TNK20381 | 2024-07-26 | Vitor Egito de Castro |  | AS1692: 2006 | Description: Vertical 316 SS cone roof and bottom on legs Design Specification: AS 1692: 2006 Tank Type: Process Container Drawing Numbers: 27433-TANK05-A01 Name of Designer: Vitor Egito de Castro Capacity: 2,178 Ltrs Compartments: 1 | Name: Sodium Bi-Sulfate Class(es): 8.2C, 8.3A | LONGVELD LIMITED 153 - 157 Ellis Street, Frankton, Hamilton 3204 | Certificate expiry is based on the mechanical design life of 25 yrs of cyclic use. Tank is destined for Aspiring Materials Addington Christchurch. | 2049-07-26
TNK20382 | 2024-07-31 | Plaspoke Limited / Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: 0117-PLASCT-01 - Single skinned 2450mm IDIA, 2670mm HOA x 15mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: PLASPOKE 0117-PLASCT-01 Sheets 1, 2, 4-6 rev D Name of Designer: Plaspoke Limited / Mech Eng Limited Capacity: 10830 litres max; 10000 litres SFL Compartments: 1 | Name: HYDROFLUOROSILICIC ACID 1.22sg Class(es): 8.2C, 8.3A | PLASPOKE LIMITED 35 Saleyards Road, Otahuhu, Auckland 1062 | Design in accordance with Mech Eng Limited Design Report 232361-RP01-Rev-A | 2029-07-31
TNK20383 | 2024-03-14 | Transtank |  | AS1692: 2006 | Description: TNTK403071-7-WADY-A01300173-1A CONTAINERISED DOUBLE SKINNED >110% SECONDARY CONTAINMENT Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: TransTank A000436-T12 GA Name of Designer: Transtank Capacity: 12,500 litres; SFL 11,200 litres Compartments: 1 | Name: Diesel & Combustible liquids AS1940 C1/C2 Class(es): 3.1D | AGGREKO (NZ) LIMITED 1048-1050 Great South Road, Mount Wellington, Auckland, 1060 | DOM 2012 | 2029-03-14
TNK20384 | 2024-08-06 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3314 - Self bunded HDPE, 1900mm DIA x 2573mm HOA x 12/24mm WT, SC >110% Design Specification: BS EN 12573 SWI Thermoplasic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: DWG-403842/03/201 Rev D; DWG- 405752/10/01 rev B Name of Designer: Mech Eng Limited Capacity: 5500 litres Max; 5000 litres SFL Compartments: 1 | Name: Sodium hydroxide (Caustic soda) 33% w/w aqueous solution max sg 1.35 Class(es):6.1D, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland, 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Mech Eng 231652-RP01-Rev-B | 2029-08-06
TNK20385 | 2024-08-06 | Tankreline NZ Limited |  | UL 1316 | Description: XRH-400016-T3: GRP Double skin 6.9m LOA x 2.5m DIA x 13m WT Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: TRL-DRW-XRH-T3-ADO-105; TRL-DRWXRH-T3-ADO-106 Name of Designer: Tankreline NZ Limited Capacity: 30,036 litres MAX - 28,354 SFL Compartments: 1 | Name: Petroleum Products Class(es):3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 130 Royal Road, Massey, Auckland, 0614 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has Hydroguard permanent interstitial monitoring system Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. Tank Owner (PCBU) requested operational SFL reduction to 27,000 litres. | 2029-08-06
TNK20386 | 2024-08-19 | Longveld Engineering |  | AS1692: 2006 | Description: Vertical 316 SS cone roof and bottom on legs. 9.180 m3 SFL Cat 5 Design Specification: AS 1692: 2006 Tank Type: Process Container Drawing Numbers: 27269-TANK 02-A01 Shts 1~3 Name of Designer: Longveld Engineering Capacity: 9.950 m3 (overflow) Compartments: 1 | Name: Dilute Nitric Acid <5.0% Class(es): 6.9A, 8.2C, 8.3A | LONGVELD LIMITED 153 Ellis Street, Frankton, Hamilton 3204 | This Tank is destined for TetraPak Maungatoroto. | 2074-08-20
TNK20387 | 2024-08-15 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3326 - Single skinned HDPE, 2000mm DIA x 2800mm HOA x 15/30mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Chemfeed DWG-403909/04-10-rev C Name of Designer: Mech Eng Limited Capacity: 7700 litres Max; 7000 litres SFL Compartments: 1 | Name: Sodium hydroxide (Caustic soda) 33% w/w aqueous solution max sg 1.35 Class(es): 6.1D, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report 231814-RP01-rev-C | 2029-08-15
FAB0098 | 2024-10-25 |  | PARRATECH GROUP PTY LIMITED PO Box 6823, Baulkham Hills BC, NewSouth Wales, Australia, 2153 71 Anzac Street, Chullora, Sydney, NewSouth Wales, Australia, 2190 |  | Approved for the shop fabrication of steel tanks up to maximum gross capacity of 60,000 litres in accordance with AS 1692-2006. Reference: TNK20396 | Diesel having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B | PARRATECH GROUP PTY LIMITED PO Box 6823, Baulkham Hills BC, NewSouth Wales, Australia, 2153 71 Anzac Street, Chullora, Sydney, NewSouth Wales, Australia, 2190 | Fabrication, inspection and testing in accordance with the specified tank design and fabrication code, approved tank design drawings and approved for construction drawings. Allocation of unique individual tank serial number to be stamped on each individual tank and recorded. Retention of individual tank fabrication, testing records and QA records for each tank. The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the compliance certifier who issued the compliance certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2027-10-25 | Fabricator of: TNK20396
TNK20388 | 2024-12-04 | Fuel Storage Limited | Fuel Storage Limited 700 Bond Road PO Box 108 Te Awamutu 3840 FAB0050 | SWRI 95-03 FAB0050 | Description: Horizontal Multi-Hazard UL142 SWI Reduced Secondary Conatainment Design Specification: SWRI 95-03 Tank Type: Above Ground Stationary Tank Name of Designer: Fuel Storage Limited Capacity: 1,000 L, 2,000 L, 3,000 L, 5,000 L, 7,500 L, 10,000 L, 20,000 L, 30,000 L, 40,000 L, 60,000 L, 80,000 L, 100,000 L. Compartments: 1 | Name: Alpine (Low Flash) Diesel Class(es): 3.1C, 6.7B Name: Diesel Class(es): 3.1D, 6.7B Name: Jet Fuel (Kerosene) Class(es): 3.1C Name: Petrol Class(es): 3.1A, 6.7B | Fuel Storage Limited 700 Bond Road, Te Awamutu 3800 | Multihazard tanks when supplying burner or engine systems supply to have an anti-siphon device installed immediately adjacent to the tank. TNK20388 applies to the following designs: FSL VMH1000-0C-01, Rev C, Vulcan Multi-Hazard Tank Range Tank Size 1,000L FSL VMH2000-0C-01, Rev C, Vulcan Multi-Hazard Tank Range Tank Size 2,000L FSL VMH3000-0C-01, Rev C, Vulcan Multi-Hazard Tank Range Tank Size 3,000L FSL VMH5000-0C-01, Rev C, Vulcan Multi-Hazard Tank Range Tank Size 5,000L FSL VMH7500-0C-01, Rev C, Vulcan Multi-Hazard Tank Range Tank Size 7,500L FSL VMH10000-0C-01, Rev C, Vulcan Multi-Hazard Tank Range Tank Size 10,000L FSL VMH20000-0C-01, Rev C, Vulcan Multi-Hazard Tank Range Tank Size 20,000L FSL VMH30000-0C-01, Rev C, Vulcan Multi-Hazard Tank Range Tank Size 30,000L FSL VMH40000-0C-01, Rev C, Vulcan Multi-Hazard Tank Range Tank Size 40,000L FSL VMH60000-0C-01, Rev C, Vulcan Multi-Hazard Tank Range Tank Size 60,000L FSL VMH80000-0C-01, Rev C, Vulcan Multi-Hazard Tank Range Tank Size 80,000L FSL VMH100000-0C-01, Rev C, Vulcan Multi-Hazard Tank Range Tank Size 100,000L | 2074-12-04 | FAB0050
TNK20389 | 2024-09-02 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T3383 Integral Secondary Containment HDPE 1800mm IDIA x 2573mm HOA x 12/20mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: PROMINENT 406090/10/01 rev A Name of Designer: Mech Eng Limited Capacity: 5500 litres Max; 5000 litres SFL Compartments: 1 | Name: Sodium hydroxide (Caustic soda) 30% w/w aqueous solution max sg 1.306 Class(es): 6.1D, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design in accordance with Mech Eng Report 241861-RP01-Rev A | 2029-09-02
TNK20390 | 2024-09-02 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T3379 HDPE Integral secondary containment >110%, 2450mm IDIA x 2510mm H x 15/30mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering 7522-001 rev 2 Name of Designer: Mech Eng Limited Capacity: 10937 litres max; 10414 litres SFL Compartments: 1 | Name: Aluminium sulphate aqueous solution 1.33 s.g. maximum Class(es): 8.1A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Design in accordance with Mech Eng Ltd 241841-RP01-Rev A Construction in accordance with Plastics Constructions QA April 2023 | 2029-09-02
TNK20391 | 2024-08-26 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3221 Single Skinned HDPE 2038mm DIA x 2217mm HOA x 12/15/25mmWT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering 78-TK-01 Name of Designer: Mech Eng Limited Capacity: 5700 litres MAX; 5390 litres SFL Compartments: 1 | Name: Hydrofluorosilic acid aqueous solution maximum 1.3 s.g. Class(es):6.1D, 8.1A, 8.2C, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation Mech Eng Limited Design Report 211855-RP01-rev-A | 2029-08-26
TNK20392 | 2024-09-18 | Totara Engineering |  | AS1692: 2006 | Description: Tank #235; 316 Stainless Steel Vertical cylinder single skinned, 2120 DIA x 3000mm H x 4mm WT Design Specification: AS 1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: Protech 9828 Rev C Name of Designer: Totara Engineering Capacity: 10,310 litres Max, 10,000 litres SFL | Name: Sulphuric acid 98%, s.g. 1.9 Class(es): 6.1D, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A | PROTECH STAINLESS LIMITED 40 Te Kowhai Road East, Burbush, Hamilton 3288 |  | 2029-09-18
TNK20393 | 2024-09-26 | Mercer Engineering | Mercer Stainless Limited 53 Lunns Road Middleton Christchurch 8024 FAB0077 | AS1692: 2006 | Description: CH17229: Single skin vertical cylinder, 316 S/S 2750mm DIA x 4342 mm HOA Category 5 FAB0077 Design Specification: AS 1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: Mercer 15506A, 15509A, 15516A, 15517A, 15519A Name of Designer: Mercer Engineering Capacity: 18000 L, 17500 L SFL | Name: Frame-Pro Class(es): 6.1D, 6.8B, 8.3A | MHM AUTOMATION LIMITED 53 Lunns Road, Middleton, Christchurch 8024 | DOM April 2012 | 2029-09-26 | FAB0077
TNK20394 | 2024-09-26 | Mercer Engineering | Mercer Stainless Limited 53 Lunns Road Middleton Christchurch 8024 FAB0077 | AS1692: 2006 | Description: CH17228: Single skin vertical cylinder; 316 S/S 2750mm DIA x 6666 mm HOA Category 5 FAB0077 Design Specification: AS 1692:2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: Mercer 15540A; 15541A; 15546A; 15547A; 15549A Name of Designer: Mercer Engineering Capacity: 27500 litres, 25000 litres SFL | Name: CCA Oxide ; Arsenic acid concentrate Class(es): 6.1B, 6.1C, 6.5A, 6.6A, 6.7A, 6.8A, 6.9A, 8.1A, 8.2B, 8.3A | MHM AUTOMATION LIMITED 53 Lunns Road, Middleton, Christchurch 8024 | DOM April 2012 | 2029-09-26 | FAB0077
TNK20395 | 2024-09-26 | Mercer Engineering | Mercer Stainless Limited 53 Lunns Road Middleton Christchurch 8024 FAB0077 | AS1692: 2006 | Description: CH17230: Single skin vertical cylinder; 316 S/S 2500mm DIA x 8133mm HOA Category 5, FAB0077 Design Specification: AS 1692:2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: Mercer 15550A; 15551A; 15556A; 15557A; 15559A Name of Designer: Mercer Engineering Capacity: 30000 litres; 28500 litres SFL. | Name: CCA RTU <6% aqueous solution Class(es): 6.1D, 6.5A, 6.6A, 6.7A, 6.8A, 6.9B, 8.3A | MHM AUTOMATION LIMITED 53 Lunns Road, Middleton, Christchurch 8024 | DOM April 2012 | 2029-09-26 | FAB0077
TNK20396 | 2024-06-14 | Parratech Group Pty Limited | PARRATECH GROUP PTY LIMITED 71 Anzac Street, Chullora, Sydney, New South Wales, Australia 2190 FAB0098 | AS1692: 2006 | Description: 41,853 Litres rectangular above grounddouble skin generator base tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stati onary Tank Drawing Numbers: P2602-DC-331.01, Rev A, Generator RoomBase Tank GA, Date: 22.04.24, By: MC Name of Designer: Parratech Group Pty Limited Capacity: 41,853 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | PARRATECH GROUP PTY LIMITED 71 Anzac Street, Chullora, Sydney, New South Wales, Australia 2190 | This Design Compliance Certificate applies to Parratech tank serial numbers: 003725, 003726, 003727, 003728, 003729 & 003730. Design Specification: AS 1692:2006, Category 3. Manufacturer: Parratech Group Pty Limited. Date of Manufacture: Name Plate. Maximum Safe Fill Level = 38,500 Litres (1,100mm). Approved For: The storage and transfer of Diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved for supplying an engine or burner. If supplying an engine or burner approved for use with diesel only having a flash point greater than 60 deg C but less than or equal to 93 deg C. | 2034-06-14 | FAB0098
TNK20397 | 2024-10-22 | Hendl & Murray Engineering Limited andTom Roberts | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton 3206 | AS1692: 2006 FAB0033 | Description: 2,473 Litres above ground, single skin,vertical, cylindrical, cone top, cone base process container Design Specification: AS1692: 2006 Tank Type: Process Container Drawing Numbers: 23299-04-01, Rev E, 2m3 CIP Tank, Drawn:M.Singh, Date: 17/10/24 Name of Designer: Hendl & Murray Engineering Limited and Tom Roberts Capacity: 2,473 Litres Compartments: 1 | Name: Nitric Acid - Maximum concentration 0.8% Class(es): 6.9B, 8.1A, 8.2C, 8.3A | HENDL & MURRAY ENGINEERING LIMITED 103 Tawa Street, Melville, Hamilton 3206 | Maximum Safe Fill Level = 1,200mm (2,000 Litres). Approved For: The storage, transfer and process of Nitric acid, 0.8% aqueous solution, having a hazard classification of 6.9B, 8.1A, 8.2C, 8.3A and Sodium Hydroxide, 1.2% aqueous solution, having a hazard classification of 6.3A, 6.4A. References: Producer Statement - PS1 - Design - 242033, Issued By: Mech Eng Ltd, To: The Tatua Co-operative Dairy Company Ltd, Signed By: Tom Roberts (CPEng #1024350), Date: 02-Oct-24. Design Report: 242033 RP01 RevA 2m³ CIP Tank Design Report, Issued By: Mech Eng Ltd, To: Hendl & Murray Engineering Ltd, Author: Tom RobertsCPEng MEng CMEngNZ, Revision A, Date: 02-Oct-24. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards | 2034-10-22 | FAB0033
FAB0099 | 2024-09-24 |  | PETROLEUM SOLUTIONS 2024 LIMITED 10 Kitchener Street, Dunedin Central, Dunedin, 9016 PO Box 238, Dunedin, Dunedin Central, Dunedin, 9054 |  | Above-ground tanks in accordance with AS1692 and reduced secondary containment for certain above-ground stationary tanks - Safe Work Instrument 2017 up to 100,000 Litres for which TNKs have been assigned. Reference: TNK0730 – 500 L to 60,000L DS & SS, AS1692, petrol & diesel TNK0741 – 1,000 L, AS1692, 3.1D, 6.1E, 6.7B, 9.1B (diesel) TNK0742 – 2,500 L, AS1692, 3.1D, 6.1E, 6.7B, 9.1B (diesel) TNK0872 – 7,400 L, AS1692, Cat 3, 3.1D, 6.1E, 6.7B, 9.1B (diesel) | Flammable liquids 3.1A, 3.1B, 3.1C or 3.1D | PETROLEUM SOLUTIONS 2024 LIMITED 10 Kitchener Street, Dunedin Central, Dunedin, 9016 PO Box 238, Dunedin, Dunedin Central, Dunedin, 9054 | The following additional conditions apply: WorkSafe NZ requires the fabricator to record: 1. A shop traveller for each batch of tanks filled out and signed at each production stage including: a. Material/fittings purchase b. Construction of tank shell(s) c. Attachment of fittings (including vents) d. Leak test e. Calibration f. Markings g. Inspection of finished tank/tank wagon including final QA A copy of each of these records must be retained by the importer for a period of 10 years. 2. A desk top review (i.e. a review of records/recently fabricated tanks) is to be undertaken six monthly by a suitably qualified person. The results of this review, if the review is not undertaken by the compliance certifier who issued the compliance certificate, are to be communicated to the certifier who issued the certificate. A copy of this review must be forwarded to WorkSafe NZ. The register number is limited to the fabrication facility described on the certificate. In the event the ownership changes or the facility is relocated, the register number is invalidated and a new register number must be obtained. | 2027-09-24 | Fabricator of: TNK0730 TNK0741 TNK0742 TNK0872
TNK20398 | 2024-10-24 | McIntyre Engineering |  | AS 1692 SWI Reduced Secondary Containment for Tanks | Description: Category 2, Octagonal section, 1530mm LOA, double skinned, integral secondary containment <110%. Design Specification: AS 1692 SWI Reduced Secondary Containment for Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: McIntyre ME20103 Name of Designer: McIntyre Engineering Capacity: 997 litres max; 947 litres SFL | Name: Diesel Class(es) 3.1D | AJ HACKETT BUNGY NEW ZEALAND LIMITED 1693 Gibbston Highway, Gibbston, Queenstown, 9371 | Date of Manufacture 2013 | 2029-10-24
TNK20399 | 2024-10-28 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T3382 HDPE Single skinned,2810mm IDIA x 3700mm HOA x 25/45mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: H2O Engineering 7765-001-A Name of Designer: Mech Eng Limited Capacity: 19215 max litres; 18285 SFL litres Compartments: 1 | Name: Sulphuric acid 77% aqueous concentration, s.g. 1.69 Class(es): 6.1D, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Design in accordance with Mech Eng Ltd 241961-RP01-Rev-A. Construction in accordance with Plastics Constructions QA April 2023 | 2029-10-28
TNK20400 | 2024-11-04 | TRL Engineering Pty Ltd |  | UL 1316:1994 (2nd Edition) | Description: Z-100914-T1 / Z Five Cross Roads, Double skinned GRP 6.9m LOA 2.4 m DIA. Design Specification: UL 1316: 1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-100914-T1-95-F101; Z-100914-T1-95-F102 Name of Designer: TRL Engineering Pty Ltd Capacity: 28,832 L / 27,300 SFL L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 243 Peachgrove Road, Fairfield, Hamilton 3214 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has permanent hydroguard interstitial monitoring.. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2029-11-04
TNK20401 | 2024-11-04 | TRL Engineering Pty Ltd |  | UL 1316:1994 (2nd Edition) | Description: Z-100914-T2 / Z Five Cross Roads, Double skinned GRP 11.7m LOA 2.4 m DIA. Design Specification: UL 1316: 1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-100914-T2-91-F103; Z-100914-T2-91-F104 Name of Designer: TRL Engineering Pty Ltd Capacity: 50,031 L / 47,500 SFL L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 243 Peachgrove Road, Fairfield, Hamilton 3214 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has permanent hydroguard interstitial monitoring.. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2029-11-04
TNK20402 | 2024-11-04 | TRL Engineering Pty Ltd |  | UL 1316:1994 (2nd Edition) | Description: Z-100914-T3 / Z Five Cross Roads, Double skinned GRP 9.3m LOA 2.4 m DIA. Design Specification: UL 1316: 1994 (2nd Edition) Tank Type: Below Ground Stationary Tank Drawing Numbers: Z-100914-T3-ADO-F105; Z-100914-T3-ADO-F106 Name of Designer: TRL Engineering Pty Ltd Capacity: 39,900 L / 37,9000 SFL L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Z ENERGY LIMITED 243 Peachgrove Road, Fairfield, Hamilton 3214 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has permanent hydroguard interstitial monitoring.. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2029-11-04
TNK20403 | 2024-11-21 | Plaspoke Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: 0133-PLASCT-01, HDPE Double skinned vertical cylinder, 2370mm IDIA x 2550mm HOA x 15/27mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plaspoke 10KL-Acetic Acid-IL3-0133 PLASCT-01 Sheets 1-7 Name of Designer: Plaspoke Limited / Mech Eng Limited Capacity: 10521 litres maximum; 10000 litres SFL Compartments: 1 | Name: Acetic acid 49% 6.1D, 6.9B, Class(es): 8.1A, 8.2C, 8.3A | Plaspoke Limited 35 Saleyards Road, Otahuhu, Auckland, 1062 | Design in accordance with Mech Eng Report 242141-RP01-Rev-A | 2029-11-21
TNK20404 | 2024-11-21 | PLASTICS CONSTRUCTIONS LIMITED |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T3317-Vertical cylinder double contained, 1800mm IDA x 2638mm HOA x 12/24mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Chemfeed 403642/01/10-A Name of Designer: Mech Eng Limited Capacity: 5500 litres Max; 5000 litres SFL Compartments: 1 | Name: FramePro(TM) HSR000907 Class(es): 6.1D, 6.8B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland,1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design in accordance with Mech Eng Report 242191-RP01-Rev-C | 2029-11-21
TNK20405 | 2024-11-27 | Ross Process Equipment |  | Design Verified to AS3990 and AS1210 | Description: SE2203-RB42B-62.5 Jacketed ribbon blender 1178mm wide x 2439mm long. Design Specification: Design Verified to AS3990 and AS1210 Tank Type: Process Container Drawing Numbers: Ross Process Equipment PA12106F RB42B-62.5 General Assembly Name of Designer: Ross Process Equipment Capacity: 2038 L max; 1769 L SFL | Name: n-Butyl acetate Class(es): 3.1B, 3.1C, 6.1D | RESIN & WAX HOLDINGS LIMITED 214 Sandhills Road, Awanui 0483 | Engineering Design Verification by Tom Roberts of Mech Eng Limited Certificate 232351 Design Verified to AS3990 and AS1210. | 2029-11-27
TNK20406 | 2024-11-27 | Ross Process Equipment |  | Design Verified to AS3990 and AS1210 | Description: SE2202-RB42B-62.5 Jacketed ribbon blender 1178mm wide x 2439mm long. Design Specification: Design Verified to AS3990 and AS1210 Tank Type: Process Container Drawing Numbers: Ross Process Equipment PA12106F RB42B-62.5 General Assembly Name of Designer: Ross Process Equipment Capacity: 2038 L max; 1769 L SFL | Name: n-Butyl acetate Class(es): 3.1B, 3.1C, 6.1D | RESIN & WAX HOLDINGS LIMITED 214 Sandhills Road, Awanui 0483 | Engineering Design Verification by Tom Roberts of Mech Eng Limited Certificate 232351 Design Verified to AS3990 and AS1210. | 2029-11-27
TNK20407 | 2024-12-02 | TIRA NDA Engineering |  | Design conforms to AS1210 in addition to AS1692 | Description: SE2404-Vertical cylindrical process vessel, 900mm DIA x 2370mm H x 5mm WT 316 Stainless Steel. Design Specification: Design conforms to AS1210 in addition to AS1692 Tank Type: Process Container Drawing Numbers: TIRA NDA 7267903-A04-J; 7267903-A05-D Name of Designer: TIRA NDA Engineering Capacity: 1500 L maximum; 1200 L operational | Name: Heptane Class(es): 3.1B, 6.9B Name: Methanol Class(es): 3.1B, 6.1C, 6.8B, 6.9A Name: n-Butyl acetate Class(es): 3.1B, 3.1C, 6.1D | RESIN & WAX HOLDINGS LIMITED 214 Sandhills Road, Awanui 0483 | Design conforms to AS1210 in addition to AS1692. Design verified by Mech Eng Limited report 242381 RP01-Rev A. Construction by TIRA NDA Engineering | 2029-12-02
TNK20408 | 2024-11-05 | Plaspoke Limited/Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#0127-PLASCT-01, Vertical cylinder, single skinned, 2750mm DIA x 2822mm H x 15/30mm WT. Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plaspoke 15KL 0127-PLASTCT-01-C Name of Designer: Plaspoke Limited / Mech Eng Limited Capacity: 15,780 litres maximum; 15,000 litres SFL Compartments: 1 | Name: Aluminium sulphate aqueous solution 1.33 s.g. maximum Class(es): 6.1D, 8.1A, 8.3A | Plaspoke Limited 35 Saleyards Road, Otahuhu, Auckland,1062 | Design in accordance with Mech Eng Limited Design Report 241891-RP01-Rev-A | 2029-11-05
TNK20409 | 2024-11-21 | Plaspoke Limited / Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#0132-PLASCT-01, Vertical cylinder, single skinned,1890mm DIA x 2200mm H x 12mm WT. Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plaspoke 5KL 0132-PLASTCT-01-E Name of Designer: Plaspoke Limited / Mech Eng Limited Capacity: 5387 litres maximum; 5000 litres SFL Compartments: 1 | Name:Aluminium sulphate 28% aqueous solution 1.33 s.g. maximum Class(es):6.1D, 8.1A, 8.3A | Plaspoke Limited 35 Saleyards Road, Otahuhu, Auckland,1062 | Design in accordance with Mech Eng Limited Design Report 242091-RP01-Rev-A | 2029-11-21
TNK20410 | 2024-12-05 | Dairy Technology Services Limited |  | Design Verified to AS3990 and AS1210 | Description: TK3201; Category 5, 1530mm DIA x 3000mm Shell x 2.5mm/3mm WT 304L Stainless steel, jacketed. Design Specification: Design Verified to AS3990 and AS1210. Tank Type: Process Container Drawing Numbers: DTS 2554-001 Shts 2, 5, 8; and DTS 2554-003 sht 9 Name of Designer: Dairy Technology Services Limited Capacity: 5852 L maximum; 4300 L operating | Name: Methanol Class(es): 3.1B, 6.1C, 6.8B, 6.9A | RESIN & WAX HOLDINGS LIMITED 214 Sandhills Road, Awanui 0483 | Engineering Design Verificaton Mech Eng Limited Report 2RP01-Rev B Design Verified to AS3990 and AS1210. One off tank design. | 2029-12-05
TNK20411 | 2024-12-05 | Dairy Technology Services Limited |  | AS1692: 2006 | Description: TK-5401; Category 5; 316 Stainless Steel; 1881mm DIA x 2000mm H x 3110mm HOA x 4mm WT Design Specification: AS 1692 :2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: DTS; 2553-001 Sheets 1,4,6 rev 13 Name of Designer: Dairy Technology Services Limited Capacity: 5690 L maximum; 5500 L SFL | Name: Heptane Class(es): 3.1B | RESIN & WAX HOLDINGS LIMITED 214 Sandhills Road, Awanui 0483 | Mech Eng Design Report 231471-1 RP01 rev D One off design. | 2029-12-05
TNK20412 | 2024-12-05 | Dairy Technology Services Limited |  | AS1692: 2006 | Description: TK-5301; Category 5; 316 Stainless Steel; 1881mm DIA x 2000mm H x 3110mm HOA x 4mm WT Design Specification: AS 1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: DTS; 2553-001 Sheet 2,4,6, Rev 13 Name of Designer: Dairy Technology Services Limited Capacity: 5690 L maximum; 5500 L SFL | Name: Methanol Class(es): 3.1B, 6.1C, 6.8B, 6.9A | RESIN & WAX HOLDINGS LIMITED 214 Sandhills Road, Awanui 0483 | Mech Eng Design Report 231471-2 RP01 rev C One off design. | 2029-12-05
TNK20413 | 2024-12-05 | Dairy Technology Services Limited |  | Design Verified to AS3990 and AS1210 | Description: TK3304; Category 5, 1530mm DIA x 3000mm Shell x 2.5mm/3mm WT 304L Stainless steel, jacketed Design Specification: Design Verified to AS3990 and AS1210. Tank Type: Process Container Drawing Numbers: DTS 2554-001 sht 3; 2554-003 sht 10; 2554-012 sht 18 rev 6 Name of Designer: Dairy Technology Services Limited Capacity: 5852 L maximum; 4300 L operating | Name: Heptane Class(es): 3.1B | RESIN & WAX HOLDINGS LIMITED 214 Sandhills Road, Awanui 0483 | Engineering Design Verificaton Mech Eng Limited Report 231472-3 RP01-Rev A Design Verified to AS3990 and AS1210. One off design. | 2029-12-05
TNK20414 | 2024-12-05 | Dairy Technology Services Limited |  | AS1692: 2006 | Description: TK-5201; Category 5; 316 Stainless Steel; 1881mm DIA x 2000mm H x 3110mm HOA x 4mm WT Design Specification: AS 1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: DTS 2553-001 Sheet 3,5,7 Rev 13 Name of Designer: Dairy Technology Services Limited Capacity: 5690 L maximum; 5500 L SFL | Name: n-Butyl acetate Class(es): 3.1B, 3.1C, 6.1D | RESIN & WAX HOLDINGS LIMITED 214 Sandhills Road, Awanui 0483 | Mech Eng Design Report 231471-3 RP01 rev C One off design. | 2029-12-05
TNK20415 | 2024-12-05 | Dairy Technology Services Limited |  | Design Verified to AS3990 and AS1210. | Description: TK-3303; Category 5, 1530mm DIA x 2000m Shell x 2.5mm/3mm WT 304L Stainless steel, jacketed. Design Specification: Design Verified to AS3990 and AS1210. Tank Type: Process Container Drawing Numbers: DTS 2554-001 Shts 1, 4, 11; 2554-003 sht 7 Name of Designer: Dairy Technology Services Limited Capacity: 4010 L maximum; 3000 L operating | Name: Heptane Class(es): 3.1B | RESIN & WAX HOLDINGS LIMITED 214 Sandhills Road, Awanui 0483 | Engineering Design Verificaton Mech Eng Limited Report 231472-1 RP01-Rev A Design Verified to AS3990 and AS1210. One off design. | 2029-12-05
TNK20416 | 2023-09-07 | Go Industrial Pty Ltd |  | AS1692: 2006 | Description: BOX range of Self Bunded Tanks Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Go Industrial Pty Ltd Gross Volume: 260 L Safe Fill Level: 240 L | Name: Diesel, Lubricants or Waste Oil Class(es): 3.1D | GO INDUSTRIAL PTY LTD Suite 15229 17B Farnham Street Parnell Auckland 1052 New Zealand | Approved to supply a burner only to meet certification requirements under Part 17 of the Health and Safety at Work (Hazardous Substances) Regulations 2017. Hazardous substances with a maximum specific gravity of 1. | 2033-09-09
TNK20417 | 2023-09-07 | Go Industrial Pty Ltd |  | AS1692: 2006 | Description: BOX range of Self Bunded Tanks Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Go Industrial Pty Ltd Gross Volume: 390 L Safe Fill Level: 350 L | Name: Diesel, Lubricants or Waste Oil Class(es): 3.1D | GO INDUSTRIAL PTY LTD Suite 15229 17B Farnham Street Parnell Auckland 1052 New Zealand | Approved to supply a burner only to meet certification requirements under Part 17 of the Health and Safety at Work (Hazardous Substances) Regulations 2017. Hazardous substances with a maximum specific gravity of 1. | 2033-09-09
TNK20418 | 2023-09-07 | Go Industrial Pty Ltd |  | AS1692: 2006 | Description: BOX range of Self Bunded Tanks Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Go Industrial Pty Ltd Gross Volume: 660 L Safe Fill Level: 600 L | Name: Diesel, Lubricants or Waste Oil Class(es): 3.1D | GO INDUSTRIAL PTY LTD Suite 15229 17B Farnham Street Parnell Auckland 1052 New Zealand | Approved to supply a burner or internal combustion engine only to meet certification requirements under Part 17 of the Health and Safety at Work (Hazardous Substances) Regulations 2017. Hazardous substances with a maximum specific gravity of 1. | 2033-09-09
TNK20419 | 2023-09-07 | Go Industrial Pty Ltd |  | AS1692: 2006 | Description: BOX range of Self Bunded Tanks Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Go Industrial Pty Ltd Gross Volume: 1,100 L Safe Fill Level: 1,000 L | Name: Diesel, Lubricants or Waste Oil Class(es): 3.1D | GO INDUSTRIAL PTY LTD Suite 15229 17B Farnham Street Parnell Auckland 1052 New Zealand | Approved to supply a burner or internal combustion engine only to meet certification requirements under Part 17 of the Health and Safety at Work (Hazardous Substances) Regulations 2017. Hazardous substances with a maximum specific gravity of 1. | 2033-09-09
TNK20420 | 2023-09-07 | Go Industrial Pty Ltd |  | AS1692: 2006 | Description: BOX range of Self Bunded Tanks Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Go Industrial Pty Ltd Gross Volume: 2,250 L Safe Fill Level: 2,000 L | Name: Diesel, Lubricants or Waste Oil Class(es): 3.1D | GO INDUSTRIAL PTY LTD Suite 15229 17B Farnham Street Parnell Auckland 1052 New Zealand | Approved to supply a burner or internal combustion engine only to meet certification requirements under Part 17 of the Health and Safety at Work (Hazardous Substances) Regulations 2017. Hazardous substances with a maximum specific gravity of 1. | 2033-09-09
TNK20421 | 2023-09-07 | Go Industrial Pty Ltd |  | AS1692: 2006 | Description: BOX range of Self Bunded Tanks Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Go Industrial Pty Ltd Gross Volume: 3,300 L Safe Fill Level: 3,000 L | Name: Diesel, Lubricants or Waste Oil Class(es): 3.1D | GO INDUSTRIAL PTY LTD Suite 15229 17B Farnham Street Parnell Auckland 1052 New Zealand | Approved to supply a burner or internal combustion engine only to meet certification requirements under Part 17 of the Health and Safety at Work (Hazardous Substances) Regulations 2017. Hazardous substances with a maximum specific gravity of 1. | 2033-09-09
TNK20422 | 2023-09-07 | Go Industrial Pty Ltd |  | AS1692: 2006 | Description: BOX range of Self Bunded Tanks Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Go Industrial Pty Ltd Gross Volume: 4,500 L Safe Fill Level: 4,000 L | Name: Diesel, Lubricants or Waste Oil Class(es): 3.1D | GO INDUSTRIAL PTY LTD Suite 15229 17B Farnham Street Parnell Auckland 1052 New Zealand | Approved to supply a burner or internal combustion engine only to meet certification requirements under Part 17 of the Health and Safety at Work (Hazardous Substances) Regulations 2017. Hazardous substances with a maximum specific gravity of 1. | 2033-09-09
TNK20423 | 2023-09-07 | Go Industrial Pty Ltd |  | AS1692: 2006 | Description: BOX range of Self Bunded Tanks Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Go Industrial Pty Ltd Gross Volume: 5,500 L Safe Fill Level: 5,000 L | Name: Diesel, Lubricants or Waste Oil Class(es): 3.1D | GO INDUSTRIAL PTY LTD Suite 15229 17B Farnham Street Parnell Auckland 1052 New Zealand | Hazardous substances with a maximum specific gravity of 1. | 2033-09-09
TNK20424 | 2023-09-07 | Go Industrial Pty Ltd |  | AS1692: 2006 | Description: BOX range of Self Bunded Tanks Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Go Industrial Pty Ltd Gross Volume: 6,600 L Safe Fill Level: 6,000 L | Name: Diesel, Lubricants or Waste Oil Class(es): 3.1D | GO INDUSTRIAL PTY LTD Suite 15229 17B Farnham Street Parnell Auckland 1052 New Zealand | Hazardous substances with a maximum specific gravity of 1. | 2033-09-09
TNK20425 | 2023-09-07 | Go Industrial Pty Ltd |  | AS1692: 2006 | Description: BOX range of Self Bunded Tanks Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Go Industrial Pty Ltd Gross Volume: 8,800 L Safe Fill Level: 8,000 L | Name: Diesel, Lubricants or Waste Oil Class(es): 3.1D | GO INDUSTRIAL PTY LTD Suite 15229 17B Farnham Street Parnell Auckland 1052 New Zealand | Hazardous substances with a maximum specific gravity of 1. | 2033-09-09
TNK20426 | 2023-09-07 | Go Industrial Pty Ltd |  | AS1692: 2006 | Description: BOX range of Self Bunded Tanks Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Name of Designer: Go Industrial Pty Ltd Gross Volume: 11,000 L | Name: Diesel, Lubricants or Waste Oil Class(es): 3.1D | GO INDUSTRIAL PTY LTD Suite 15229 17B Farnham Street Parnell Auckland 1052 New Zealand | Hazardous substances with a maximum specific gravity of 1. | 2033-09-09
TNK20427 | 2024-11-05 | Plaspoke Limited / Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#0131-PLASCT-01, Vertical cylinder, single skinned, 2800mm DIA x 2744mm H x 15/30mm WT. Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plaspoke 15KL 0131-PLASTCT-01-E Name of Designer: Plaspoke Limited / Mech Eng Limited Capacity: 16,057 litres maximum; 15,000 litres SFL Compartments: 1 | Name:Sodium hydroxide (Caustic soda) 30% w/w aqueous solution Class(es):6.1D, 8.1A, 8.2B, 8.3A | Plaspoke Limited 35 Saleyards Road, Otahuhu, Auckland, 1062 | Design in accordance with Mech Eng Limited Design Report 242092-RP01-Rev-B | 2029-11-05
TNK20428 | 2024-12-17 | Longveld Limited |  | AS 1692:2006 | Description: Vertical 316 SS cone roof on legs Design Specification: AS 1692 Tank Type: Process Container Drawing Numbers: 27434-TANK 03-A01 Rev 6; 27434-TANK 03-NP; LV_VENT-150-A001. Name of Designer: Longveld Engineering Capacity: 3,600 Ltrs Compartments: 1 | Name: 1% Nitric Acid, Class(es): 6.9B, 8.1A, 8.2C, 8.3A | Longveld Limited 153 - 157 Ellis Street, Frankton, Hamilton, 3204 | This tank is for CIP wash at OCD Waharoa Waikato. The 1260mm diameter floor is reduced in thickness to 3mm with added stiffening to AS1210 requirements to allow a knuckle joint floor to shell. The vessel's cyclic design life is 25 years. TNK20428 | 2049-12-17
TNK20429 | 2025-01-06 | MASKELL PRODUCTIONS LIMITED |  | UL 1316 | Description: J21909-D2; Double-skinned GRP, 1200mm DIA x 2100mm LOA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Maskell, Envirotank 1037.02.08 rev 6 - J21909 Name of Designer: Maskell Productions Limited Capacity: 2140 litres maximum; 2000 litres SFL | Name: Pipeline pigging washings; Used and waste transmission oil and non-flammable fuel oil. Class(es): 3.1D, 6.7B | MASKELL PRODUCTIONS LIMITED 24 Bowden Road, Mount Wellington, Auckland, 1060 | Design Report John M Clark 1.0-Oct-01, 2024. Includes classifications of 6.3B and 9.1C which do not require certification under these Regulations. This Stationary Container Design Certificate has been issued retrospectively for the fabrication of the tank in 2024. | 2030-01-06
TNK20430 | 2024-12-16 | Page & Macrae Limited |  | AS1692: 2006 | Description: 01TK1000; Category 5; 304L Stainless Steel 3100mm H x 2220mm DIA x 4mm WT Design Specification: AS 1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: Lincoln Taylor 5687 Sht 1 Name of Designer: Page & Macrae Limited Capacity: 10447 L maximum; 9925 L SFL | Name: Ethanol Class(es): 3.1B | Pure Bottling (NZ) Limited 129 Maleme Street, Greerton, Tauranga 3112 | This tank is a one off construction and certified retrospectively for the tank constructed in 2018. | 2029-12-16
TNK20431 | 2025-01-06 | TIRA Group Limited |  | API Standard 650 | Description: Vertical 304 SS cone roof on concrete foundation Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: 7175901-G01~7175901-G02; 7175901-A01~A05; 7175901-A21~A23; 7175901-D01~D02, D15.1 Name of Designer: TIRA Capacity: 1,000,000 L | Name: Sodium Hydroxide 50% Class(es): 8.1A, 8.2B, 8.3A | TIRA GROUP LIMITED 709 Te Rapa Road, Te Rapa, Hamilton 3200 | Tank is for IXOM Timaru, 7 Charman St. Timaru 7910. Design life is 50 years. | 2075-01-06
TNK20432 | 2025-01-16 | Mainline Sheetmetals Limited | Mainline Sheetmetals Limited 209 Ellis Street, Frankton, Hamilton, 3204 FAB0018 | AS 1692 SWI Reduced Secondary Containment for Tanks | Description: Tank No. 1609-56812; Double-skinned 1800mm DIA x 1850mm LOA x 5/6mm WT Category 4. Design Specification: AS 1692 SWI Reduced Secondary Containment for Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: APD INNER-M2-568-2; APD OUTER-M2- 568-2 Name of Designer: Mainline Sheetmetals Limited Capacity: 4800 litres max 4560 litres SFL | Name: Diesel Class(es): 3.1D, 6.9B | Mainline Sheetmetals Limited 209 Ellis Street, Frankton, Hamilton, 3204 | This a one off-Stationary Container Tank Design Certificate and is issued retrospectively for the tank manufactured in 2006. | 2030-01-16 | FAB0018
TNK20433 | 2025-01-23 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T3405; HDPE Single skinned 2900mm DIA x 3500mm H x 20mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Prominent 270/02/10 rev D Name of Designer: Mech Eng Limited Capacity: 22,000 litres maximum; 20,000 litres SFL Compartments: 1 | Name: Acetic acid 49% s.g. 1.025 Class(es): 6.1D, 6.9B, 8.1A, 8.2C, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland, 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design in accordance with Mech Eng 242221-RP01- rev B This certificate is issued retrospectively for the tank manufactured in 2024. | 2030-01-23
TNK20434 | 2025-01-23 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T3408; HDPE Single Skinned 2300mm DIA x 2800mm H x 15mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Prominent 270/05/10 rev B Name of Designer: Mech Eng Limited Capacity: 11,000 litres maximum; 10,000 litres SFL Compartments: 1 | Name: Citric acid 50% aqueous solution 1.25 s.g. Class(es): 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland, 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Tom Robert, Mech Eng Limited Report 242224-RP01-revB This certificate is issued retrospectively for the tank manufactured in 2024. | 2030-01-23
TNK20435 | 2025-01-23 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T3406; HDPE Single skinned, 2300mm DIA x 2020mm H x 12mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Prominent 270/04/10 rev A Name of Designer: Mech Eng Limited Capacity: 7700 litres max; 7000 lirres SFL Compartments: 1 | Name: Sodium hypochlorite 10% w/w aqueous solution Class(es): 8.2C, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland, 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Tom Robert, Mech Eng Limited Report 242222-RP01-revA. This certificate is issued retrospectively for the tank manufactured in 2024. | 2030-01-23
TNK20436 | 2025-01-23 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T3407: HDPE Single Skin, 2800mm DIA x 2800mm H x 15mm WT. Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Prominent 270-01-10 rev C Name of Designer: Mech Eng Limited Capacity: 16510 litres maximum; 15000 litres SFL Compartments: 1 | Name: Sodium hydroxide (Caustic soda) 30% w/w aqueous solution max sg 1.306 Class(es): 6.1D, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland, 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design in accordance with Mech Eng Design Report -242223-RP01-RevA This certificate is issued retrospectively for the tank manufactured in 2024. | 2030-01-23
TNK20437 | 2025-02-05 | Fuelchief Limited | FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | UL 142 FAB0093 | Description: 80,000 Litres three compartments, above ground, double skin, horizontal, cylindrical stationary tank Design Specification: UL 142 Tank Type: Above Ground Stationary Tank Drawing Numbers: SV4.5-80,000 TC Rev A, Sheet 1 of 1 Name of Designer: Fuelchief Limited Capacity: 77,541 Litres (Gross capacity of all 3 compartments combined) Split Tank?: Yes Compartments: 3 | Name: 91 Petroleum Class(es): 3.1A, 6.7B Name: 98 Petroleum Class(es): 3.1A, 6.6A, 6.7B, 6.8A Name: Diesel Class(es): 3.1D, 6.7B Name: Hazardous Liquids Classes 3.1A, 3.1B, 3.1C, 3.1D Class(es): 3.1A, 3.1B, 3.1C, 3.1D | FUELCHIEF LIMITED Innovation Park Lot 15/185 Kirk Road, Templeton, Christchurch 7675 | Design Specifi cations: UL142, SwRI 95-03, SwRI 93-01. TNK No.: TNK20437. FAB No.: FAB0093. Manufacturer's Tank Serial No.: Name Plate. Date of Manufacture: Name Plate. Capacities: - Compartment A - Gross capacity = 36,308 Litres, Safe Fill Level = 35,213 Litres. - Compartment B - Gross capacity = 30,925 Litres, Safe Fill Level = 30,000 Litres. - Compartment C - Gross capacity = 10,308 Litres, Safe Fill Level = 10,000 Litres. Approved For: The storage and transfer of hazardous liquids having hazardous classifications of 3.1A, 3.1B, 3.1C, 3.1D. In particular Diesel having hazard classification of 3.1D, 6.1E, 6.7B, 9.1B, 91 Petroleum having hazard classification of 3.1A, 6.1E, 6.3B, 6.7B, 9.1B and 98 Petroleum having hazard classification of 3.1A, 6.1E, 6.6A, 6.7B, 6.8A, 9.1B. | 5/0/2035 | FAB0093
TNK20438 | 2024-12-19 | CONTRACT MECHANICAL SERVICES LIMITED 11 Harvard Way, Mount Maunganui, 3116 |  | API 650, Thirteen Edition March 2020 | Nitric Acid Tank Nominal volume of up to 25 cubic meters | Nitric Acid 60-64% Class(es): 6.1D, 6.9B, 8.1A, 8.2B, 8.3A | CONTRACT MECHANICAL SERVICES LIMITED 11 Harvard Way, Mount Maunganui, 3116 | Subject to 2EJ389-CMS-Nitric Acid Tank - Design Report-RevA | 2034-12-19
TNK20439 | 2025-01-06 | Plaspoke Limited / Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: 0130-PLASCT-01, HDPE Single skinned vertical cylinder, 2350mm IDIA x 3362mm HOA x 20/40mm WT Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Plaspoke APEX 25KL Acetic acid Tank - 0130-PLASCT-01 shts 1-5 rev D Name of Designer: Plaspoke Limited / Mech Eng Limited Capacity: 26130 litres maximum; 25000 litres SFL Compartments: 1 | Name: Acetic acid 49% Class(es):6.1D, 6.9B, 8.1A, 8.2C, 8.3A | Plaspoke Limited 35 Saleyards Road, Otahuhu, Auckland,1062 | Design in accordance with Mech Eng Report 242093-RP01-Rev-A | 2030-01-06
TNK20440 | 2025-02-20 | Fuelchief Limited | FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS1692: 2006 FAB0093 | Description: 499 Litres above ground, single skin, rectangular stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: PXR-499, Rev A, Sheet 1 of 1, Date:07/01/2025 Name of Designer: Fuelchief Limited - DL Capacity: 499 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | FUELCHIEF LIMITED Innovation Park Lot 15/185 Kirk Road, Templeton, Christchurch 7675 | Maximum Safe Fill Level = 474 Litres. Approved For: The storage and transfer of diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved to supply an engine or burner. References: Design Statement Cert. No. 8378-5001, by Joe Bain CPEng 248672, Date: 14/02/2025. 8378-3001 – Seismic & Wind Assessment for PXR-499 Tank, by Joe Bain CPEng 248672, Date: 14/02/2025. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank name plate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2035-02-20 | FAB0093
TNK20441 | 2025-02-13 | DESIGN ENGINEERING |  | AS 1692:2006 | Description: GO-INDUSTRIAL BOX-SERIES-4950 Design Specification: AS 1692:2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: GOBOX-2024NOV-4950 sheets 1-5 Name of Designer: DESIGN ENGINEERING Capacity: 4950 litres max; 4700 litres SFL | Name: Diesel & Combustible liquids AS1940 C1/C2 Class(es): 3.1D | GO INDUSTRIAL PTY LTD Suite 15229 17B Farnham Street Parnell Auckland 1052 New Zealand | GO BOX Series all have greater than 110% Secondary Containment | 2030-02-13
TNK20442 | 2025-02-04 | Longveld Limited |  | AS1692: 2006 | Description: Vertical 316 SS cone roof and bottom on legs, CIP process SFL 2000 Ltrs Design Specification: AS1692: 2006 Tank Type: Process Container Drawing Numbers: 27806-01-A001 Name of Designer: Longveld Capacity: 2,500 L Compartments: 1 | Name: 1~2% Nitric Acid in water Class(es): 8.1A, 8.2C, 8.3A Name: Caustic Soda 0.5 ~ 5% Class(es): 8.1A, 8.2B, 8.3A | LONGVELD LIMITED 153 -157 Ellis Street, Frankton, Hamilton 3204 | The design is destined for Fonterra Studholme 12 Packers Road, Waimate 7980, for CIP process for either Nitric Acid or Caustic Soda diluted with water to 1~2 % strength. | 2075-02-04
TNK20443 | 2025-02-20 | FUELCHIEF LIMITED | FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS1692: 2006 FAB0093 | Description: Tank 30048; Vertical cylinder, Category 5; 2350mm DIA, 3839mm HOA x 6mm WT Design Specification: AS 1692:2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: Fuelchief 15,000 LITRE VERTICAL TANK rev B Name of Designer: Fuelchief Capacity: 15484 litres MAX; 15019 litres SFL Compartments: 1 | Name: Frame-Pro timber preservative Class(es):6.8B, 8.3A | FUELCHIEF LIMITED 185 Kirk Road, Templeton, Christchurch, 8042 | Includes 6.1E, 6.3A, 6.8A, 8.3A; 9.1B, only 6.8B & 8.3A for certification Design Engineering Certificate 31740 | 2030-02-20 | FAB0093
TNK20444 | 2025-02-20 | Totara Engineering |  | AS1692: 2006 | Description: D1PV1031#293; Vertical cylinder; Category 5; Steam jacketed; 304 Stainless steel, 2600mm DIA x 4027m Design Specification: AS 1692:2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: Protech 11791-A001 GA rev B sheets 1-4 Name of Designer: Totara Engineering Capacity: 13,671 litres max; 13,000 litres SFL | Name: Phosphoric acid (maximum 10% w/w) Classes:6.1D, 8.1A, 8.2C, 8.3A Name:Sodium hydroxide (maximum 10% w/w aqueous solution) Class(es): 6.1D, 8.1A, 8.2B, 8.3A | PROTECH STAINLESS LIMITED 40 Te Kowhai Road East, Burbush, Hamilton, 3288 |  | 2030-02-20
TNK20445 | 2025-02-20 | Tankreline NZ Limited |  | UL 1316 | Description: XHS-400027-T1-98; 10.7m LOA x 2.45m DIA x 13mm WT Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: TRL-DRW-XHS-T1-98-101; TRL-DRW-XHST1-98-102 Name of Designer: Tankreline NZ Limited Capacity: 49564 litres Maximum; 47,085 litres SFL Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 140-146 Wairau Road, Wairau Valley, Auckland 0627 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has Hydroguard permanent interstitial monitoring system Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. Tank Owner (PCBU) requested operational SFL reduction to 44,600 litres. | 2030-02-20
TNK20446 | 2025-02-27 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Description: T#3409; Double skinned HDPE, 2100mm IDIA x 2933mm HOA x 12mm WT. Design Specification: BS EN 12573 SWI Thermoplastic Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: Prominent DWG#406845/20-10 rev D Name of Designer: Mech Eng Limited Capacity: 8,800 L maximum; 8,000 L SFL Compartments: 1 | Name: Sodium hydroxide (Caustic soda) 30% w/w aqueous solution Class(es): 6.1D, 8.1A, 8.2B, 8.3A | PLASTICS CONSTRUCTIONS LIMITED 26 Fremlin Place, Avondale, Auckland 1026 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023 Design Report Tom Robert, Mech Eng Limited Report 242391-RP01-Rev-C This certificate is issued retrospectively for the tank manufactured in 2025. | 2030-02-27
TNK20447 | 2025-03-04 | Eneraque NZ Limited |  | AS1692: 2006 | Description: ENR-BT1870 - s/n APG-BS315-1870; Generator Engine Belly Tank - Category 3; 3.76m LOA x 1.1m W x 0.64 Design Specification: AS 1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: Eneraque 12244-PD-DWG-0001 rev A sheets 1-3 Name of Designer: Eneraque NZ Limited Capacity: 1964 L MAXIMUM; 1870 L SFL | Name: Diesel & Combustible liquids AS1940 C1/C2 Class(es): 3.1D | ENERAQUE NZ LIMITED 40 Oranga Avenue, Onehunga, Auckland 1061 | Tank vent to be fitted such that it terminates external to the generator engine container a minimum of 150mm above the tank top and the tank fill point. Tank manufactured by Wuxi Aplus Power Machinery Co. Limited, China. | 2030-03-04
TNK20448 | 2025-03-10 | Longveld Limited |  | AS1692: 2006 | Description: Vertical 304L SS cone roof and bottom on legs Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 27806-03-A001 rev 4 Name of Designer: Longveld Capacity: 10,000 Litres Compartments: 1 | Name: Sodium Hydroxide 50% Class(es): 6.1D, 8.1A, 8.2B, 8.3A | LONGVELD LIMITED 153-157 Ellis Street, Frankton, Hamilton 3204 | This tank TAG NO. R6TK5020 is destined for Fonterra Studholme 12 Packers Road, RD10, Waimate Sth Canterbury. | 2075-03-10
TNK20449 | 2025-03-14 | APD Limited / Armatec Environmental | APD Ltd PO Box 12663 Penrose, Auckland 1642 49 McLaughlins Road, Wiri, Auckland, 2104 | ASME RTP-1:2015 FAB0032 | Description: 17,479 Litres above ground, vertical, cylindrical, PVC/GRP (Vinyl Ester)stationary tank Design Specification: ASME RTP-1: 2015 Tank Type: Above Ground Stationary Tank Drawing Numbers: 40781-3.1-000 (-001 to -006 & -008 to-0020), 19 sheets, Rev H, Date: 04/03/2025 Name of Designer: APD Limited / Armatec EnvironmentalLimited Capacity: 17,479 L Compartments: 1 | Name: Sodium Hypochlorite Class(es): 8.2C, 8.3A | APD LIMITED / ARMATECENVIRONMENTAL LIMITED 49 McLaughlins Road, Wiri, Auckland 2104 | Manufacturer’s Tank No.: S1101764. Date of Manufacture: October 2024. Maximum Safe Fill Level = 2,436mm. Approved For: The storage and transfer of Sodium Hypochlorite, having a hazard classification of 8.2C, 8.3A, 9.1A. References: APD report E8521, Rev 6, 11Sep2024, By: Todd Landers. AREND report APD039, Rev 4, 24Sep2024, By: Arend Groen. PS1, 11Nov24, Signed By: Arend Groen. PS2, 25Sep24, Signed By: Phil Hurdle. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2035-03-14 | FAB0032
TNK20465 | 2024-03-19 | Longveld Engineering |  | AS1692: 2006 | Description: Vertical 304 SS cone roof and bottom on legs Design Specification: AS1692: 2006 Tank Type: Process Container Drawing Numbers: 27806-05-A001 Name of Designer: Longveld Engineering Capacity: 1210 L | Name: Caustic Soda 10% Class(es): 6.1D, 8.1A, 8.2B, 8.3A | LONGVELD LIMITED 153-157 Ellis Street, Frankton, Hamilton 3204 | This tank TAG NO. R6TK5200 is destined for Fonterra Studholme 12 Packers Road, RD10, Waimate Sth Canterbury. TNK20450 | 2075-03-19
TNK20451 | 2025-03-20 | Aurecon New Zealand Limited |  | API Standard 650 | Description: CS Vertical Cone Roof cone floor Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: MM-3001 Name of Designer: Aurecon Capacity: 4,745,140 L | Up to 20/03/2026: Name: AGO (Diesel) Class(es): 3.1D, 6.7B As of 20/03/2026: Name: Flammable liquids Class(es): 3.1A, 3.1B, 3.1C, 3.1D, 6.7B | AURECON NEW ZEALAND LIMITED Level 8, 42-52 Willis Street, Wellington Central, Wellington 6011 | Tank ID D-14 designed for NZOSL. The Tank is to be installed at the BP’s terminal; 102 Parry Street, Central Dunedin. Initially designed for diesel. Now re-purposed for jet-Fuel or Petrol fuels. | 2075-03-20
TNK20452 | 2025-03-20 | Tankreline NZ Limited |  | UL 1316 | Description: XHS-400027-T2; 10.8m LOA x 2.5m DIA x 13mm WT Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: TRL-DRW-XHS-T2-91-103; TRL-DRW-XHST2-91-104 Name of Designer: Tankreline NZ Limited Capacity: 48,356 L maximum; 45,900 L SFL. Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 140-146 Wairau Road, Wairau Valley, Auckland 0627 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has Hydroguard permanent interstitial monitoring system Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. Tank Owner (PCBU) requested operational SFL reduction to 43,500 litres | 2030-03-20
TNK20453 | 2025-03-20 | Transtank / Qingdao Jinhuanghai Container Co |  | AS1692: 2006 | Description: T30-TNTK-402844-8 CONTAINERISED DOUBLE SKINNED >110% SECONDARY CONTAINMENT Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: Trans-Tank A000437; T-C30-GA01 shts 1 & 2. Name of Designer: Transtank / Qingdao Jinhuanghai Container Co Capacity: 31400 litres; 28000 litres SFL Compartments: 1 | Name: Diesel & Combustible liquids AS1940 C1/C2 Class(es): 3.1D | AGGREKO (NZ) LIMITED 1048-1050 Great South Road, Mount Wellington, Auckland 1060 | Tank manufacturer Qingdao Jinhuanghai Container Co, China, DOM 2012. This Design Certificate is issued post construction as verification that the Design conforms to the required standard at the time of construction. The PCBU must insure that vessel remains in serviceable condition and meet minimum design specifications of material thickness and venting as constructed. | 2030-03-20
TNK20454 | 2025-03-24 | Maskell Productions Limited |  | UL 1316 | Description: J21909-D3; Double-skinned GRP, 1200mm DIA x 3000mm LOA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Maskell, Envirotank 1037.03.10 rev 5 - J21909 Name of Designer: Maskell Productions Limited Capacity: 3100 litres maximum; 3000 litres SFL | Name: Pipeline pigging washings; Used and waste transmission oil and non-flammable fuel oil. Class(es): 3.1D, 6.7B | Maskell Productions Limited 24 Bowden Road, Mount Wellington, Auckland, 1060 | Design Report John M Clark 1.0-March 12, 2025. Includes classifications of 6.3B and 9.1C which do not require certification under these Regulations. This Stationary Container Design Certificate has been issued retrospectively for the fabrication of the tank in 2024. | 2030-03-24
TNK20455 | 2025-04-07 | VISA S.P.A. - Angelo Claut | Visa S.p.a. Via I Maggio, 55 Fontanelle (TV) Italia | AS1692: 2006 FAB0061 | Description: ST60 - 2,615 Litres above ground, single skin, rectangular, generator stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 103000004050-000-02, Sheets 1 to 13, Rev02, SERBATOIO 2500LT/03 x ST60, Date:13/02/2023 Name of Designer: VISA S.P.A. - Angelo Claut Capacity: 2,615 L Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | QUALITY POWER LIMITED 212 Crawford Street, Central Dunedin, Dunedin 9016 | Maximum Safe Fill Level = 2,500 Litres. Approved For: The storage and transfer of Diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved for supplying an engine or burner. If supplying an engine or burner approved for use with diesel only having a flash point greater than 60 deg C but less than or equal to 93 deg C. References: 2500L C60 Product presentation rev 01, Date: 05/04/2025. The maximum seismic acceleration that the tank has been assessed for is 0.19g. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank name plate in addition to the manufacturer's serial number, date of manufacture, pressure testin kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2035-04-07 | FAB0061
TNK20456 | 2025-04-07 | VISA S.P.A. - Angelo Claut | Visa S.p.a. Via I Maggio, 55 Fontanelle (TV) Italia | AS1692: 2006 FAB0061 | Description: GV151 - 1,805 Litres above ground, single skin, rectangular, generator stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 103000008484-000-01, Sheets 1 to 10, Rev01, SERB. 1800 LT X GV151/02, Date:18/06/2024 Name of Designer: VISA S.P.A. - Angelo Claut Capacity: 1,805 L Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | QUALITY POWER LIMITED 212 Crawford Street, Central Dunedin, Dunedin 9016 | Maximum Safe Fill Level = 1,742 Litres. Approved For: The storage and transfer of Diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved for supplying an engine or burner. If supplying an engine or burner approved for use with diesel only having a flash point greater than 60 deg C but less than or equal to 93 deg C. References: 1800 L GV151 Product presentation rev 01, Date: 05/04/2025. The maximum seismic acceleration that the tank has been assessed for is 0.19g. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure testin kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2035-04-07 | FAB0061
TNK20457 | 2025-04-07 | VISA S.P.A. - Angelo Claut | Visa S.p.a. Via I Maggio, 55 Fontanelle (TV) Italia | AS1692: 2006 FAB0061 | Description: GV121 - 1,865 Litres above ground, single skin, rectangular, generator stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 103000006881-000-02, Sheets 1 to 9, Rev02, SERBATOIO GV121 (1800 LT), Date:27/01/2025 Name of Designer: VISA S.P.A. - Angelo Claut Capacity: 1,865 L Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | QUALITY POWER LIMITED 212 Crawford Street, Central Dunedin, Dunedin 9016 | Maximum Safe Fill Level = 1,800 Litres. Approved For: The storage and transfer of Diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved for supplying an engine or burner. If supplying an engine or burner approved for use with diesel only having a fl ash point greater than 60 deg C but less than or equal to 93 deg C. References: 1800 L GV121 Product presentation rev 01, Date: 05/04/2025. The maximum seismic acceleration that the tank has been assessed for is 0.19g. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure testin kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2035-04-07 | FAB0061
TNK20458 | 2025-04-10 | Tankreline NZ Limited |  | UL 1316 | Description: XHS-400027-T3; 6.8m LOA x 2.4m DIA x 13mm WT Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: TRL-DRW-XHS-T3-ADO-105; TRL-DRW-XHST3-ADO-106 Name of Designer: Tankreline NZ Limited Capacity: 30138 litres maximum / 28630 litres SFL Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | MOBIL OIL NEW ZEALAND LIMITED 40-146 Wairau Road, Wairau Valley, Auckland, 0627 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank has Hydroguard permanent interstitial monitoring system Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. Tank Owner (PCBU) requested operational SFL reduction to 27,100 litres | 2030-04-10
TNK20459 | 2025-04-14 | Maskell Productions Limited |  | UL 1316 | Description: DWT-1200D-Series; Double skinned, GRP, Permanent hydro-guard interstitial monitoring. 1.2m Diameter Design Speciﬁcation: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Maskell, Envirotank 1466/12/B; 1037-01-01; 1037/02/01; 1037/03/01; 1037/04/01;1037/05/01; 1115/P2 Name of Designer: Maskell Productions Limited Capacity: 1000, 2000, 3000, 4000, 5000 litres. Split Tank?: Yes Compartments: 3 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Maskell Productions Limited 24 Bowden Road, Mount Wellington, Auckland, 1060 | Engineering Certificate: Clark Engineers, Russell L. Wilkins PE, 02 December 2019. Nominal volumes: 1000, 2000, 3000, 4000, 5000 litres. Maximum volumes and Safe Fill Levels provided in Maskell DWT-1200D Tank Volume table; Safe Fill level not to exceed 95% of maximum tank volume; Tank Installation to be completed in accordance with Envirotank Fibreglass Underground Storage Tanks, Installation instruction for PetroleumStorage Tanks - 02 - 2017; Tanks may be compartmentalized to a maximum of 5 compartment provided each compartment is separated by a bulkhead constructed according to drawing Maskell-Envirotank 1115/P2 Rev A, and fitted with identical manways to each compartment. Tank design parameters: Min/Max Design Operating Pressure Atmospheric, Test Pressure maximum 35kPa Maximum product density 1.0 s.g. This Design Certificate applies retrospectively also to tanks constructed between this date of issue and the date of expiry of previous design certificates. 15.04.2025(ASC) Drawing number 1037/02/02 changed to 1037/02/01 | 2030-04-14
TNK20460 | 2025-04-14 | Maskell Productions Limited |  | UL 1316 | Description: DWT-2000D-Series; Double skinned, GRP,Permanent hydro-guard interstitial monitoring. 2.0m Diameter Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Maskell Envirotank 1466/20/B;1037/10/02; 1037/15/02; 1037/20/02;1037/25/02; 1037/30/02; 1115/P2 Name of Designer: Maskell Productions Limited Capacity: 10,000, 15,000, 20,000, 25,000, 30,000 litres. Split Tank?: Yes Compartments: 5 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Maskell Productions Limited 24 Bowden Road, Mount Wellington, Auckland, 1060 | Engineering Certificate: Clark Engineers, Russell L. Wilkins PE, 02 December 2019. Maximum volumes and Safe Fill Levels provided in Maskell DWT-2000D Tank Volume table; Safe Fill level not to exceed 95% of maximum tank volume; Tank Installation to be completed in accordance with Envirotank Fibreglass Underground Storage Tanks, Installation instruction for Petroleum Storage Tanks - 02 - 2017; Tanks may be compartmentalized to a maximum of 5 compartment provided each compartment is separated by a bulkhead constructed according to drawing Maskell-Envirotank 1115/P2 Rev A, and fitted with identical manways to each compartment. Tank design parameters: Min/Max Design Operating Pressure Atmospheric, Test Pressure maximum 35kPa Maximum product density 1.0 s.g. This Design Certificate applies retrospectively also to tanks constructed between this date of issue and the date of expiry of previous design certificates. | 2030-04-14
TNK20461 | 2025-04-14 | Maskell Productions Limited |  | UL 1316 | Description: DWT-2500D-Series; Double skinned, GRP, Permanent hydro-guard interstitial monitoring. 2.5m Diameter Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Maskell: 1466/25/B; 1037/10/01; 1037/15/01; 1037/20/01; 1037/25/01; 1037/30/01; 1037/35/01; 1037/40/01; 1037/45/01;1037/50/01; 1037/55/01; 1037/60/01; 1037/65/01; 1037/70/01; 1115/P2 Name of Designer: Maskell Productions Limited Capacity: 10,000; 15,000; 20,000; 25,000; 30,000; 35,000; 40,000; 45,000; 50,000; 55,000; 60,000; 65,000; 70,000 litres. Split Tank?: Yes Compartments: 5 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Maskell Productions Limited 24 Bowden Road, Mount Wellington, Auckland, 1060 | Engineering Certificate: Clark Engineers, Russell L. Wilkins PE, 02 December 2019. Maximum volumes and Safe Fill Levels provided in Maskell DWT-2500D Tank Volume table; Safe Fill level not to exceed 95% of maximum tank volume; Tank Installation to be completed in accordance with Envirotank Fibreglass Underground Storage Tanks, Installation instruction for Petroleum Storage Tanks - 02 - 2017; Tanks may be compartmentalized to a maximum of 5 compartment provided each compartment is separated by a bulkhead constructed according to drawing Maskell-Envirotank 1115/P2 Rev A, and fitted with identical manways to each compartment. Tank design parameters: Min/Max Design Operating Pressure Atmospheric, Test Pressure maximum 35kPa Maximum product density 1.0 s.g. This Design Certificate applies retrospectively also to tanks constructed between this date of issue and the date of expiry of previous design certificates. | 2030-04-14
TNK20462a | 2025-04-14 | Maskell Productions Limited |  | UL 1316 | Description: DWT-3000D-Series; Double skinned, GRP,Permanent hydro-guard interstitialmonitoring. 3.0m Diameter Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Maskell Envirotank 1466/30/B; 1037/45/02; 1037/50/02; 1037/55/02; 1037/60/02; 1037/65/02; 1037/70/02; 1037/75/01;1037/80/01; 1037/85/01; 1037/90/01; 1037/95/01; 1037/100/01; 1037/105/01; 1037/110/01; 1115/P2; Name of Designer: Maskell Productions Limited Capacity: 45,000, 50,000, 55,000, 60,000, 65,000, 70,000, 75,000, 80,000, 85,000, 90,000, 95,000, 100,000, 105,000, 110,000 litres. Split Tank?: Yes Compartments: 5 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Maskell Productions Limited 24 Bowden Road, Mount Wellington, Auckland, 1060 | Engineering Certificate: Clark Engineers, Russell L. Wilkins PE, 02 December 2019. Maximum volumes and Safe Fill Levels provided in Maskell DWT-3000D Tank Volume table; Safe Fill level not to exceed 95% of maximum tank volume; Tank Installation to be completed in accordance with Envirotank Fibreglass Underground Storage Tanks, Installation instruction for PetroleumStorage Tanks - 02 - 2017; Tanks may be compartmentalized to a maximum of 5 compartment provided each compartment is separated by a bulkhead constructed accordingto drawing Maskell-Envirotank 1115/P2 Rev A, and fitted with identical manways to each compartment. Tank design parameters: Min/Max Design Operating Pressure Atmospheric, Test Pressure maximum 35kPa Maximum product density 1.0 s.g. This Design Certificate applies retrospectively also to tanks constructed between this date of issue and the date of expiry of previous design certificates. | 2030-04-14 | TNK number allocated to two entries, assigned TNK20462a
TNK20462b | 2025-04-29 | Longveld Limited |  | AS 1692: 2006 | Description: Vertical 304 SS cone roof and bottom on legs Design Specification: AS 1692: 2006 Tank Type: Process Container Drawing Numbers: 27806-04-A001 rev 7 Name of Designer: Longveld Limited Capacity: 2,277 Litres Compartments: 1 | Name: Caustic Soda 10% Class(es): 8.1A, 8.2B, 8.3A | LONGVELD LIMITED 153 - 157 Ellis Street, Frankton, Hamilton 3204 | This tank is destined for Fonterra Studholme plant 12 Packers Road Waimate, 7980. Purposed for mixing Caustic. | 2075-04-30 | TNK number allocated to two entries, assigned TNK20462b
TNK20463 | 2025-05-08 | Fuelco | Zhangjiagang Fuel Equipment Systems Company. Ltd Trading as FES 3 Hai Xin North Road, Nanfeng Town, Zhangjiagang City, Jiangsu Province P.R. China, 215600 | SWRI 93-01 FAB0052 | Description: 7,784 litres to 59,467 litres rectangular double skinned 4 hour fire rated tank Design Specification: SWRI 93-01 Tank Type: Above Ground Stationary Tank Drawing Numbers: LTKB-010-4HR-GA-0, 15, 27, 32, 55, 60 & 65 Name of Designer: Fuelco Capacity: 7,784 litres to 59,467 litre Compartments: 1 Max Safe Fill: LTKB10 = 7,175L, LTKB15 = 11,900L, LTKB27 = 21,280L, LTKB32 = 26,110L, LTKB55 = 46,360L, LTKB60 = 49,640L & LTKB65 = 54,460L | Name: Acetone Class(es): 3.1B, 8.2C Name: Aviation Fuel Class(es): 3.1C Name: Diesel Class(es): 3.1D, 6.7B Name: Ethanol Class(es): 3.1B Name: Kerosene Class(es): 3.1C Name: Methanol Class(es): 3.1B, 6.1C, 6.8B, 6.9A Name: Petrol Class(es): 3.1A, 6.7B Name: P-xylene Class(es): 3.1C, 6.1D | PETROTEC SERVICES LIMITED 12 Venture Place, Middleton, Christchurch 8024 PO Box 10125, Philipstown, Christchurch 8145 | As of 26/09/2025, approved for: The storage and transfer of Petrol having a Hazard Classifi cation of 3.1A, 6.1E, 6.7B, 9.1B, or Methanol having a Hazard Classification of 3.1B, 6.1C,6.4A, 6.8B, 6.9A, or Ethanol having a Hazard Classification of 3.1B, 6.4A, or Acetone having a Hazard Classification of 3.1B, 6.1E, 6.4A, 8.2C, or Kerosene having a Hazard Classification of 3.1C, 6.1E, 6.3B, 9.1B, or Aviation Fuel having a Hazard Classification of 3.1C, 6.1E, 6.3B, 9.1B or P-xylenehaving a Hazard Classification of 3.1C, 6.1D, 6.1E, 6.3A, 6.4A or Diesel having a Hazard Classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. SwRI 93-01 Tank,4 hour fire rated tank. Approved to supply a burner or engine. When supplying burner or engine system supply to have an anti-siphon device installed immediately adjacent to the tank. References: Producer Statement – PS1 – 8442-1001, Rev 01, Date: 29Aug25, by: Joe Bain (CPEng 248672). UL 2085 Certificate of Compliance - Certificate Number: 20180129-MH62698 - Report Reference: MH17883-19940124 - Issue Date: 2018-JANUARY-29 - Issued to: Zhangjiagang Fuel Equipment System Co. Ltd. Zhangjiagang Fuel Equipment System Co Ltd is a member of Steel tank Institute - Licensed Manufacturer of Fireguard - Certificate. Fireguard® - Licensed Manufacturer Certificate – Zhangjiagang Fuel Equipment System Co. Ltd – Steel Tank Institute. Underwriters Laboratories Inc. ® - Letter – May 24, 1995 – Reference: MH17883. SwRI Reference No.15077-01/100-08, product: Fireguard ® 93-01 – Label. Petro Tec Services Limited and (FES) Zhangjiagang Fuel Equipment System Co. Ltd. responsibility to ensure each individual tank manufactured isinstalled with the suitable SwRI labelling. Allocate unique serial number for each tank and retain individual tank fabrication and test records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture / pressure test, design code, test pressure in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced drawings or applicable standards. | 2035-09-26 | FAB0052
TNK20464 | 2025-05-09 | Hendl & Murray Engineering Limited | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton 3206 | API Standard 650 FAB0033 | Description: 35,009 Litres above ground, insulated, vertical, cylindrical, cone top, flat bottom stationary tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: 23922-01-00, Rev A, 30m3 D-Zolv Tank, Pictorial View, Drawn: K.Patil, Date: 10/03/25 Name of Designer: Hendl & Murray Engineering Limited Capacity: 35,009 Litres Compartments: 1 | Name: D-Zolv Class(es): 6.1D, 8.1A, 8.2B, 8.3A | HENDL & MURRAY ENGINEERING LIMITED 103 Tawa Street, Melville, Hamilton 3206 | Maximum Safe Fill Level = 30,000 Litres. Approved for the storage and transfer of D-Zolv, having a hazard classification of 6.1D, 8.1A, 8.2B, 8.3A. References: Producer Statement - PS1 - Design - 251322, Issued By: Mech Eng Ltd, To: Fonterra Te Rapa, To Be Supplied To: Hamilton City Council, In Respect Of: 30m³ D-Zolv Tank, At: 1344 Te Rapa Road, Te Rapa, Hororiu 3200, Drawings: 23922-01-00 Rev A, 01 Rev D, 02 Rev A, 03 Rev C, 04 Rev A, 05 Rev B, 06 Rev A, 07 Rev A, 08 Rev A, 09 Rev A, Signed By: Tom Roberts (CPEng #1024350), Date: 29-Apr-25. Design Report: 251322 RP01 RevA Te Rapa 30m3 D-ZOLV Tank Design Report, Issued By: Mech Eng Ltd, To: Hendl & Murray Engineering Ltd, Author: Tom Roberts CPEng Meng CMEngNZ, Design Actions: NZS 1170.5:2004, NZS3106, API 650, NZSEE SDST, AS 3990, Design Standard: API 650 13th Ed 2020, Revision A, Date: 03-Apr-25. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2035-05-09 | FAB0033
TNK20465 | 2025-05-09 | Hendl & Murray Engineering Limited | Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton 3206 | API Standard 650 FAB0033 | Description: 30,372 L above ground, single skin, vertical, cylindrical, cone top, flat bottom stationary tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: 23922-00-00, Rev A, 25m3 Nitric Acid Tank, Pictorial View, Drawn: K.Patil, Date:06/03/25 Name of Designer: Hendl & Murray Engineering Limited Capacity: 30,372 Litres Compartments: 1 | Name: Nitric Acid (Max. concentration 64%) Class(es): 6.1D, 6.9B, 8.1A, 8.2B, 8.3A | HENDL & MURRAY ENGINEERING LIMITED 103 Tawa Street, Melville, Hamilton 3206 | Maximum Safe Fill Level = 25,000 Litres. Approved For: The storage and transfer of Nitric Acid (Max. concentration 64%), having a hazard classifi cation of 6.1D, 6.9B, 8.1A, 8.2B, 8.3A. References: Producer Statement - PS1 - Design - 251321, Issued By: Mech Eng Ltd, To: Fonterra Te Rapa, To Be Supplied To: Hamilton City Council, In Respect Of:25m³ Nitric Acid Tank, At: 1344 Te Rapa Road, Te Rapa, Hororiu 3200, Drawings: 23922-00-00 Rev A, 01 Rev E, 02 Rev C, 03 Rev A, 04 Rev A, 05 Rev B, 06 RevA, 07 Rev A, 08 Rev A, 09 Rev C, 10 Rev A, Signed By: Tom Roberts (CPEng #1024350), Date: 29-Apr-25. Design Report: 251321 RP01 RevA Te Rapa 25m³ Nitric Acid Tank Design Report, Issued By: Mech Eng Ltd, To: Hendl & Murray Engineering Ltd,Author: Tom Roberts CPEng MEng CMEngNZ, Design Actions: NZS 1170.5:2004, NZS3106, API 650, NZSEE SDST, AS 3990, Design Standard: API 65013th Ed 2020, Revision A, Date: 03-Apr-25. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2035-05-09 | FAB0033
TNK20466 | 2025-05-26 | TRL Engineering Limited |  | UL 1316 | Tank Type: Below Ground, Fibreglass, Double Skin, Single Compartment Design Specification: UL 1316 Capacity: 46,283 litres maximum; 43,970 litres SFL Drawing Numbers: TRL-DRW-XPK-T1-98-101; TRL-DRW-XPK-T1-98-102 Name of Designer: TRL Engineering Limited Description: XPK-400023-T1 98; GRP Double skinned, 2.3m DIA x 10.9m LOA x 13mm WT. Split Tank: No | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | TRL - Mobil Papakura 347 Great South Road, Papakura, Auckland 2113 | SFL @ 95% Maximum In-Situ constructed tank. PCBU has reduced SFL to 41,600 litres for operational requirements. Tank fitted with Hydro-guardpermanent interstitial monitoring. | 2030-05-26
TNK20467 | 2025-05-23 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 8,800 litres maximum; 8,000 litres SFL Drawing Numbers: ProMinent 304242/01/10/E Name of Designer: Mech Eng Limited Description: T#3427; Self-bunded HDPE 2300mm ID x 2633mm HOA x 12/20mm WT Split Tank: No | Name: Acetic acid 49% aqueous solution, s.g.1.05 Class(es): 6.1D, 6.9A, 8.1A, 8.2C, 8.3A | ProMinent New Zealand 97 Stella Drive Henderson Auckland 2122 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023; Mech Eng Design Report 251221-RP01-A | 2030-05-23
TNK20468 | 23/05/20025 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 8,800 litres maximum; 8,000 litres SFL Drawing Numbers: ProMinent 304242/05/10/D Name of Designer: Mech Eng Limited Description: T#3428; Self-bunded HDPE 2300mm ID x 2633mm HOA x 12/20mm WT Split Tank: No | Name: Sodium hydroxide 45% w/w aqueous solution, s.g. 1.45 Class(es): 6.1D, 8.1A, 8.2B, 8.3A | ProMinent New Zealand 97 Stella Drive Henderson Auckland 2122 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023; Mech Eng Design Report 251224-RP01-A | 2030-05-23
TNK20469 | 23/05/20025 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 2200 litres maximum; 2000 litres SFL. Litres Drawing Numbers: ProMinent 304242/04/40/C Name of Designer: Mech Eng Limited Description: T#3429; Self-bunded HDPE 1400mm ID x 1749mm HOA x 12mm WT Split Tank: No | Name: Sodium hypochlorite 15% aqueous solution s.g. 1.2. Class(es): 8.2C, 8.3A | ProMinent New Zealand 97 Stella Drive Henderson Auckland 2122 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023; Mech Eng Design Report 251223-RP01-A | 2030-05-23
TNK20470 | 2025-05-20 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 2200 litres maximum; 2000 litres SFL. Drawing Numbers: ProMinent 304242/02/40/C Name of Designer: Mech Eng Limited Description: T#3430; Self-bunded HDPE 1400mm ID x 1749mm HOA x 12mm WT Split Tank: No | Name: Citric acid 50% aqueous solution s.g. 1.25 Class(es): 8.3A | ProMinent New Zealand 97 Stella Drive Henderson Auckland 2122 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023; Mech Eng Design Report 251222-RP01-A | 2030-05-20
TNK20471 | 2025-05-23 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 8,800 litres maximum; 8,000 litres SFL Drawing Numbers: ProMinent 303577/03/200/C Name of Designer: Mech Eng Limited Description: T#3433; Self-bunded HDPE 2300mm ID x 2633mm HOA x 12/20mm WT Split Tank: No | Name: Sodium hydroxide 45% aqueous solution s.g. 1.45 Class(es): 6.1D, 8.1A, 8.2B, 8.3A | ProMinent New Zealand 6A Enterprise Drive Henderson Auckland 0612 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023; Mech Eng Design Report 251073-RP01-A | 2030-05-23
TNK20472 | 2025-05-23 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 8,800 litres maximum; 8,000 litres SFL Drawing Numbers: ProMinent 303577/01/200/D Name of Designer: Mech Eng Limited Description: T#3432; Self-bunded HDPE 2300mm ID x 2633mm HOA x 12/20mm WT Split Tank: No | Name: Acetic acid 49% aqueous solution s.g.1.05 Class(es): 6.1D, 6.9A, 8.1A, 8.2C, 8.3A | ProMinent New Zealand 6A Enterprise Drive Henderson Auckland 0612 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023; Mech Eng Design Report 251071-RP01-A | 2030-05-23
TNK20473 | 2025-05-23 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 8,800 litres maximum; 8,000 litres SFL Drawing Numbers: ProMinent 303577/02/200/C Name of Designer: Mech Eng Limited Description: T#3431; Self-bunded HDPE 2300mm ID x 2633mm HOA x 12/20mm WT Split Tank: No | Name: Aluminium sulphate 28% aqueous solution s.g.1.33. Class(es): 8.3A | ProMinent New Zealand 6A Enterprise Drive Henderson Auckland 0612 | Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023; Mech Eng Design Report 251072-RP01-A | 2030-05-23
TNK20474 | 2025-06-04 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 27516 litres maximum, 26458 litres SFL Drawing Numbers: H2O Engineering: P808-001/B Name of Designer: Mech Eng Limited Description: T#3170; HDPE Single skin, 3500mm DIA x 3500mm HOA x 25mm WT Split Tank: No | Name: Ferrous chloride 30% aqueous solution, maximum 1.45 s.g. Class(es):6.1D, 8.2C, 8.3A, 9.3C | Plastics Constructions Limited 26 Fremlin Place Avondale Auckland 1026 | Mech Eng Design Report 201731-RP01-RevA This certificate is for a previously constructed tank. Construction verified in accordance with Plastics Constructions Limited QA documents. | 2030-06-04
TNK20475 | 2025-06-04 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 27516 litres maximum, 26458 litres SFL Drawing Numbers: H2O Engineering: P808-002/B Name of Designer: Mech Eng Limited Description: T#3171; HDPE Single skin, 3500mm DIA x 3500mm HOA x 25mm WT Split Tank: No | Name: Ferrous chloride 30% aqueous solution, maximum 1.45 s.g. Class(es):6.1D, 8.2C, 8.3A, 9.3C | Plastics Constructions Limited 26 Fremlin Place Avondale Auckland 1026 | Mech Eng Design Report 201731-RP01-RevA This certificate is for a previously constructed tank. Construction verified in accordance with Plastics Constructions Limited QA documents. | 2030-06-04
TNK20476 | 2025-06-16 | Fuelchief Limited | FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS 1692: 2006 | Tank Type: Above Ground, Steel, Double Skin Design Specification: AS 1692 Capacity: 350 litres maximum, 335 litres SFL; 499 litres maximum, 484 litres SFL Litres Drawing Numbers: Fuelchief: VGR-499 FAB; VGR-350 FAB Name of Designer: Fuelchief Limited Description: AS1692-Category 3; FAB0093 Split Tank: No | Name: Flammable liquids and petroleum products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Fuelchief Limited Innovation Park, Lot 15/185 Kirk Road Christchurch Templeton Canterbury 8062 | This Design Certificate is for two models of the Vanguard series double-contained tanks with greater than 110% secondary containment. The interstice is filled with thermal insulation but does not confer a formal fire rating for the tank. | 2030-06-17 | FAB0093
TNK20477 | 2025-06-24 | TRL Engineering Limited |  | UL 1316 | Tank Type: Below Ground, Fibreglass, Double Skin, Single Compartment Design Specification: UL 1316 Capacity: 48,953 litres maximum / 46,500 litres SFL Drawing Numbers: TRL-DRW-XPK-T2-91-103; TRL-DRW-XPK-T2-91-104 Name of Designer: TRL Engineering Limited Description: XPK-400023-T2; GRP Double skinned construction; 2.4m DIA x 10.8m LOA x 13 mm WT Split Tank: No | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Tankreline NZ Limited 347 Great South Road Papakura Auckland 2110 | SFL @ 95% Maximum In-Situ constructed tank. PCBU has reduced SFL to 44,000 litres for operational requirements. Tank fitted with Hydro-guard permanent interstitial monitoring. | 2030-06-24
TNK20478 | 2025-05-24 | Mech Eng Limited |  | AS 2634 | Tank Type: Above Ground Stationary Tank Design Specification: AS 2634 Capacity: 10,430 litres maximum; 10,000 litres SFL. Drawing Numbers: Prominent 406765/10/01/K; 406765/10/02/B Name of Designer: Mech Eng Limited Description: T#3399; FRP/PVC vertical cylinder, 2300mm DIA x 3037mm HOA x 12mm WT. Split Tank: No | Name: Sodium hypochlorite 16% aqueous solution. Class(es): 8.2C, 8.3A | Plastics Constructions Limited 26 Fremlin Place Avondale Avondale Auckland 1026 | Mech Eng Report 242132-RP01-Rev C. This design certificate has been prepared post construction of the tank. | 2030-06-24
TNK20479 | 2025-06-26 | Willson Su - CPEng - NZ-1022048 |  | N/A | Tank Type: Above Ground Process Container Design Specification: Process Containers Standard not on List -- see Tank Details Capacity: 9750 litres maximum; 9000 litres SFL Drawing Numbers: CK-DXT01-04-four-Rins-water-C; CK-DXT01-01-One-Galv-A Name of Designer: Willson Su - CPEng - NZ-1022048 Description: Process Vessels used for powder coating processes. 304 Stainless Steel, 7500mm LOA x 2000mm H x 650mm W x 3mm WT, Open top. Split Tank: No | Name: Bonderite C-AK-44; Bonderite C-IC-425; Bonderite M-CR-723C, 5% aqueous solutions maximum s.g. 1.0 Class(es): 6.1D, 6.5A, 6.5B, 6.6B, 6.7A, 6.8B, 6.9B, 8.1A, 8.2B, 8.3A | NZ Powder Coating Company Limited 15 Gabador Place Mount Wellington Auckland 1060 | This design certificate is issued for seven identical tanks after the date of manufacture. Serial numbers 20190901001; 20190901002 ; 20190901003; 20190901004; 20190901005; 20190901006; 20190901007. Tank Manufacturer: Chang Fan Sheetmetal Co. Ltd Fengshang St Quliang Town Zheng Zhou City He Nan Province China | 2023-06-26
TNK20480 | 2025-06-30 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 11083 litres Maximum; 10555 litres SFL Drawing Numbers: Plastics Constructions 2014185-201-B Name of Designer: Mech Eng Limited Description: T#3452; Single skin, shielded HDPE, Vertical cylinder, 2400mm DIA x 2700mm HOA x 12mm WT Split Tank: No | Name: Aluminium sulphate aqueous solution maximum s.g. 1.33. Class(es): 8.3A | Plastics Constructions Limited 26 Fremlin Place Avondale Avondale Auckland 1026 | Mech Eng Limited Design Report-251511-RP01-Rev A Tank Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023. This Design Certificate has been issued after the construction of the tank. | 2030-06-30
TNK20481 | 2025-06-30 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 5443 litres maximum; 5184 litres SFL Drawing Numbers: Plastics Constructions 2014185-202-B Name of Designer: Mech Eng Limited Description: T#3451; Single skin, shielded HDPE, Vertical cylinder, 1790mm DIA x 2250mm HOA x 12mm WT Split Tank: No | Name: Sodium hydroxide 50% aqueous solution s.g.1.48 Class(es): 6.1D, 8.1A, 8.2B, 8.3A | Plastics Constructions Limited 26 Fremlin Place Avondale Avondale Auckland 1026 | Mech Eng Limited Design Report-251512-RP01-Rev A Tank Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023. This Design Certificate has been issued after the construction of the tank. | 2025-06-30
TNK20482 | 2025-07-04 | Fuel Storage Limited |  | SWRI 95-03 | Description: Split Vulcan 1,035L - 101,920L range of above ground, double skinned, rectangular, fire rated tank Design Specification: SWRI 95-03 Tank Type: Above Ground Stationary Tank Drawing Numbers: Refer to Details of Certification for drawings Name of Designer: Fuel Storage Limited Capacity: 1,035L - 101,920L Split Tank?: Yes Compartments: 2 | Name: Alpine (Low Flash) Diesel Class(es): 3.1C, 6.7B Name: Diesel Class(es): 3.1D, 6.7B Name: Jet Fuel (Kerosene) Class(es): 3.1C Name: Petrol Class(es): 3.1A, 6.6A, 6.7A, 6.8B | FUEL STORAGE LIMITED 700 Bond Road, Te Awamutu 3800 | Approved Drawings: - FSL VMH TANK SPLIT COMPARTMENT COMPLIANCE, Sheets: 1 to 4, Date: 28/04/2025. - FSL VMH1000-0C-01, Rev C, Sheets: 1 to 9, Vulcan Multi Hazard Tank Range Tank Size 1,000L, Date: 21/10/2024. - FSL VMH2000-0C-01, Rev C, Sheets: 1 to 10, Vulcan Multi Hazard Tank Range Tank Size 2,000L, Date: 21/10/2024. - FSL VMH3000-0C-01, Rev C, Sheets: 1 to 10, Vulcan Multi Hazard Tank Range Tank Size 3,000L, Date: 21/10/2024. - FSL VMH5000-0C-01, Rev C, Sheets: 1 to 10, Vulcan Multi Hazard Tank Range Tank Size 5,000L, Date: 21/10/2024. - FSL VMH7500-0C-01, Rev C, Sheets: 1 to 10, Vulcan Multi Hazard Tank Range Tank Size 7,500L, Date: 21/10/2024. - FSL VMH10000-0C-01, Rev C, Sheets: 1 to 10, Vulcan Multi Hazard Tank Range Tank Size 10,000L, Date: 21/10/2024. - FSL VMH20000-0C-01, Rev C, Sheets: 1 to 10, Vulcan Multi Hazard Tank Range Tank Size 20,000L, Date: 21/10/2024. - FSL VMH30000-0C-01, Rev C, Sheets: 1 to 10, Vulcan Multi Hazard Tank Range Tank Size 30,000L, Date: 21/10/2024. - FSL VMH40000-0C-01, Rev C, Sheets: 1 to 10, Vulcan Multi Hazard Tank Range Tank Size 40,000L, Date: 21/10/2024. - FSL VMH60000-0C-01, Rev C, Sheets: 1 to 10, Vulcan Multi Hazard Tank Range Tank Size 60,000L, Date: 21/10/2024. - FSL VMH80000-0C-01, Rev C, Sheets: 1 to 10, Vulcan Multi Hazard Tank Range Tank Size 80,000L, Date: 21/10/2024. - FSL VMH100000-0C-01, Rev C, Sheets: 1 to 10, Vulcan Multi Hazard Tank Range Tank Size 100,000L, Date: 21/10/2024. - FSL Cert Plate - Vulcan. - Vulcan Compliance Info Sticker2 05.09.24. Approved For: The storage and transfer of Petrol having a hazard classification of 3.1A, 6.1E, 6.3A, 6.6A, 6.7A, 6.9B, or Jet Fuel (Kerosene) having a hazard classification of 3.1C, 6.1E, 6.3B, 9.1B, or Alpine (Low Flash) Diesel having a hazard classification of 3.1C, 6.1E, 6.3B, 6.7B, 9.1B, or diesel, having a hazard classification of 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. 4 hour fire rated tank. Approved to supply an engine or burner. When supplying burner or engine systems supply to have an anti-siphon device installed immediately adjacent to the tank. References: 6998-CAN-5001 Split Compartment Tanks, Rev 00 Released, 13Feb25. 6998-2000, Fire Rated Tank Range PS1, Rev 02. R28752.01.001, SwRI final report, October 25, 2024. EV28752.02.001, SwRI Engineering Evaluation, May 14, 2025. Allocate unique serial number for each tank and retain individual tank fabrication and test records. The TNK register number is to be marked on the tank nameplate in addition to the manufacturers serial number, date of manufacture, design code, test pressure in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, referenced drawings or applicable standards. | 2050-07-04
TNK20483 | 2025-07-14 | TRL Engineering Limited |  | UL 1316 | Tank Type: Below Ground, Fibreglass, Double Skin, Single Compartment Design Specification: UL 1316 Capacity: 30,111 litres maximum; 28,600 litres SFL Drawing Numbers: TRL-DRW-XPK-T3-ADO-105; TRL-DRW-XPK-T3-ADO-106 Name of Designer: TRL Engineering Limited Description: XPK-400023-T3; GRP Double skinned construction; 2.5m DIA x 6.8m LOA x 13 mm WT Split Tank: No | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Tankreline NZ Limited 347 Great South Road Papakura Auckland 2110 | SFL @ 95% Maximum In-Situ constructed tank. PCBU has reduced SFL to 27,100litres for operational requirements. Tank fitted with Hydro-guard permanent interstitial monitoring. | 2030-07-14
TNK20484 | 2025-07-15 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 5500 litres Max; 5000 litres SFL Drawing Numbers: Prominent 303437/10/30/A Name of Designer: Mech Eng Limited Description: T#3435; HDPE Integral Secondary containment >110%; 1800mm ID x 2573mm HOAx 12 mm WT Split Tank: No | Name: Aluminium sulphate 28% aqueous solution maximum 1.31 s.g. Class(es):8.3A | ProMinent New Zealand Limited 6A Enterprise Drive Henderson Auckland 0612 | This design certificate has been issue after construction in accordance with Plastics Constructions QA Manual April 2023. Mech Eng Limited design report 251362-RP01-Rev A | 2030-07-15
TNK20485 | 2025-07-15 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 5500 litres Max; 5000 litres SFL Drawing Numbers: Prominent 303437/10/20/A Name of Designer: Mech Eng Limited Description: T#3434; HDPE Integral Secondary containment >110%; 1800mm ID x 2573mm HOA x 12mm WT Split Tank: No | Name: Acetic acid 49%, s.g. 1.03 Class(es): 6.1D, 6.9B, 8.1A, 8.2C, 8.3A | ProMinent New Zealand Limited 6A Enterprise Drive Henderson Auckland 0612 | This design certificate has been issue after construction in accordance with Plastics Constructions QA Manual April 2023. Mech Eng Limited design report 251361-RP01-Rev A | 2030-07-15
TNK20486 | 2025-07-15 | Mech Eng Limited | PLASPOKE LIMITED 35 Saleyards Road, Ōtāhuhu, Auckland, 1062 | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 5263 litres maximum; 5000 litres SFL Drawing Numbers: Plaspoke 0140-PLASCT-01-Rev B sheets 1-6 Name of Designer: Mech Eng Limited Description: PLASCT-0140: Double contained greater than 110%; HDPE 1850mm ID x 2122mm H x 12mm WT Split Tank: No | Name: Sodium hydroxide (Caustic soda) 30% w/w aqueous solution; 1.31 maximum s.g. Class(es): 6.1D, 8.1A, 8.2B, 8.3A | Plaspoke Limited Unit 8, 35 Saleyards Road Otahuhu Auckland 1062 | FAB0094 | 2030-07-15
TNK20487 | 2025-07-17 | Longveld |  | AS 1692: 2006 | Description: Vertical 316 SS cone roof and bottom on 304 SS legs, shell insulated. CAT-5 Design Specification: AS 1692:2006 Tank Type: Process Container Drawing Numbers: 27824-03-A01-GA; Rev 19: 4 Sheets Name of Designer: Longveld Capacity: 17,760 L Compartments: 1 | Name: Nitric Acid 1% Class(es): 6.9B, 8.2C, 8.3A | LONGVELD LIMITED 153 Ellis Street, Frankton, Hamilton 3204 | Tank is destined for Fonterra Edendale 60 North Rd EDENDALE 9825. Part of CIP process. | 2075-12-31
TNK20488 | 2025-07-21 | Longveld Limited |  | AS 1692: 2006 | Description: Vertical 304 SS Cone roof and bottom Skirt supported. Cat 5. Design Specification: AS 1692:2006 Tank Type: Process Container Drawing Numbers: 28038-TANK 08-A01 (3 shts). Name of Designer: Longveld Limited Capacity: 21,078 L Compartments: 1 | Name: Nitric Acid 1% Class(es): 8.1A, 8.2C, 8.3A | LONGVELD LIMITED 153 Ellis Street, Frankton, Hamilton 3204 | Tank is destined for OLAM Dairy Factory, Cambell Road Tokoroa. Part of CIP process. | 2075-12-31
TNK20489 | 2025-08-01 | Longveld Limited |  | AS 1692: 2006 | Description: Vertical 304 SS Cone roof and bottom Skirt supported. Cat 5. Design Specification: AS 1692: 2006 Tank Type: Process Container Drawing Numbers: 28038-TANK 09-A01 (3 shts). Name of Designer: Longveld Limited Capacity: 21,078 L Compartments: 1 | Name: Sodium Hydroxide 2~5% Class(es): 8.2C, 8.3A | LONGVELD LIMITED 153 Ellis Street, Frankton, Hamilton 3204 | Tank is destined for OLAM Dairy Factory, Cambell Road Tokoroa. Part of CIP process. | 2075-08-01
TNK20490 | 2025-08-01 | Hendl & Murray Engineering Limited | FAB0033 Hendl & Murray Engineering Ltd 103 Tawa Street, Melville, Hamilton, 3206 | API 620 | Description: 64,090 Litres above ground, insulated, vertical, cylindrical, dome top, dome bottom stationary tank Design Specification: API 620 Tank Type: Above Ground Stationary Tank Drawing Numbers: 23775-TK1-01 & 23775-TK2-01, 60m³ MDI Resin Tank TK1 & TK2, Rev H & Rev I, Date: 24/06/25 Name of Designer: Hendl & Murray Engineering Limited Capacity: 64,090 L Compartments: 1 | Name: Suprasec® 5005 Class(es): 6.1D, 6.5A, 6.5B, 6.7B, 6.9A | HENDL & MURRAY ENGINEERING LIMITED 103 Tawa Street, Melville, Hamilton 3206 | Approve+K1237:R1237wo configurations: - 23775-TK1-01, 60m³ MDI Resin Tank TK1, General Arrangement, Rev H, date: 24/06/25. - 23775-TK2-01, 60m³ MDI Resin Tank TK2, General Arrangement, Rev I, date: 24/06/25. The storage and transfer of Suprasec® 5005, having a hazard classification of 6.1D, 6.3A, 6.4A, 6.5A, 6.5B, 6.7B, 6.9A. The two configurations are mirror images of each other. References: Producer Statement - PS1 - Design - 251261, Issued By: Mech Eng Ltd, To: Laminex Taupo, To Be Supplied To: Taupo District Council, In Respect Of:Laminex Taupo60m3 MDI Silo, At: 177 Centennial Drive, Rotokawa 3378, Signed By: Tom Roberts (CPEng #1024350), Date: 24-June-25. Design Report: 251261 RP01 RevA 60m3 MDI Resin Tank Design Report, Issued By: Mech Eng Ltd, To: Hendl & Murray Engineering Ltd, Author: Tom Roberts CPEng Meng CMEngNZ, Revision A, Date: 10-June-25. Unique serial number to be allocated for each tank. Tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure testin kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2035-08-01 | FAB0033
TNK20491 | 2025-08-05 | Longveld Limited |  | AS 1692: 2006 | Description: Vertical 316 SS cone roof and bottom on legs. CAT 5 Design Specification: AS 1692: 2006 Tank Type: Process Container Drawing Numbers: 28289-Tank 02-A01; 4 shts. 28289-Tank 02-NP (Name Plate) Name of Designer: Longveld Limited Capacity: 13,824 L Compartments: 1 | Name: 0.8~1% Nitric Acid Class(es): 6.9B, 8.1A, 8.2C, 8.3A | LONGVELD LIMITED 153 Ellis Street, Frankton, Hamilton 3204 | This tank is destined for Fonterra's Tetra Pak Factory,1269 Waitoa Road, Waitoa 3386 | 2075-08-05
TNK20492 | 2025-08-12 | Mech Eng Limited |  | AS 2634 | Tank Type: Above Ground Stationary Tank Design Specification: AS 2634 Capacity: 4460 litres maximum/4070 litres SFL Drawing Numbers: Plastics Constructions ANZCO Foods Ashburton GA - TK-01-A2 Name of Designer: Mech Eng Limited Description: T#3454: GRP/PVC Single skinned vertical cylinder, 1800 mm DIA x 2000 mm HOA x 12mm WT. Split Tank: No | Name: Sulphuric acid 98% 1.85 s.g. Class(es): 6.1D, 6.7A, 6.9A, 6.9B, 8.1A, 8.2B, 8.3A | Plastics Constructions Limited 26 Fremlin Place Avondale Auckland 1026 | Design Report Mech Eng Limited 251621-RP01-Rev A; This design certificate has been issued after the construction of the tank made in accordance with Plastics Constructions QA Manual April 2023. | 2030-08-12
TNK20493 | 2025-08-03 | Tankreline NZ Limited |  | UL 1316 | Description: 400170-T1 GRP Double skin 8750mm LOA x 2500mm DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Number: Mobil Kapiti XMK 400170-T1 Name of Designer: Tankreline NZ Limited Capacity: 40000 L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Mobil Oil New Zealand Limited 22 Amohia Street, Paraparaumu, 5032 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-08-03
TNK20494 | 2025-08-03 | Tankreline NZ Limited |  | UL 1316 | Description: 400170-T2 GRP Double skin 8750mm LOA x 2500mm DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Mobil Kapiti XMK 400170-T2 Name of Designer: Tankreline NZ Limited Capacity: 40000 L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Mobil Oil New Zealand Limited 22 Amohia Street, Paraparaumu, 5032 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-08-03
TNK20495 | 2025-08-03 | Tankreline NZ Limited |  | UL 1316 | Description: 400170-T3 GRP Double skin 8750mm LOA x 2500mm DIA Design Specification: UL 1316 Drawing Number: Mobil Kapiti XMK 400170-T3 Name of Designer: Tankreline NZ Limited Capacity: 40000 L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Mobil Oil New Zealand Limited 22 Amohia Street, Paraparaumu, 5032 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-08-03
TNK20496 | 2025-08-03 | Tankreline NZ Limited |  | UL 1316 | Description: 400170-T4 GRP Double skin 8750mm LOA x 2500mm DIA Design Specification: UL 1316 Tank Type: Below Ground Stationary Tank Drawing Numbers: Mobil Kapiti XMK 400170-T4 Name of Designer: Tankreline NZ Limited Capacity: 40000 L Compartments: 1 | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | Mobil Oil New Zealand Limited 22 Amohia Street, Paraparaumu, 5032 | This tank is constructed as a one-off FIELD CONSTRUCTED TANK. Tank to be constructed in accordance with Tankreline NZ Limited QA Documents QLY-MAN-044. Tank data plate to be attached inside manway. Tank installation to be verified to meet installation requirements of UPSS 1992. | 2028-08-03
TNK20497 | 2025-08-06 | CT Engineering Services Ltd |  | API Standard 650 | Description: 2.4m x 2.6m High CCA/MCA/Boron Tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: C23077D-T178RV1820 Rev.0 & V5RV T1 Name of Designer: CT Engineering Services Ltd Capacity: 11,760L Compartments: 1 | Name: CCA/MCA/Boron Class(es): 6.1B, 6.1D, 6.5A, 6.5B, 6.6A, 8.1A, 8.2B, 8.3A | C T ENGINEERING SERVICES LIMITED 10A Gateway Park Drive, Pōkeno 2402 | Serial no.: T178RV1820 Specific Gravity: 2.0 Seismic design: NZ1170.5 by CMK Engineering. Report No.: C23077-RV1820-2.4x4 Site location: Rosvall Sawmill, 658 Whareora Rd, Whangarei. No wind loading to AS/NZS 1170.2 required as tank to be installed indoors Safe fill height: 2.44m. High level alarm at 2.34m, extra-high level alarm at 2.39m Tank venting to API 2000 (7th Ed.). Max inflow/outflow 270m3/hr. 125mmNB vent. | 2030-08-06
TNK20498 | 2025-08-06 | CT Engineering Services Ltd |  | API Standard 650 | Description: 4.0m x 4.4m High Dilute CCA/MCA/Boron Tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: C23077D-T179RV1820 Rev.0 & V5RV T2 Name of Designer: CT Engineering Services Ltd Capacity: 55,290L Compartments: 1 | Name: Dilute CCA/MCA/Boron Class(es): 6.1B, 6.1D, 6.5A, 6.5B, 6.6A, 8.1A, 8.2B, 8.3A | C T ENGINEERING SERVICES LIMITED 10A Gateway Park Drive, Pōkeno 2402 | Serial no.: T179RV1820 Specific Gravity: 1.1 Seismic design: NZ1170.5 by CMK Engineering. Report No.: C23077-RV1820-4x6 Site location: Rosvall Sawmill, 658 Whareora Rd, Whangarei. No wind loading to AS/NZS 1170.2 required as tank to be installed indoors Safe fill height: 4.19m. High level alarm at 4.09m, extra-high level alarm at 4.14m Tank venting to API 2000 (7th Ed.). Max inflow/outflow 1200m3/hr. Two 200mmNB vents. | 2030-08-06
TNK20499 | 2025-08-06 | CT Engineering Services Ltd |  | API Standard 650 | Description: 4.0m x 4.4m High Dilute CCA/MCA/Boron Tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: C23077D-T180RV1820 Rev.0 & V5RV T3 Name of Designer: CT Engineering Services Ltd Capacity: 55,290L Compartments: 1 | Name: Dilute CCA/MCA/Boron Class(es): 6.1B, 6.1D, 6.5A, 6.5B, 6.6A, 8.1A, 8.2B, 8.3A | C T ENGINEERING SERVICES LIMITED 10A Gateway Park Drive, Pōkeno 2402 | Serial no.: T180RV1820 Specific Gravity: 1.1 Seismic design: NZ1170.5 by CMK Engineering. Report No.: C23077-RV1820-4x6 Site location: Rosvall Sawmill, 658 Whareora Rd, Whangarei. No wind loading to AS/NZS 1170.2 required as tank to be installed indoors Safe fill height: 4.19m. High level alarm at 4.09m, extra-high level alarm at 4.14m Tank venting to API 2000 (7th Ed.). Max inflow/outflow 1200m3/hr. Two 200mmNB vents. | 2030-08-06
TNK20500 | 2025-08-06 | CT Engineering Services Ltd |  | API Standard 650 | Description: 4.0m x 6.0m High Dilute CCA/MCA/Boron Tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: C23077D-T181RV1820 Rev.0 & V5RV T4 Name of Designer: CT Engineering Services Ltd Capacity: 75,400L Compartments: 1 | Name: Dilute CCA/MCA/Boron Class(es): 6.1B, 6.1D, 6.5A, 6.5B, 6.6A, 8.1A, 8.2B, 8.3A | C T ENGINEERING SERVICES LIMITED 10A Gateway Park Drive, Pōkeno 2402 | Serial no.: T181RV1820 Specific Gravity: 1.1 Seismic design: NZ1170.5 by CMK Engineering. Report No.: C23077-RV1820-4x6 Site location: Rosvall Sawmill, 658 Whareora Rd, Whangarei. No wind loading to AS/NZS 1170.2 required as tank to be installed indoors Safe fill height: 5.79m. High level alarm at 5.69m, extra-high level alarm at 5.74m Tank venting to API 2000 (7th Ed.). Max inflow/outflow 1200m3/hr. Two 200mmNB vents. | 2030-08-06
TNK20501 | 2025-08-06 | CT Engineering Services Ltd |  | API Standard 650 | Description: 2.4m x 4.0m High CCA/MCA/Boron Tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: C23077D-T182RV1820 Rev.0 & V5RV T5 Name of Designer: CT Engineering Services Ltd Capacity: 18,100L Compartments: 1 | Name: CCA/MCA/Boron Class(es): 6.1B, 6.1D, 6.5A, 6.5B, 6.6A, 8.1A, 8.2B, 8.3A | C T ENGINEERING SERVICES LIMITED 10A Gateway Park Drive, Pōkeno 2402 | Serial no.: T182RV1820 Specific Gravity: 2.0 Seismic design: NZ1170.5 by CMK Engineering. Report No.: C23077-RV1820-2.4x4 Site location: Rosvall Sawmill, 658 Whareora Rd, Whangarei. No wind loading to AS/NZS 1170.2 required as tank to be installed indoors Safe fill height: 3.84m. High level alarm at 3.74m, extra-high level alarm at 3.79m Tank venting to API 2000 (7th Ed.). Max inflow/outflow 270m3/hr. 125mmNB vent. | 2030-08-06
TNK20502 | 2025-08-06 | CT Engineering Services Ltd |  | API Standard 650 | Description: 2.4m x 2.6m High CCA/MCA/Boron Tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: C23077D-T183RV1820 Rev.0 & V5RV T6 Name of Designer: CT Engineering Services Ltd Capacity: 11,760L Compartments: 1 | Name: CCA/MCA/Boron Class(es): 6.1B, 6.1D, 6.5A, 6.5B, 6.6A, 8.1A, 8.2B, 8.3A | C T ENGINEERING SERVICES LIMITED 10A Gateway Park Drive, Pōkeno 2402 | Serial no.: T183RV1820 Specific Gravity: 2.0 Seismic design: NZ1170.5 by CMK Engineering. Report No.: C23077-RV1820-2.4x4 Site location: Rosvall Sawmill, 658 Whareora Rd, Whangarei. No wind loading to AS/NZS 1170.2 required as tank to be installed indoors Safe fill height: 2.44m. High level alarm at 2.34m, extra-high level alarm at 2.39m Tank venting to API 2000 (7th Ed.). Max inflow/outflow 270m3/hr. 125mmNB vent. | 2030-08-06
TNK20503 | 2025-08-06 | CT Engineering Services Ltd |  | API Standard 650 | Description: 2.4m x 2.6m High CCA/Boron Concentrate Tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: C23077D-T184RV1820 Rev.0 & V5RV T7 Name of Designer: CT Engineering Services Ltd Capacity: 11,760L Compartments: 1 | Name: CCA/Boron Concentrate Class(es): 6.1B, 6.1C, 6.1D, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 6.9A, 8.2B, 8.3A | C T ENGINEERING SERVICES LIMITED 10A Gateway Park Drive, Pōkeno 2402 | Serial no.: T184RV1820 Specific Gravity: 2.0 Seismic design: NZ1170.5 by CMK Engineering. Report No.: C23077-RV1820-2.4x4 Site location: Rosvall Sawmill, 658 Whareora Rd, Whangarei. No wind loading to AS/NZS 1170.2 required as tank to be installed indoors Safe fill height: 2.44m. High level alarm at 2.34m, extra-high level alarm at 2.39m Tank venting to API 2000 (7th Ed.). Max inflow/outflow 60m3/hr. 65mmNB vent. | 2030-08-06
TNK20504 | 2025-08-06 | CT Engineering Services Ltd |  | API Standard 650 | Description: 2.4m x 2.6m High CCA/Boron Concentrate Tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: C23077D-T185RV1820 Rev.0 & V5RV T8 Name of Designer: CT Engineering Services Ltd Capacity: 11,760L Compartments: 1 | Name: CCA/Boron Concentrate Class(es): 6.1B, 6.1C, 6.1D, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 6.9A, 8.2B, 8.3A | C T ENGINEERING SERVICES LIMITED 10A Gateway Park Drive, Pōkeno 2402 | Serial no.: T185RV1820 Specific Gravity: 2.0 Seismic design: NZ1170.5 by CMK Engineering. Report No.: C23077-RV1820-2.4x4 Site location: Rosvall Sawmill, 658 Whareora Rd, Whangarei. No wind loading to AS/NZS 1170.2 required as tank to be installed indoors Safe fill height: 2.44m. High level alarm at 2.34m, extra-high level alarm at 2.39m Tank venting to API 2000 (7th Ed.). Max inflow/outflow 60m3/hr. 60mmNB vent. | 2030-08-06
TNK20505 | 2025-09-15 | TRL Engineering Limited |  | UL 1316 | Tank Type: Below Ground, Fibreglass, Double Skin, Single Compartment Design Specification: UL 1316 Capacity: 37677 litres maximum; SFL 35793 litres Drawing Numbers: TRL-DRW-XCW-103-T2; TRL-DRW-XCW-104-T2 Name of Designer: TRL Engineering Limited Description: GRP Double skinned construction; 2.5m DIA x 8.5m LOA x 13 mm WT Split Tank: No | Name: Petroleum products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | TRL Engineering Limited 60 Chapel Street Otumoetai Tauranga 3110 | SFL @ 95% Maximum In-Situ constructed tank. PCBU has requested reduced SFL to 33,900 litres for operational requirements. Tank fitted with Hydro-guard permanent interstitial monitoring | 2030-09-15
TNK20506 | 2025-09-15 | TRL Engineering Limited |  | UL 1316 | Tank Type: Below Ground, Fibreglass, Double Skin, Single Compartment Design Specification: UL 1316 Capacity: 38587 litres maximum; SFL 36658 litres Drawing Numbers: TRL-DRW-XCW-101-T1; TRL-DRW-XCW-102-T1 Name of Designer: TRL Engineering Limited Description: GRP Double skinned construction; 2.5m DIA x 8.5m LOA x 13 mm WT Split Tank: No | Name: Petroleum products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | TRL Engineering Limited 60 Chapel Street Otumoetai Tauranga 3110 | SFL @ 95% Maximum In-Situ constructed tank. PCBU has requested reduced SFL to 34,700 litres for operational requirements. Tank fitted with Hydro-guard permanent interstitial monitoring | 2030-09-15
TNK 20507 | 2025-09-15 | TRL Engineering Limited |  | UL 1316 | Tank Type: Below Ground, Fibreglass, Double Skin, Single Compartment Design Specification: UL 1316 Capacity: 37751 litres maximum; SFL 35864 litres Drawing Numbers: TRL-DRW-XCW-105-T3; TRL-DRW-XCW-106-T3 Name of Designer: TRL Engineering Limited Description: GRP Double skinned construction; 2.5m DIA x 8.5m LOA x 13 mm WT Split Tank: No | Name: Petroleum products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | TRL Engineering Limited 60 Chapel Street Otumoetai Tauranga 3110 | SFL @ 95% Maximum In-Situ constructed tank. PCBU has requested reduced SFL to 33,900 litres for operational requirements. Tank fitted with Hydro-guard permanent interstitial monitoring. | 2030-09-15
TNK20508 | 2025-09-15 | TRL Engineering Limited |  | UL 1316 | Tank Type: Below Ground, Fibreglass, Double Skin, Single Compartment Design Specification: UL 1316 Capacity: 39009 litres maximum; SFL 37059 litres Drawing Numbers: TRL-DRW-XCW-107-T4; TRL-DRW-XCW-108-T4 Name of Designer: TRL Engineering Limited Description: GRP Double skinned construction; 2.5m DIA x 8.5m LOA x 13 mm WT Split Tank: No | Name: Petroleum products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | TRL Engineering Limited 60 Chapel Street Otumoetai Tauranga 3110 | SFL @ 95% Maximum In-Situ constructed tank. PCBU has requested reduced SFL to 35,100 litres for operational requirements. Tank fitted with Hydro-guard permanent interstitial monitoring. | 2030-09-15
TNK20509 | 2025-09-15 | Dialog Fitzroy Limited |  | AS 1692: 2006 | Description: Horizontal C/S AS3678-300; AS1692:2006 Cat 4, SN: V-1296 Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Drawing Numbers: 102074-MEC-DWG-022 Shts 1~3 Name of Designer: Dialog Fitzroy Capacity: 81,820 Litres Compartments: 1 | Name: Jet Fuel Class(es): 3.1C | Dialog Fitzroy Limited 691 Devon Road, Waiwhakaiho, New Plymouth 4312 |  | 2075-09-15
TNK20510 | 2025-09-15 | Dialog Fitzroy Limited |  | AS 1692: 2006 | Description: Horizontal C/S AS3678-300; AS1692:2006 Cat 4, SN: V-1297 Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 102074-MEC-DWG-022 Shts 1~3 Name of Designer: Dialog Fitzroy Limited Capacity: 81,820 Litres Compartments: 1 | Name: Jet Fuel Class(es): 3.1C | Dialog Fitzroy Limited 691 Devon Road, Waiwhakaiho, New Plymouth 4312 |  | 2075-09-15
TNK20511 | 2025-09-15 | Dialog Fitzroy Limited |  | AS 1692: 2006 | Description: Horizontal C/S AS3678-300; AS1692:2006 Cat 4, SN: V-1295 Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 102074-MEC-DWG-001 Shts 1~3 Name of Designer: Dialog Fitzroy Limited Capacity: 81,820 Litres Compartments: 1 | Name: Jet Fuel Class(es): 3.1C | Dialog Fitzroy Limited 691 Devon Road, Waiwhakaiho, New Plymouth 4312 |  | 2075-09-15
TNK20512 | 2025-09-15 | Ewings Construction Ltd |  | API Standard 650 | Description: Vertical single skin C/S AS3678-250 API650 13th Ed 2020, Seismic NZS1170.5 Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: 6999-51-001 Shts 1~4 Name of Designer: Ewings Construction Ltd Capacity: 663,000 Litres Compartments: 1 | Name: Jet Fuel Class(es): 3.1C | Ewings Engineering Contractors Limited 210 Cumnor Terrace, Woolston, Christchurch 8023 |  | 2075-09-12
TNK20513 | 2025-09-15 | Ewings Construction Ltd |  | API Standard 650 | Description: Vertical single skin C/S AS3678-250 API650 13th Ed 2020, Seismic NZS1170.5. SN:ECL00081 Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: 6999-52-001 Shts 1~4 Name of Designer: Ewing Construction Ltd Capacity: 663,000 Litres Compartments: 1 | Name: Jet Fuel Class(es): 3.1C | Ewings Engineering Contractors Limited 210 Cumnor Terrace, Woolston, Christchurch 8023 |  | 2075-09-15
TNK20514 | 2025-09-15 | Ewings Construction Ltd |  | API Standard 650 | Description: Vertical single skin C/S AS3678-250 API650 13th Ed 2020, Seismic NZS1170.5. SN:ECL00082 Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: 6999-53-001 Shts 1~4 Name of Designer: Ewing Construction Ltd Capacity: 663,000 litres Compartments: 1 | Name: Jet Fuel Class(es): 3.1C | Ewings Engineering Contractors Limited 210 Cumnor Terrace, Woolston, Christchurch 8023 |  | 2075-09-15
TNK20515 | 2025-09-19 | Hendl & Murray Engineering Limited |  | AS1692: 2006 | Description: 3,312L above ground, vertical, cylindrical, single skin, cone top & bottom, bottom insulation Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 23946-03-01, Rev I, 3.1m3 3XDA Holding Tank - 32T75, General Arrangement, Date: 01/09/25 Name of Designer: Hendl & Murray Engineering Limited Capacity: 3,312 Litres Compartments: 1 | Name: Cholic Acid Class(es): 6.5B Name: Isopropyl Alcohol Class(es): 3.1B | HENDL & MURRAY ENGINEERING LIMITED 103 Tawa Street, Melville, Hamilton 3206 | Approved For Drawings: - 23946-03-00, Rev E, 3.1m3 3XDA Holding Tank - 32T75, Pictorial View, Drawn: M.Singh, Date: 10/06/25. - 23946-03-01, Rev I, 3.1m3 3XDA Holding Tank - 32T75, General Arrangement, Drawn: M.Singh, Date: 01/09/25. - 23946-03-02, Rev E, 3.1m3 3XDA Holding Tank - 32T75, Body Details, Drawn: M.Singh, Date: 28/05/25. - 23946-03-03, Rev C, 3.1m3 3XDA Holding Tank - 32T75, Nozzle Detail, Drawn: M.Singh, Date: 10/06/25. - 23946-03-04, Rev B, 3.1m3 3XDA Holding Tank - 32T75, Nozzle Detail 2, Drawn: M.Singh, Date: 09/06/25. - 23946-03-05, Rev B, 3.1m3 3XDA Holding Tank - 32T75, Nozzle Detail 3, Drawn: M.Singh, Date: 09/06/25. - 23946-03-06, Rev B, 3.1m3 3XDA Holding Tank - 32T75, Nozzle Detail 4, Drawn: M.Singh, Date: 09/06/25. - 23946-03-07, Rev A, 3.1m3 3XDA Holding Tank - 32T75, Name Plate Detail, Drawn: M.Singh, Date: 28/05/25. - 23946-01-10, Rev A, Holding & Separation Tank, Typical Inlet Arrangement, Drawn: D.Bell, Date: 01/09/25. - 23946-01-11, Rev A, Holding & Separation Tank, Typical Earth Lug, Drawn: D.Bell, Date: 01/09/25. Approved For: The storage and transfer of Cholic Acid, having a hazard classification of 6.3A, 6.4A, 6.5B and Isopropyl Alcohol, having a hazard classification of 3.1B, 6.1E, 6.4A. References: Design Report: 251521 RP01 RevA 3.1m3 3XDA Holding Tank – 32T75 Design Report, Issued By: Mech Eng Ltd, To: Hendl & Murray Engineering Ltd, Author: Tom Roberts CPEng Meng CMEngNZ, Revision A, Date:12/06/25. Unique serial number to be allocated for tank. Tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2035-09-19
TNK20516 | 2025-09-19 | Hendl & Murray Engineering Limited |  | AS1692: 2006 | Description: 3,793L above ground, vertical, cylindrical,single skin, cone top and bottomstationary container Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 23946-01-01, Rev G, 3.5m3 ML HoldingTank #1 – 32T76, General Arrangement,Date: 01/09/25 Name of Designer: Hendl & Murray Engineering Limited Capacity: 3,793 Litres Compartments: 1 | Name: Cholic Acid Class(es): 6.5B Name: Methanol Class(es): 3.1B, 6.1C, 6.8B, 6.9A | HENDL & MURRAY ENGINEERING LIMITED 103 Tawa Street, Melville, Hamilton 3206 | Approved For Drawings: - 23946-01-00, Rev C, 3.5m3 ML Holding Tank #1 – 32T76, Pictorial View, Drawn: D.Bell, Date: 18/06/25. - 23946-01-01, Rev G, 3.5m3 ML Holding Tank #1 – 32T76, General Arrangement, Drawn: D.Bell, Date: 01/09/25. - 23946-01-02, Rev A, 3.5m3 ML Holding Tank #1 – 32T76, Body Details, Drawn: M.Singh, Date: 29/05/25. - 23946-01-03, Rev A, 3.5m3 ML Holding Tank #1 – 32T76, Nozzle Detail 1, Drawn: D.Bell, Date: 05/06/25. - 23946-01-04, Rev B, 3.5m3 ML Holding Tank #1 – 32T76, Nozzle Detail 2, Drawn: D.Bell, Date: 10/06/25. - 23946-01-05, Rev B, 3.5m3 ML Holding Tank #1 – 32T76, Nozzle Detail 3, Drawn: D.Bell, Date: 18/06/25. - 23946-01-06, Rev B, 3.5m3 ML Holding Tank #1 – 32T76, Nozzle Detail 4, Drawn: D.Bell, Date: 11/06/25. - 23946-01-07, Rev A, 3.5m3 ML Holding Tank #1 – 32T76, Name Plate Detail, Drawn: D.Bell, Date: 10/06/25. - 23946-01-10, Rev A, Holding & Separation Tank, Typical Inlet Arrangement, Drawn: D.Bell, Date: 01/09/25. - 23946-01-11, Rev A, Holding & Separation Tank, Typical Earth Lug, Drawn: D.Bell, Date: 01/09/25. Approved For: The storage and transfer of Cholic Acid, having a hazard classification of 6.3A, 6.4A, 6.5B and Methanol, having a hazard classification of 3.1B, 6.1C,6.4A, 6.8B, 6.9A. References: Design Report: 251522 RP01 RevA 3.5m3 ML Holding Tank – 32T76 Design Report, Issued By: Mech Eng Ltd, To: Hendl & Murray Engineering Ltd,Author: Tom Roberts CPEng Meng CMEngNZ, Revision A, Date:30/06/25. Unique serial number to be allocated for tank. Tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2035-09-19
TNK20517 | 2025-09-19 | Hendl & Murray Engineering Limited |  | AS1692: 2006 | Description: 3,000L above ground, vertical, cylindrical, single skin, cone top and bottom stationary container Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 23946-02-01, Rev G, 2.8m3 ML Holding Tank #2 – 32T77, General Arrangement, Date: 01/09/25 Name of Designer: Hendl & Murray Engineering Limited Capacity: 3,000 Litres Compartments: 1 | Name: Cholic Acid Class(es): 6.5B Name: Methanol Class(es): 3.1B, 6.1C, 6.8B, 6.9A | HENDL & MURRAY ENGINEERING LIMITED 103 Tawa Street, Melville, Hamilton 3206 | Approved For Drawings: - 23946-02-00, Rev C, 2.8m3 ML Holding Tank #2 – 32T77, Pictorial View, Drawn: D.Bell, Date: 18/06/25. - 23946-02-01, Rev G, 2.8m3 ML Holding Tank #2 – 32T77, General Arrangement, Drawn: D.Bell, Date: 01/09/25. - 23946-02-02, Rev A, 2.8m3 ML Holding Tank #2 – 32T77, Body Details, Drawn: M.Singh, Date: 05/06/25. - 23946-02-03, Rev A, 2.8m3 ML Holding Tank #2 – 32T77, Nozzle Detail 1, Drawn: D.Bell, Date: 05/06/25. - 23946-02-04, Rev C, 2.8m3 ML Holding Tank #2 – 32T77, Nozzle Detail 2, Drawn: D.Bell, Date: 18/06/25. - 23946-02-05, Rev B, 2.8m3 ML Holding Tank #2 – 32T77, Nozzle Detail 3, Drawn: D.Bell, Date: 18/06/25. - 23946-02-06, Rev B, 2.8m3 ML Holding Tank #2 – 32T77, Nozzle Detail 4, Drawn: D.Bell, Date: 11/06/25. - 23946-02-07, Rev A, 2.8m3 ML Holding Tank #2 – 32T77, Name Plate Detail, Drawn: D.Bell, Date: 10/06/25. - 23946-01-10, Rev A, Holding & Separation Tank, Typical Inlet Arrangement, Drawn: D.Bell, Date: 01/09/25. - 23946-01-11, Rev A, Holding & Separation Tank, Typical Earth Lug, Drawn: D.Bell, Date: 01/09/25 Approved For: The storage and transfer of Cholic Acid, having a hazard classification of 6.3A, 6.4A, 6.5B and Methanol, having a hazard classification of 3.1B, 6.1C, 6.4A, 6.8B, 6.9A. References: Design Report: 251523 RP01 RevA 2.8m3 ML Holding Tank – 32T77 Design Report, Issued By: Mech Eng Ltd, To: Hendl & Murray Engineering Ltd, Author: Tom Roberts CPEng Meng CMEngNZ, Revision A, Date:30/06/25. Unique serial number to be allocated for tank. Tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2035-09-19
TNK20518 | 2025-09-19 | Hendl & Murray Engineering Limited |  | AS1692: 2006 | Description: 3,566L above ground, vertical, cylindrical, single skin, cone top and bottom stationary container Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 23946-00-01, Rev E, 3.2m3 IPA-TOL Separation Vessel – 32T78, General Arrangement, Date: 01/09/25 Name of Designer: Hendl & Murray Engineering Limited Capacity: 3,566 Litres Compartments: 1 | Name: Bile Acid Solids Class(es): 6.1D, 6.5B Name: Isopropyl Alcohol Class(es): 3.1B | HENDL & MURRAY ENGINEERING LIMITED 103 Tawa Street, Melville, Hamilton 3206 | Approved For Drawings: - 23946-00-00, Rev C, 3.2m3 IPA-TOL Separation Vessel – 32T78, Pictorial View, Drawn: K.Patil, Date: 04/07/25. - 23946-00-01, Rev E, 3.2m3 IPA-TOL Separation Vessel – 32T78, General Arrangement, Drawn: D.Bell, Date: 01/09/25. - 23946-00-02, Rev B, 3.2m3 IPA-TOL Separation Vessel – 32T78, Body Details, Drawn: M.Singh, Date: 23/06/25. - 23946-00-03, Rev A, 3.2m3 IPA-TOL Separation Vessel – 32T78, Nozzle Detail 1, Drawn: K.Patil, Date: 11/06/25. - 23946-00-04, Rev C, 3.2m3 IPA-TOL Separation Vessel – 32T78, Nozzle Detail 2, Drawn: K.Patil, Date: 03/07/25. - 23946-00-05, Rev B, 3.2m3 IPA-TOL Separation Vessel – 32T78, Nozzle Detail 3, Drawn: K.Patil, Date: 12/06/25. - 23946-00-06, Rev A, 3.2m3 IPA-TOL Separation Vessel – 32T78, Name Plate Detail, Drawn: D.Bell, Date: 11/06/25. - 23946-00-08, Rev B, Custom Sight Glass, Glass, Drawn: D.Bell, Date: 03/07/25. - 23946-00-09, Rev A, Custom Sight Glass, Gaskets, Drawn: D.Bell, Date: 19/06/25. - 23946-00-10, Rev B, Custom Sight Glass, Black Flange Machining Detail, Drawn: D.Bell, Date: 03/07/25. - 23946-00-11, Rev B, Custom Sight Glass, Front Flange Machining Detail, Drawn: D.Bell, Date: 03/07/25. - 23946-00-13, Rev A, Custom Sight Glass, Sight Glass Assembly, Drawn: D.Bell, Date: 04/08/25. - 23946-01-10, Rev A, Holding & Separation Tank, Typical Inlet Arrangement, Drawn: D.Bell, Date: 01/09/25. - 23946-01-11, Rev A, Holding & Separation Tank, Typical Earth Lug, Drawn: D.Bell, Date: 01/09/25. Approved For: The storage and transfer of Bile Acid Solids, having a hazard classification of 6.1D, 6.3A, 6.4A, 6.5B and Isopropyl Alcohol, having a hazard classification of 3.1B, 6.1E, 6.4A. References: Design Report: 251524 RP01 RevA 3.2m3 IPA-TOL Separation Vessel – 32T78 Design Report, Issued By: Mech Eng Ltd, To: Hendl & MurrayEngineering Ltd, Author: Tom Roberts CPEng Meng CMEngNZ, Revision A, Date:14/07/25. Design Statement - Custom Component - Sight Glass - Job No.: 251524, Date: 22/08/25, Tom Roberts, 32T78. Unique serial number to be allocated for tank. Tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank name plate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fi ll level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2035-09-19
TNK20519 | 2025-09-29 | TP Mechanical & Engineering Limited |  | AS 1692 | Tank Type: Above Ground, Steel, Single Skin Design Specification: AS 1692 Capacity: 70,000 litres maximum; 65,000 litres SFL. Drawing Numbers: TPME-23567-01-00 Tank GA, shts 1-19 Name of Designer: TP Mechanical & Engineering Limited Description: Single skinned, horizontal Category 4 tank, 3.7m DIA x 7.1m LOA Split Tank: No | Name: Refined waste oil for fuel oil under HSNOCOP63 - HSR002607. Flash point exceeding 93 degrees Celsius. Maximum s.g. 0.89. Class(es): 6.3B, 6.7B | T&G Global Limited 135 Lynds Road Ohaupo 3881 | This design certificate is issued after the construction of the tank in 2022. | 2030-09-29
TNK20520 | 2025-10-07 | TRL Engineering Limited |  | UL 1316 | Tank Type: Below Ground, Fibreglass, Double Skin, Single Compartment Design Specification: UL 1316 Capacity: 38,506 litres maximum; 36,580 litres SFL Drawing Numbers: TRL-DRW-XMW-103; TRL-DRW-XMW-104 Name of Designer: TRL Engineering Limited Description: XMW-400018-T2; GRP Double skinned, 2.5m DIA x 8.6m LOA x 13mm WT. Split Tank: No | Name: Petroleum Products Class(es):3.1A, 3.1B, 3.1C, 3.1D | TRL Engineering Limited 319 Great South Road Manurewa Auckland 2102 | SFL @ 95% Maximum In-Situ constructed tank. PCBU has reduced SFL to 34,600 litres for operational requirements. Tank fitted with Hydro-guard permanent interstitial monitoring. | 2030-10-07
TNK20521 | 2025-10-07 | TRL Engineering Limited |  | UL 1316 | Tank Type: Below Ground, Fibreglass, Double Skin, Single Compartment Design Specification: UL 1316 Capacity: 37,807 litre maximum; 35,900 litres SFL Drawing Numbers: TRL-DRW-XMW-101; TRL-DRW-XMW-102 Name of Designer: TRL Engineering Limited Description: XMW-400018-T1; GRP Double skinned, 2.5m DIA x 8.5m LOA x 13mm WT. Split Tank: No | Name: Petroleum Products Class(es):3.1A, 3.1B, 3.1C, 3.1D | TRL Engineering Limited 319 Great South Road Manurewa Auckland 2102 | SFL @ 95% Maximum In-Situ constructed tank. PCBU has reduced SFL to 34,000 litres for operational requirements. Tank fitted with Hydro-guard permanent interstitial monitoring | 2030-10-07
TNK20522 | 2025-10-30 | TRL Engineering Limited |  | UL 1316 | Tank Type: Below Ground, Fibreglass, Double Skin, Single Compartment Design Specification: UL 1316 Capacity: 39,011 litres maximum; 37,000 litres SFL Drawing Numbers: TRL-DRW-XMW-400018-T3-105; TRL-DRW-XMW-400018-T3-106 Name of Designer: TRL Engineering Limited Description: XMW-400018-T3; GRP Double skinned, 2.5m DIA x 8.5m LOA x 13mm WT. Split Tank: No | Name: Petroleum Products Class(es):3.1A, 3.1B, 3.1C, 3.1D | TRL Engineering Limited 319 Great South Road Manurewa Auckland 2102 | SFL @ 95% Maximum In-Situ constructed tank. PCBU has reduced SFL to 35,100 litres for operational requirements. Tank fitted with Hydro-guard permanent interstitial monitoring | 2030-10-30
TNK20523 | 2025-10-30 | TRL Engineering Limited |  | UL 1316 | Tank Type: Below Ground, Fibreglass, Double Skin, Single Compartment Design Specification: UL 1316 Capacity: 29956 litres maximum; 28,400 litres SFL Drawing Numbers: TRL-DRW-XWS-T1-101; TRL-DRW-XWS-T1-102 Name of Designer: TRL Engineering Limited Description: XWS-20001-T1; GRP Double skinned, 2.5m DIA x 6.8m LOA x 13mm WT. Split Tank: No | Name: Petroleum Products Class(es):3.1A, 3.1B, 3.1C, 3.1D | TRL Engineering Limited 319 Great South Road Manurewa Auckland 2102 | SFL @ 95% Maximum In-Situ constructed tank. PCBU has reduced SFL to 26,900 litres for operational requirements. Tank fitted with Hydro-guard permanent interstitial monitoring | 2030-10-30
TNK20524 | 2025-11-03 | NDA Tira Limited |  | AS1692: 2006 | Description: Vertical Cone roof, cone down floor on legs 304L S/S Cat 5 Design Specification: AS1692: 2006 Tank Type: Process Container Drawing Numbers: 7652902-G01 Name of Designer: NDA Tira Limited Capacity: 25,393 litres Compartments: 1 | Name: Nitric Acid 5% Class(es): 6.9B, 8.1A, 8.2C, 8.3A | NDA Engineering Limited 709 Te Rapa Road, Te Rapa, Hamilton 3200 | This tank is destined for Fonterra at Te Rapa. This certificate expiry is based on the design life of 25Yrs | 2055-11-03
TNK20525 | 2025-11-03 | NDA Tira Limited |  | AS1692: 2006 | Description: Vertical Cone roof, cone down floor on legs 304L S/S Cat 5 Design Specification: AS1692: 2006 Tank Type: Process Container Drawing Numbers: 7652901-G01 Name of Designer: NDA Engineering (Tira) Capacity: 25393 litres Compartments: 1 | Name: Caustic Soda 5% Class(es): 6.1D, 8.1A, 8.2B, 8.3A | NDA Engineering Limited 709 Te Rapa Road, Te Rapa, Hamilton 3200 | This tank is destined for Fonterra at Te Rapa. This certificate expiry is based on the design life of 25Yrs | 2055-11-03
TNK20526 | 2025-11-03 | Etech Engineering Services |  | AS1692: 2006 | Description: Rectangular lift off lid 316ss/304ss Design Specification: AS1692: 2006 Tank Type: Process Container Drawing Numbers: EES-TPP-1050 11 shts Name of Designer: Etech Engineering Services Capacity: 1050 litres Compartments: 1 | Name: Ethanol Class(es): 3.1B Name: Formaldehyde Class(es): 3.1C, 6.1B, 6.1C, 6.5B, 6.6B, 6.7A, 6.9B, 8.2C, 8.3A Name: Iso Propyl Alcohol Class(es): 3.1B | ETECH NZ Limited 130 Kaimanawa Street, Kelvin Grove, Palmerston North 4414 | Tank is destined for Te Papa Trentham. Emergency Vent subject to periodic testing. Tank is not to be lifted by the lid eyes. Tank only lifted when empty. | 2075-11-03
TNK20527 | 2025-11-03 | Etech Engineering Services |  | AS1692: 2006 | Description: Rectangular lift oﬀ lid 316ss/304ss Design Specification: AS1692: 2006 Tank Type: Process Container Drawing Numbers: EES-TPP-1600 11 shts Name of Designer: Etech Engineering Services Capacity: 1600 Litres Compartments: 1 | Name: Ethanol Class(es): 3.1B Name: Formaldehyde Class(es): 3.1C, 6.1B, 6.1C, 6.5B, 6.6B, 6.7A, 6.9B, 8.2C, 8.3A Name: Iso Propyl Alcohol Class(es): 3.1B | ETECH NZ Limited 130 Kaimanawa Street, Kelvin Grove, Palmerston North 4414 | Tank is destined for Te Papa Trentham. Emergency Vent subject to periodic testing. Tank is not to be lifted by the lid eyes. Tank only lifted when empty. | 2075-11-03
TNK20528 | 2025-11-03 | Etech Engineering Services |  | AS1692: 2006 | Description: Rectangular lift oﬀ lid 316ss/304ss Design Specification: AS1692: 2006 Tank Type: Process Container Drawing Numbers: EES-EES-TPP-1660 (11 sheets) Name of Designer: Etech Engineering Services Capacity: 1660 Litres Compartments: 1 | Name: Ethanol Class(es): 3.1B Name: Formaldehyde Class(es): 3.1C, 6.1B, 6.1C, 6.5B, 6.6B, 6.7A, 6.9B, 8.2C, 8.3A Name: Iso Propyl Alcohol Class(es): 3.1B | ETECH NZ Limited 130 Kaimanawa Street, Kelvin Grove, Palmerston North 4414 | Tank is destined for Te Papa Trentham. Emergency Vent subject to periodic testing. Tank is not to be lifted by the lid eyes. Tank only lifted when empty. | 2075-11-03
TNK20529 | 2025-11-03 | Etech Engineering Services |  | AS1692: 2006 | Description: Rectangular lift off lid 316ss/304/ss Design Specification: AS1692: 2006 Tank Type: Process Container Drawing Numbers: EES-EES-TPP-3349 (11 sheets) Name of Designer: Etech Engineering Services Capacity: 3349 Litres Compartments: 1 | Name: Ethanol Class(es): 3.1B Name: Formaldehyde Class(es): 3.1C, 6.1B, 6.1C, 6.5B, 6.6B, 6.7A, 6.9B, 8.2C, 8.3A Name: Iso Propyl Alcohol Class(es): 3.1B | ETECH NZ Limited 130 Kaimanawa Street, Kelvin Grove, Palmerston North 4414 | Tank is destined for Te Papa Trentham. Emergency Vent subject to periodic testing. Tank is not to be lifted by the lid eyes. Tank only lifted when empty. | 2075-11-03
TNK20530 | 2025-11-10 | Plastics Constructions Limited |  | AS 2634 | Tank Type: Above Ground Stationary Tank Design Specification: AS 2634 Capacity: 12032 litres maximum; 11431 litres SFL. Drawing Numbers: H2O Engineering P731-002-rev-D Name of Designer: Plastics Constructions Limited Description: #3122 Fibre-glass wrapped PVC 2200mm diameter x 3400mm high, single skinned 8mm WT Split Tank: No | Name: Sodium hypochlorite <15% aqueous solution Class(es): 8.2C, 8.3A | Plastics Constructions Limited 26 Fremlin Place Avondale Auckland 1026 | This design certificate has been issued after the construction of the tank. DOM 2020. Mech Eng Limited Design Report 191963-RP-01 & RP02. Verification of construction to the design standard is required for a Stationary Container System certification. | 2030-11-10
TNK20531 | 2025-11-10 | Plastics Constructions Limited / Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 5217 litres maximum; 4956 litres SFL Drawing Numbers: H2O Engineering, P731-006-rev E, Citric acid tank, General Arrangement Name of Designer: Plastics Constructions Limited / Mech Eng Limited Description: #3125 HDPE 1800mm diameter x 2200mm high, single skinned 12mm WT Split Tank: No | Name: Citric acid 49% aqueous solution s.g 1.25 maximum Class(es): 8.3A | Plastics Constructions Limited 26 Fremlin Place Avondale Auckland 1026 | This design certificate has been issued after the construction of the tank. DOM 2020. Mech Eng Limited Design Report 191965-RP-01 & RP02. Verification of construction to the design standard is required for a Stationary Container System certification. | 2030-11-10
TNK20532 | 2025-11-10 | Plastics Constructions Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 27423 litres maximum; 26052 litres SFL. Drawing Numbers: H2O Engineering: P731-004 Alum Tank 1 General Arrangement Name of Designer: Plastics Constructions Limited Description: #3123 HDPE 3500mm diameter x 3000mm high, single skinned 24/12mm WT Split Tank: No | Name: Aluminium sulphate aqueous solution, s.g. 1.2 maximum Class(es): 6.1D, 8.1A | Plastics Constructions Limited 26 Fremlin Place Avondale Auckland 1026 | This design certificate has been issued after the construction of the tank DOM 2020. Mech Eng Limited Design Report 191961-RP01-RP02. Verification of construction to the design standard is required for a Stationary Container System certification. | 2030-11-10
TNK20533 | 2025-11-10 | Plastics Constructions Limited |  | AS 2634 | Tank Type: Above Ground Stationary Tank Design Specification: AS 2634 Capacity: 12032 litres maximum; 11431 litres SFL. Drawing Numbers: H2O Engineering P731-001-rev-D, Sodium hypochlorite tank 1 - General Arrangement Name of Designer: Plastics Constructions Limited Description: #3121 Fibre-glass wrapped PVC 2200mm diameter x 3400mm high, single skinned 8mm WT Split Tank: No | Name: Sodium hypochlorite <15% aqueous solution Class(es): 8.2C, 8.3A | Plastics Constructions Limited 26 Fremlin Place Avondale Auckland 1026 | This design certificate has been issued after the construction of the tank. DOM 2020. Mech Eng Limited Design Report 191963-RP-01 & RP02. Verification of construction to the design standard is required for a Stationary Container System certification. | 2030-11-10
TNK20534 | 2025-11-10 | Plastics Constructions Limited / Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 27423 litres maximum; 26052 litres SFL. Drawing Numbers: H2O Engineering: P731-005 Alum Tank 2 General Arrangement Name of Designer: Plastics Constructions Limited / Mech Eng Limited Description: #3124 HDPE 3500mm diameter x 3000mm high, single skinned 24/12mm WT Split Tank: No | Name: Aluminium sulphate aqueous solution, s.g. 1.2 maximum Class(es): 6.1D, 8.1A | Plastics Constructions Limited 26 Fremlin Place Avondale Auckland 1026 | This design certificate has been issued after the construction of the tank. DOM 2020. Mech Eng Limited Design Report 191961-RP01-RP02. Verification of construction to the design standard is required for a Stationary Container System certification | 2030-11-10
TNK20535 | 2025-11-19 | Motovated Design & Analysis Limited | FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS 1692 | Tank Type: Above Ground, Steel, Double Skin Design Specification: AS 1692 Capacity: See Details of Certification Drawing Numbers: Fuelchief: VG5-110,000-FAB, VG5-RANGE-DETAILS, VG5-Secondary-End-Assy; Name of Designer: Joe Bain, Motovated Design & Analysis Limited Description: Category 4 Double-skinned tank. Integral secondary containment is greater than 110%. Split Tank: No | Name: Diesel, Refined waste oil. Class(es): 3.1D, 6.7B | Fuelchief Limited Innovation Park Lot 15/185 Kirk Road, Templeton, Christchurch 7678 | This certificate includes VG5-49,100; VG5-73,600; VG5-98,000; VG5-110,000. Primary and Secondary Tank shell construction must be minimum 6.35mm thick mild steel (1/4"). End plates 8mm minimum mild steel and braced per drawings. Maximum capacities and safe fill levels per drawing VG5-RANGE-DETAILS. | 2030-11-19 | FAB0093
TNK20536 | 2025-11-19 | TRL Engineering Limited |  | UL 1316 | Tank Type: Below Ground, Fibreglass, Double Skin, Single Compartment Design Specification: UL 1316 Capacity: 37,950 litres maximum; 36,050 litres SFL Drawing Numbers: TRL-DRW-XMW-107; TRL-DRW-XMW-108 Name of Designer: TRL Engineering Limited Description: XMW-400018-T4; GRP Double skinned, 2.5m DIA x 8.5m LOA x 13mm WT Split Tank: No | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | TRL Engineering Limited 319 Great South Road, Manurewa, Auckland 2102 | SFL @ 95% Maximum In-Situ constructed tank. PCBU has reduced SFL to 34,100 litres for operational requirements. Tank fitted with Hydro-guard permanent interstitial monitoring.34,100 litres | 2030-11-19
TNK20537 | 2025-11-24 | TRL Engineering Limited |  | UL 1316 | Tank Type: Below Ground, Fibreglass, Double Skin, Single Compartment Design Specification: UL 1316 Capacity: 39791 litres maximum; 37,800 litres SFL Drawing Numbers: TRL-DRW-XWS-103; TRL-DRW-XWS-104 Name of Designer: TRL Engineering Limited Description: XWS-20001-T2; GRP Double skinned, 2.4m DIA x 8.8m LOA x 13mm WT. Split Tank: No | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | TRL Engineering Limited 17 Seddon Street Waihi, Hauraki District 3610 | SFL @ 95% Maximum In-Situ constructed tank. PCBU has reduced SFL to 35,800 litres for operational requirements. Tank fitted with Hydro-guard permanent interstitial monitoring. | 2030-11-24
TNK20538 | 2025-12-02 | Eneraque Pty Ltd |  | AS 1692 | Tank Type: Above Ground, Steel, Double Skin Design Specification: AS 1692 Capacity: 680 litres maximum; 600 litres SFL Drawing Numbers: 12354-PD-DWG-00004 rev A Shts 1-3 Name of Designer: Eneraque Pty Ltd Description: ENR-BT-600-251118NZ; Generator Engine Belly Tank - Category 3; 2.96m LOA x 1.29m W x 0.21m H x 5mm WT, double skinned > 110% secondary containment. Split Tank: No | Name: Diesel Only Class(es): 3.1D | Eneraque NZ Limited 40 Oranga Avenue Onehunga Auckland 1061 | One off tank construction. Manufactured by FUZHOU UNIWELL POWER EQUIPMENT Co. Ltd. Stationary container system certification to verify manufacturer QA for fabrication of the tank. Tank vent to be fitted such that it terminates external to the generator engine container a minimum of 150mm above the tank top and the tank fill point. | 2030-12-02
TNK20539 | 2025-12-02 | Eneraque Pty Ltd |  | AS 1692 | Tank Type: Above Ground, Steel, Double Skin Design Specification: AS 1692 Capacity: 1350 litres maximum; 1250 litres SFL Drawing Numbers: 12354-PD-DWG-00003 rev A Shts 1-3 Name of Designer: Eneraque Pty Ltd Description: ENR-BT-1250-251117NZ; Generator Engine Belly Tank - Category 3; 3.4m LOA x 1.8m W x 0.26m H x 5mm WT, double skinned > 110% secondary containment. Split Tank: No | Name: Diesel Only Class(es): 3.1D | Eneraque NZ Limited 40 Oranga Avenue Onehunga Auckland 1061 | One off tank construction. Manufactured by FUZHOU UNIWELL POWER EQUIPMENT Co. Ltd. Stationary container system certification to verify manufacturer QA for fabrication of the tank. Tank vent to be fitted such that it terminates external to the generator engine container a minimum of 150mm above the tank top and the tank fill point | 2030-12-02
TNK20540 | 2025-12-08 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 2175 litres maximum; 2000 litres SFL. Drawing Numbers: PCL: 3458: 2000L Bunded Tank TK0301 (#3458) Caustic Soda General Arrangement Name of Designer: Mech Eng Limited Description: T#3458; Integral secondary contained, HDPE, 1630mm H x 1450mm OD x 12/22mm WT. Split Tank: No | Name: Sodium hydroxide (Caustic soda) 50% w/w aqueous solution, maximum s.g.1.52. Class(es): 6.1D, 6.7A, 6.9A, 8.1A, 8.2B, 8.3A | Plastics Constructions Limited 26 Fremlin Place Avondale Auckland 1026 | Tank is a one off construction. Design report Mech Eng Limited 252181-RP01-RevA. Construction to be according to Plastics Constructions Limited QA manual. | 2030-12-08
TNK20541 | 9/12/025 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 20,000 litres maximum; 19,000 litres SFL Drawing Numbers: Prominent 408698-01/10 Name of Designer: Mech Eng Limited Description: T#3459; Integral secondary contained, HDPE, 3348mm OD, 3330mm HOA, 15/27mm WT. Greater than 110% SC. Split Tank: No | Name: Aluminium sulphate aqueous solution, 1.33 s.g max. Class(es): 8.1A | ProMinent New Zealand Limited 6A Enterprise Drive Henderson Auckland 0612 | Tank is a one off construction. Design report Mech Eng Limited 252121-RP01-RevA. Construction to be according to Plastics Constructions Limited QA manual. | 2030-12-09
TNK20542 | 2025-12-12 | Carlyon Civil Construction Limited |  | API Standard 650 | Description: 107,184L above ground, vertical, cylindrical, single skin, cone top & flat bottom stationary tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: J1065 - 100kL-001, (100kL Processed Oil Tank #7 & #9), Sheet 1: General Arrangement, Rev 4, 27/08/25 Name of Designer: Carlyon Civil Construction Limited Capacity: 107,184 Litres Compartments: 1 | Name: Processed oil Class(es): 6.7B | CARLYON CIVIL CONSTRUCTION LIMITED 12 Manchester Place, Te Rapa, Hamilton 3200 | Motovated's Project Number: 8522. FAB No.: FAB0083. Manufacturer's Tank Serial No.: Name Plate. Date of Manufacture: Name Plate. Maximum Safe Fill Level = 8728mm = 96,398 Litres. Approved For Drawings: - J1065 - 100kL-001, (100kL Processed Oil Tank #7 & #9), Sheet 1: General Arrangement, Rev 4, 27/08/25. - J1065 - 100kL-002, (100kL Processed Oil Tank #7 & #9), Sheet 2: Nozzle Layout, Rev 4, 27/08/25. - J1065 - 100kL-003, (100kL Processed Oil Tank #7 & #9), Sheet 3: Construction Detail, Rev 4, 27/08/25. - J1065 - 100kL-004, (100kL Processed Oil Tank #7 & #9), Sheet 4: Drain Detail, Rev 4, 27/08/25. - J1065 - 100kL-004, (100kL Processed Oil Tank #7 & #9), Sheet 5: Part Detailing, Rev 4, 27/08/25. - J1065 - 100kL-105, (100kL Processed Oil Tank #7 & #9), Sheet 6: Anchoring Seat Detailing, Rev 4, 27/08/25. - J1065 - 100kL-106, (100kL Processed Oil Tank #7 & #9), Sheet 7: Lifting Lug Detail, Rev 4, 27/08/25. - J1065 - 100kL-106, (100kL Processed Oil Tank #7 & #9), Sheet 8: Lifting Lug Detail, Rev 4, 27/08/25. - J1065 - 100kL-106, (100kL Processed Oil Tank #7 & #9), Sheet 9: Barrier Rail Detail, Rev 4, 27/08/25. - J1065 - 100kL-106, (100kL Processed Oil Tank #7 & #9), Sheet 10: Barrier Rail Parts, Rev 4, 27/08/25. Approved For: The storage and transfer of processed oil, having a hazard classification of 6.3B, 6.7B, 9.1C. Tank manufacturer's Serial Numbers: 1065-315 & 1065-320. References: Engineering PS1: 8316-1002, 100kL WPC Oil Tank PS1, Rev00, 14Mar25. Unique serial number to be allocated for tank. Tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2035-12-12
TNK20543 | 2025-12-13 | NDA - TIRA |  | AS1692: 2006 | Description: Vertical Cone roof, cone down floor on legs 304L S/S Cat 5 Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: 7789401-G01 and 7789401-001~010; 7789401-014~015; 7789401-018~019 Name of Designer: NDA - TIRA Capacity: 50,000 Litres Compartments: 1 | Name: Ethanol 96.6% Class(es): 3.1B | NDA ENGINEERING LIMITED 709 Te Rapa Road, Te Rapa, Hamilton 3200 | This design is for 2 tanks destined for Lion Nathan Auckland. | 2075-12-13
TNK20544 | 2025-12-16 | TRL Engineering Limited |  | UL 1316 | Tank Type: Below Ground, Fibreglass, Double Skin, Single Compartment Design Specification: UL 1316 Capacity: 39894 litres maximum; 37,900 litres SFL Drawing Numbers: TRL-DRW-XWS-105; TRL-DRW-XWS-106 Name of Designer: TRL Engineering Limited Description: XWS-20001-T3; GRP Double skinned, 2.5m DIA x 8.8m LOA x 13mm WT. Split Tank: No | Name: Petroleum Products Class(es): 3.1A, 3.1B, 3.1C, 3.1D | TRL Engineering Limited 17 Seddon Street Waihi Hauraki District 3610 | SFL @ 95% Maximum In-Situ constructed tank. PCBU has reduced SFL to 35,900 litres for operational requirements. Tank fitted with Hydro-guard permanent interstitial monitoring. | 2030-12-16
TNK20545 | 2025-12-17 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 4973 litres maximum; 4704 litres SFL. Drawing Numbers: H2O Engineering 2013454.041-revA Name of Designer: Mech Eng Limited Description: T#3460; HDPE single-skinned, 2160 mm HOA x 1850 mm DIA x 15/27 mm WT. Split Tank: No | Name: Sodium hypochlorite 1% aqueous solution maximum 1.02 s.g. Class(es): 8.2C, 8.3A | Plastics Constructions Limited 26 Fremlin Place Avondale Auckland 1026 | Mech Eng Limited Design Report-252201-RP01-Rev A Tank Construction to be in accordance with Plastics Constructions Limited QA Documentation April 2023. This Design Certificate has been issued after the construction of the tank. | 2030-12-17
TNK20546 | 2026-01-21 | Hendl & Murray Engineering Limited and Tom Roberts |  | API Standard 650 | Description: 29,242 L above ground, vertical, cylindrical, insulated tank Design Specification: API Standard 650 Tank Type: Above Ground Stationary Tank Drawing Numbers: 24178-00-00 to 09, Rev E, 25m³ Caustic Tank, Drawn: K.Patil, Date: 24/11/25 Name of Designer: Hendl & Murray Engineering Limited and Tom Roberts Capacity: 29,242 Litres Compartments: 1 | Name: ALKBLEND S500 (Caustic) Class(es): 8.1A, 8.2B, 8.3A | HENDL & MURRAY ENGINEERING LIMITED 103 Tawa Street, Melville, Hamilton, 3206 | Approved For Drawings: - 24178-00-00, Rev E, 25m³ Caustic Tank, Pictorial View, Drawn: K.Patil, Date: 19/11/25. - 24178-00-01, Rev E, 25m³ Caustic Tank, General Arrangement, Drawn: K.Patil, Date: 19/11/25. - 24178-00-02, Rev D, 25m³ Caustic Tank, Body Detail, Drawn: K.Patil, Date: 24/11/25. - 24178-00-03, Rev D, 25m³ Caustic Tank, Nozzle Detail I, Drawn: K.Patil, Date: 24/11/25. - 24178-00-04, Rev E, 25m³ Caustic Tank, Nozzle Detail II, Drawn: K.Patil, Date: 24/11/25. - 24178-00-05, Rev C, 25m³ Caustic Tank, Circ Handrail Detail, Drawn: K.Patil, Date: 20/11/25. - 24178-00-06, Rev D, 25m³ Caustic Tank, Manway Detail, Drawn: K.Patil, Date: 24/11/25. - 24178-00-07, Rev B, 25m³ Caustic Tank, Ladder Detail, Drawn: K.Patil, Date: 12/11/25. - 24178-00-08, Rev A, 25m³ Caustic Tank, Ladder Support Bracket, Drawn: K.Patil, Date: 11/11/25. - 24178-00-09, Rev B, 25m³ Caustic Tank, Name Plate, Drawn: K.Patil, Date: 13/10/25. Approved For: The storage and transfer of ALKBLEND S500 (Caustic) having hazard classification 8.1A, 8.2B, 8.3A, 9.1D, 9.3C. References: Producer Statement - PS1 - Design - 252051, Issued By: Mech Eng Ltd, To: H2O Engineering / Contact Energy, To Be Supplied To: Taupo District Council, In Respect Of: 25m³ Caustic Tank, At: Contact Energy, Te Mihi Stage 2, Wairakei Steamfield, Taupo, Signed By: Tom Roberts (CPEng #1024350), Date: 20-Jan-26. Design Report: 252051 RP01 RevA H20 Engineering 25m3 Caustic Tank Design Report, Issued By: Mech Eng Ltd, To: Hendl & Murray Engineering Ltd, Author: Tom Roberts (CPEng #1024350), Date: 05-Dec-25. Unique serial number to be allocated for tank. Tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-01-21
TNK20547 | 2026-01-27 | Motovated Design & Analysis Limited | FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | BS 799-5 SWI Above Ground Tank Connected to Gen Set | Tank Type: Above Ground Stationary Tank Design Specification: BS 799-5 SWI Above Ground Tank Connected to Gen Set Capacity: See Details of Certification Drawing Numbers: Fuelchief GT-2000-GA Rev A; GT-1000-GA Rev A Name of Designer: Motovated Design & Analysis Limited Description: GT-2025; Generator set belly tank, double skinned >110% secondary containment. Split Tank: No | Name: Diesel Class(es): 3.1D | Fuelchief Limited Innovation Park, Lot 15/185 Kirk Road Templeton Christchurch 7678 | Two variant sizes: 2198 litres maximum; 2000 litres SFL. OR 1000 litres maximum, 970 litres SFL. Motovated Design & Analysis Ltd, PS1-8824. Genset-belly tank limited to the JCB G400QX-G600QX gen-set range. 50mm (2" BSP) free vent to be fitted to tank nozzle without reduction of nominal bore. Vent nozzle must terminate at least 150mm above the top of the filling nozzle. FAB0069 | 2031-01-27 | FAB0093
TNK20548 | 2026-02-27 | Go Industrials |  | AS 1692 SWI Reduced Secondary Containment for Tanks | Description: GOBOX 495L Self Bunded Tank Design Specification: AS 1692, SWI Reduced Secondary Containment for Tanks Tank Type: Above Ground Stationary Tank Drawing Numbers: GOBOX-2026MAR-495, Rev: 02 sheets 1-4 & GOBOX-2026MAR-495 Rev: 01 Name of Designer: Go Industrials Capacity: 495L Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | GO INDUSTRIAL PTY LTD Suite 15229 17B Farnham Street Parnell Auckland 1052 New Zealand | Specific Gravity: 1.0 Seismic & wind design: AS/NZS1170.2 & NZ1170.5 by Mikhail Joseph Tank can be used to supply a burner. Site location: NZ wide | 2036-02-27
TNK20549 | 2026-03-09 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 1612 litres maximum; 1500 litres SFL Drawing Numbers: Promax OPP8607-000-001-rev-C Name of Designer: Mech Eng Limited Description: Tank #PMX1005; HDPE Double walled, 1400mm OD x 1475mm HOA; 10mm WT, greater than 110% secondary containment. Split Tank: No | Name: Sodium hydroxide (Caustic soda) aqueous solution 50%w/w maximum s.g.1.53. Class(es): 6.1D, 8.1A, 8.2B, 8.3A | Promax Engineered Plastics Limited 389 Waipapa Road, Waipapa, Kerikeri 0295 | Construction to be in accordance with Promax Engineered Plastics Limited QA Documentation 2026. Design Report Tom Roberts, Mech Eng Limited Report 251081-RP01-revA | 2031-03-09
TNK20550 | 2026-03-12 | Consolidated Engineering Company Limited |  | AS3990-1993. | Tank Type: Above Ground Process Container Design Specification: AS3990-1993. Capacity: 1700 litres maximum; 1500 litres SFL Drawing Numbers: Stainless Engineering Co. Ltd.: 1940-01-A3 sht 1. Name of Designer: Consolidated Engineering Company Limited Description: Serial number 15645: Vertical cylinder, bottom cone, sealed and jacketed mixing vessel; 316 Stainless Steel 2.5mm WT, 1.6m HOA x 1.4m ID. Split Tank: No | Name: Miscellaneous proprietary pharmaceutical compounds. Class(es): 6.5B, 6.8B, 6.9B, 8.2C, 8.3A | Quantum Pacific Limited 14 Norman Spencer Drive Papatoetoe Auckland 2104 | This certificate is for a previously manufactured process vessel that has changed service duty. | 2031-03-12
TNK20551 | 2026-03-10 | Longveld |  | AS 1692 | Description: Vertical Single Skin Cone roof and bottom 304L S/S on legs Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Drawing Numbers: 28782-02000 5 shts Name of Designer: Longveld Capacity: 35,263 Litres Compartments: 1 | Name: 50% Sodium Hydroxide Class(es): 6.1D, 8.1A, 8.2B, 8.3A | LONGVELD LIMITED 153 - 157 Ellis Street, Frankton, Hamilton 3204 | This Tank is destined for Fonterra Pahiatua. SFL 34,050 Litres. | 2076-03-10
TNK20552 | 2026-03-10 | Longveld |  | AS 1693 | Description: Vertical Single Skin Cone roof and bottom 304L S/S on legs Design Specification: AS 1692 Tank Type: Above Ground Stationary Tank Drawing Numbers: 28782-01000 Name of Designer: Longveld Capacity: 20,000 Litres Compartments: 1 | Name: Nitric Acid 64% Class(es): 6.1D, 6.9B, 8.1A, 8.2B, 8.3A | LONGVELD LIMITED 153 - 157 Ellis Street, Frankton, Hamilton 3204 | This Tank is destined for Fonterra Pahiatua. SFL 19,020 Litres. | 2076-03-10
TNK20553 | 2026-03-13 | Fuelchief Limited | FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | AS1692: 2006 | Description: 37,176 Litres above ground, single skin, vertical, oval shape stationary tank Design Specification: AS1692: 2006 Tank Type: Above Ground Stationary Tank Drawing Numbers: VT-35,000 SP, Rev C MDA Corrected (13/03/2026), Sheet 1 of 1, Drawn: DL, Date: 26/02/2026 Name of Designer: Fuelchief Limited - DL Capacity: 37,176 Litres Compartments: 1 | Name: FramePro Class(es): 6.1D, 6.8B, 8.3A Name: MP200A RTU (5%) Class(es): 6.9B | FUELCHIEF LIMITED Innovation Park Lot 15/185 Kirk Road, Templeton, Christchurch 7675 | Motovated's Project Number: 8725. Design Specification: AS 1692:2006, Category 5. FAB No.: FAB0093. Manufacturer's Tank Serial No.: Name Plate. Date of Manufacture: Name Plate. Maximum Safe Fill Level = 34,453 Litres. Approved For: The storage and transfer of MP200A RTU (5%) having hazard classification 6.9B, 9.1B or FramePro having hazard classification 6.1D, 6.3A, 6.8B, 8.3A, 9.1A. References: 35kL Treatment Plant Tank PS1, Document number: 8724-0001, Rev 02, Issued By: Motovated Design and Analysis Ltd, To: FuelChief Ltd, To be Supplied to: Clutha District Council, In Respect of: New Build, At: 26 Duncan Road South, Tapanui 9542, We have been engaged by FuelChief Ltd to provide: Structural assessment of a new 35kL chemical tank, The design carried out by Motovated Design and Analysis Ltd has been prepared in accordance with: compliance documents issued by the Ministry of Business, Innovation & Employment (Verification method/acceptable solution): VM1, Signed by: Stuart Jackson (CPEng number 2011869), Date: 13Mar26. Unique serial number to be allocated for tank. Tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with the Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-03-13 | FAB0093
TNK20554 | 2026-03-23 | Caterpillar | BAOKAI No. 15-3, Jianshe 6th Road, BeizhakouTown, Jinnan District, Tianjin, China FAB0101 | BS 799-5 | Description: C9 - 558L above ground, double skin, rectangular, generator base tank design Design Specification: BS 799-5 Tank Type: Above Ground Stationary Tank Drawing Numbers: 606-5586, Title: BASE GP-F TANK & (9L DUAL WALL 530L), Sheets: 1 to 2, Rev E Name of Designer: Caterpillar Capacity: 558 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | CATERPILLAR INC. No.2 Xi Er Road, Tianjin Port Free Trade Zone (Airport), Tianjin 300308, PR CHINA | Terra Cat (Terra Industrial New Zealand Limited) authorised by Caterpillar Inc. as the supplier, installer and product support agent within New Zealand and Pacific Islands. Terra Industrial New Zealand Limited details as follows: - Address: 27 Enterprise Ave, Christchurch, 8042. - Contact person: Steve Lawson, Email: Steve.Lawson@terracat.co.nz & Phone: +64 27 217 1381. Design Specification: BS 799-5:2010 & Health and Safety at Work (Hazardous Substances—Above Ground Stationary Tanks Connected to a Generator Set) Safe Work Instrument 2017. FAB No.: Baokai. Manufacturer's Tank Serial No.: Name Plate. Date of Manufacture: Name Plate. Maximum Safe Fill Level = 501 Litres. Approved Drawings: - 6V-9830, CAP, Sheet: 1, Rev B. - 510-1036, CAP-VENT, Sheet: 1, Rev B. - 605-9559, PLATE AS-BUND, Sheet: 1, Rev C. - 605-9560, PLATE-BUND, Sheet: 1, Rev D. - 606-4903, BASE AS (9L DUAL WALL 530L), Sheet: 1, Rev D. - 606-4906, BASE AS, Sheet: 1, Rev E. - 606-4911, TANK AS (INNER 530L), Sheet: 1, Rev E. - 514-6660, PLUG-BSPP (EXTERNAL HEX.), Sheet: 1, Rev B. - 606-5586, BASE GP-F TANK & (9L DUAL WALL 530L), Sheet: 1 OF 1, Rev E. - 606-5586, BASE GP-F TANK & (9L DUAL WALL 530L), Sheet: 2 OF 2, Rev E. - TYPICAL NAME PLATE - Revised - Supplied 18-Feb-26. - P0000XX.X.XX, CATEPILLAR TYPICAL BUND INSPECTION DETAIL, Sheet: 1, Rev B. Approved For: The storage and transfer of diesel having hazard classification 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved to supply a generator. References: 8736-0001, Generator Base Tank and Anchoring Design Statement, Rev00, Released, 17Dec25. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-03-23 | FAB0101
TNK20555 | 2026-03-23 | Caterpillar | YUAO Dacheng zhuang Village, Da mengzhuangTown, Wuqing, Tianjin, China FAB0100 | BS 799-5 | Description: C15 - 960L above ground, double skin, rectangular, generator base tank design Design Specification: BS 799-5 Tank Type: Above Ground Stationary Tank Drawing Numbers: 608-5636, Title: BASE GP-ENGIN& GENERATOR (15L DEFRA), Sheet: 1, Rev D Name of Designer: Caterpillar Capacity: 960 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | CATERPILLAR INC. No.2 Xi Er Road, Tianjin Port Free Trade Zone (Airport), Tianjin 300308, PR CHINA | Terra Cat (Terra Industrial New Zealand Limited) authorised by Caterpillar Inc. as the supplier, installer and product support agent within New Zealand and Pacific Islands. Terra Industrial New Zealand Limited details as follows: - Address: 27 Enterprise Ave, Christchurch, 8042. - Contact person: Steve Lawson, Email: Steve.Lawson@terracat.co.nz & Phone: +64 27 217 1381. Design Specification: BS 799-5:2010 & Health and Safety at Work (Hazardous Substances—Above Ground Stationary Tanks Connected to a Generator Set) Safe Work Instrument 2017. FAB No.: Yuao. Manufacturer's Tank Serial No.: Name Plate. Date of Manufacture: Name Plate. Maximum Safe Fill Level = 910 Litres. Approved Drawings: - 604-3112, CAP-FUEL (3 INCH BSPP), Sheet: 1, Rev D. - 510-1036, CAP-VENT, Sheet: 1, Rev B. - 608-5636, BASE GP-ENGIN& GENERATOR (15L DEFRA), Sheet: 1, Rev D. - 608-5636, BASE GP-ENGIN& GENERATOR (15L DEFRA), Sheet: 2, Rev D. - 608-5635, BASEFRAME AS (15L DEFRA BASE), Sheet: 1, Rev C. - 608-5634, BASE AS-TANK (INNER), Sheet: 1, Rev D. - 608-0164, PLATE AS-BUND, Sheet: 1, Rev D. - 606-5574, BASEFRAME AS (15L/13L DEFRA), Sheet: 1, Rev E. - TYPICAL NAME PLATE - Revised - Supplied 18-Feb-26. - P0000XX.X.XX, CATEPILLAR TYPICAL BUND INSPECTION DETAIL, Sheet: 1, Rev B. Approved For: The storage and transfer of diesel having hazard classification 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved to supply a generator. References: 8736-0001, Generator Base Tank and Anchoring Design Statement, Rev00, Released, 17Dec25. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2026-03-23 | FAB0100
TNK20556 | 2026-03-23 | Caterpillar | YUAO Dacheng zhuang Village, Da mengzhuangTown, Wuqing, Tianjin, China FAB0100 | BS 799-5 | Description: C13 - 960L above ground, double skin, rectangular, generator base tank design Design Specification: BS 799-5 Tank Type: Above Ground Stationary Tank Drawing Numbers: 606-5573, Title: BASEFRAME AS (15L/13L DEFRA BASE), Sheet: 1, Rev C Name of Designer: Caterpillar Capacity: 960 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | CATERPILLAR INC. No.2 Xi Er Road, Tianjin Port Free Trade Zone (Airport), Tianjin 300308, PR CHINA | Terra Cat (Terra Industrial New Zealand Limited) authorised by Caterpillar Inc. as the supplier, installer and product support agent within New Zealand and Pacific Islands. Terra Industrial New Zealand Limited details as follows: - Address: 27 Enterprise Ave, Christchurch, 8042. - Contact person: Steve Lawson, Email: Steve.Lawson@terracat.co.nz & Phone: +64 27 217 1381. Design Specification: BS 799-5:2010 & Health and Safety at Work (Hazardous Substances—Above Ground Stationary Tanks Connected to a Generator Set) Safe Work Instrument 2017. FAB No.: Yuao. Manufacturer's Tank Serial No.: Name Plate. Date of Manufacture: Name Plate. Maximum Safe Fill Level = 910 Litres. Approved Drawings: - 604-3112, CAP-FUEL (3 INCH BSPP), Sheet: 1, Rev D. - 6V-9830, CAP (ORFS), Sheet: 1, Rev B. - 510-1036, CAP-VENT, Sheet: 1, Rev B. - 611-7517, HOSE AS, Sheet: 1, Rev B. - 611-3998, BASEFRAME GP (13L DEFRA), Sheet: 1, Rev D. - 611-3998, BASEFRAME GP (13L DEFRA), Sheet: 2, Rev D. - 252-4878, CAP, Sheet: 1, Rev C. - 514-6660, PLUG-BSPP (EXTERNAL HEX.), Sheet: 1, Rev B. - 606-5573, BASEFRAME AS (15L/13L DEFRA BASE), Sheet: 1, Rev C. - 606-5574, BASEFRAME AS (15L/13L DEFRA), Sheet: 1, Rev E. - 606-5575, BASE AS-TANK (INNER), Sheet: 1, Rev D. - 611-3996, PLATE AS-BUND, Sheet: 1, Rev D. - TYPICAL NAME PLATE - Revised - Supplied 18-Feb-26. - P0000XX.X.XX, CATEPILLAR TYPICAL BUND INSPECTION DETAIL, Sheet: 1, Rev B. Approved For: The storage and transfer of diesel having hazard classification 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved to supply a generator. References: 8736-0001, Generator Base Tank and Anchoring Design Statement, Rev00, Released, 17Dec25. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-03-23 | FAB0100
TNK20557 | 2026-03-23 | Caterpillar | YUAO Dacheng zhuang Village, Da mengzhuangTown, Wuqing, Tianjin, China FAB0100 | BS 799-5 | Description: C18 - 1223L above ground, double skin, rectangular, generator base tank design Design Specification: BS 799-5 Tank Type: Above Ground Stationary Tank Drawing Numbers: 606-5588, Title: BASE GP-ENGINE & GENERATOR (18L DEFRA), Sheet: 1, Rev D Name of Designer: Caterpillar Capacity: 1,223 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | CATERPILLAR INC. No.2 Xi Er Road, Tianjin Port Free Trade Zone (Airport), Tianjin 300308, PR CHINA | Terra Cat (Terra Industrial New Zealand Limited) authorised by Caterpillar Inc. as the supplier, installer and product support agent within New Zealand and Pacific Islands. Terra Industrial New Zealand Limited details as follows: - Address: 27 Enterprise Ave, Christchurch, 8042. - Contact person: Steve Lawson, Email: Steve.Lawson@terracat.co.nz & Phone: +64 27 217 1381. Design Specification: BS 799-5:2010 & Health and Safety at Work (Hazardous Substances—Above Ground Stationary Tanks Connected to a Generator Set) Safe Work Instrument 2017. FAB No.: Yuao. Manufacturer's Tank Serial No.: Name Plate. Date of Manufacture: Name Plate. Maximum Safe Fill Level = 1,160 Litres. Approved Drawings: - 604-3112, CAP-FUEL (3 INCH BSPP), Sheet: 1, Rev D. - 510-1036, CAP-VENT, Sheet: 1, Rev B. - 605-9559, PLATE AS-BUND, Sheet: 1, Rev C. - 605-9560, PLATE-BUND, Sheet: 1, Rev D. - 606-5578, BASE AS (18L DEFRA BASE), Sheet: 1, Rev C. - 606-5579, BASE AS-TANK (8 HR)(18L), Sheet: 1, Rev E. - 606-5580, TANK AS (18L DEFRA BASE), Sheet: 1, Rev E. - 606-5581, BEAM-LH (18L), Sheet: 1, Rev E. - 606-5582, PLATE-TOP, Sheet: 1, Rev E. - 606-5588, BASE GP-ENGINE & GENERATOR (18L DEFRA), Sheet: 1, Rev D. - 606-5588, BASE GP-ENGINE & GENERATOR (18L DEFRA), Sheet: 2, Rev D. - TYPICAL NAME PLATE - Revised - Supplied 18-Feb-26. - P0000XX.X.XX, CATEPILLAR TYPICAL BUND INSPECTION DETAIL, Sheet: 1, Rev B. Approved For: The storage and transfer of diesel having hazard classification 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved to supply a generator. References: 8736-0001, Generator Base Tank and Anchoring Design Statement, Rev00, Released, 17Dec25. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-03-23 | FAB0100
TNK20558 | 2026-03-23 | Caterpillar | YUAO Dacheng zhuang Village, Da mengzhuangTown, Wuqing, Tianjin, China FAB0100 | BS 799-5 | Description: C18 - 1442L above ground, double skin, rectangular, generator base tank design Design Specification: BS 799-5 Tank Type: Above Ground Stationary Tank Drawing Numbers: 605-9552, Title: BASE GP-ENGINE & (GENERATOR), Sheets: 1 to 2, Rev E Name of Designer: Caterpillar Capacity: 1,442 Litres Compartments: 1 | Name: Diesel Class(es): 3.1D, 6.7B | CATERPILLAR INC. No.2 Xi Er Road, Tianjin Port Free Trade Zone (Airport), Tianjin 300308, PR CHINA | Terra Cat (Terra Industrial New Zealand Limited) authorised by Caterpillar Inc. as the supplier, installer and product support agent within New Zealand and Pacific Islands. Terra Industrial New Zealand Limited details as follows: - Address: 27 Enterprise Ave, Christchurch, 8042. - Contact person: Steve Lawson, Email: Steve.Lawson@terracat.co.nz & Phone: +64 27 217 1381. Design Specification: BS 799-5:2010 & Health and Safety at Work (Hazardous Substances—Above Ground Stationary Tanks Connected to a Generator Set) Safe Work Instrument 2017. FAB No.: Yuao. Manufacturer's Tank Serial No.: Name Plate. Date of Manufacture: Name Plate. Maximum Safe Fill Level = 1,362 Litres. Approved Drawings: - 604-3112, CAP-FUEL (3 INCH BSPP), Sheet: 1, Rev D. - 6V-9830, CAP (ORFS), Sheet: 1, Rev B. - 510-1036, CAP-VENT, Sheet: 1, Rev B. - 605-9559, PLATE AS-BUND, Sheet: 1, Rev C. - 605-9560, PLATE-BUND, Sheet: 1, Rev D. - 371-1798, HOSE AS., Sheet: 1, Rev B. - 514-6660, PLUG-BSPP (EXTERNAL HEX.), Sheet: 1, Rev B. - 605-9552, BASE GP-ENGINE & (GENERATOR), Sheet: 1, Rev E. - 605-9552, BASE GP, Sheet: 2, Rev E. - 605-9553, BASE AS, Sheet: 1, Rev E. - 605-9554, BASE AS, Sheet: 1, Rev E. - 605-9554, BASE AS, Sheet: 2, Rev E. - 605-9555, TANK AS, Sheet: 1, Rev E. - 605-9555, TANK AS, Sheet: 2, Rev E. - 605-9556, BEAM, Sheet: 1, Rev E. - 605-9557, PLATE, Sheet: 1, Rev E. - 670-9697, INSTALLATION AR, Sheet: 1, Rev E. - TYPICAL NAME PLATE - Revised - Supplied 18-Feb-26. - P0000XX.X.XX, CATEPILLAR TYPICAL BUND INSPECTION DETAIL, Sheet: 1, Rev B. Approved For: The storage and transfer of diesel having hazard classification 3.1D, 6.1E, 6.3B, 6.7B, 9.1B. Approved to supply a generator. References: 8736-0001, Generator Base Tank and Anchoring Design Statement, Rev00, Released, 17Dec25. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-03-23 | FAB0100
TNK20559 | 2026-03-24 | Fuelchief Limited |  | AS 1692 | Tank Type: Above Ground, Steel, Double Skin Design Specification: AS 1692 Capacity: 65,900 litres maximum; 62,600 litres SFL Drawing Numbers: SPS-TT65-DR001; SPS-TT65-DR002; SPS-TT65-DR003; SPS-TT65-DR004 Name of Designer: Fuelchief Limited Description: FC682026012501: Category 3, integral secondary containment greater than 110%. Split Tank: No | Name: Diesel UN3082/UN1202 Class(es): 3.1D | Fuelchief Limited Innovation Park, Lot 15/185 Kirk Road Templeton Christchurch 7678 | This certificate is for a one off tank manufactured by Superise Heavy Industry Machinery Co Ltd, No.5 East Xinjing Road, Yangshe Town, Zhangjiagang City, Jiangsu Province, China | 2031-03-24
TNK20560 | 2026-03-24 | Fuelchief Limited |  | AS 1692 | Tank Type: Above Ground, Steel, Double Skin Design Specification: AS 1692 Capacity: 65,900 litres maximum; 62,600 litres SFL Drawing Numbers: SPS-TT65-DR001; SPS-TT65-DR002; SPS-TT65-DR003; SPS-TT65-DR004 Name of Designer: Fuelchief Limited Description: FC68-2026012502: Category 3, integral secondary containment greater than 110%. Split Tank: No | Name: Diesel UN3082/UN1202 Class(es): 3.1D | Fuelchief Limited Innovation Park, Lot 15/185 Kirk Road Templeton Christchurch 7678 | This certificate is for a one off tank manufactured by Superise Heavy Industry Machinery Co Ltd, No.5 East Xinjing Road, Yangshe Town, Zhangjiagang City, Jiangsu Province, China | 2031-03-24
TNK20561 | 2026-03-24 | Eneraque Pty Limited |  | AS 1692 | Tank Type: Above Ground, Steel, Double Skin Design Specification: AS 1692 Capacity: 1720 litres maximum; 1700 litres SFL Drawing Numbers: 12420-PD-DWG-00001 rev B Shts 1-3 Name of Designer: Eneraque Pty Limtied Description: ENR-BT1700-260224NZ: Generator Engine Belly Tank - Category 3; 3.5m LOA x 1.4m W x 0.5m H x 5mm WT, double skinned > 110% secondary containment. Split Tank: No | Name: Diesel only UN3082/UN1202 Class(es): 3.1D | Eneraque NZ Limited 40 Onehunga Mall Onehunga Auckland 1061 | One off tank construction. Manufactured by FUZHOU UNIWELL POWER EQUIPMENT Co. Ltd. Stationary container system certification to verify manufacturer QA for fabrication of the tank. Tank vent to be fitted such that it terminates external to the generator engine container a minimum of 150mm above the tank top and the tank fill point. | 2031-03-24
TNK20562 | 2026-03-25 | Mech Eng Limited |  | BS EN 12573 SWI Thermoplastic Tanks | Tank Type: Above Ground Stationary Tank Design Specification: BS EN 12573 SWI Thermoplastic Tanks Capacity: 8650 litres maximum; 7500 litres SFL Drawing Numbers: Plastics Constructions MA-6002-Sheet 1; MA-6002-sheet 2 Name of Designer: Mech Eng Limited Description: T#3457: HPDE integral secondary contained, Primary Tank 2100mm DIA x 2500mm H. Secondary containment 3100mm x 2700mm HOA Split Tank: No | Name: Poly-aluminium chloride 23% aqueous solution maximum 1.35 s.g. Class(es): 6.1D, 8.3A | Plastics Constructions Limited 26 Fremlin Place Avondale Auckland 1026 | Design Report Mech Eng Limited 252281-RP01-RevA Tank to constructed in accordance with Plastics Constructions Ltd QA Documents March 2026. | 2031-03-25
FAB0100 | 2026-03-31 |  | YUAO Dacheng zhuang Village, Da mengzhuangTown, Wuqing, Tianjin, China | BS 799-5:2010 | Approved for the shop fabrication of steel tanks in accordance with BS 799-5:2010 for which TNK numbers have been registered with WorkSafe New Zealand. Reference: TNK20555, TNK20556, TNK20557, TNK20558 | Name: Diesel Class(es): 3.1D, 6.7B | YUAO Dacheng zhuang Village, Da mengzhuangTown, Wuqing, Tianjin, China | Yuao are authorised by Caterpillar Inc. and on behalf of Terra Cat (Terra Industrial New Zealand Limited) to fabricate listed TNK numbers. Approved for the shop fabrication of steel tanks in accordance with BS 799-5:2010 for which TNK numbers have been registered with WorkSafe NewZealand. Allocation of unique individual tank serial number to be stamped on each individual tank and recorded. Retention of individual tank fabrication, testing records and QA records for each tank. | 2029-03-31 | Fabricator of: TNK20555 TNK20556 TNK20557 TNK20558
FAB0101 | 2026-03-31 |  | BAOKAI No. 15-3, Jianshe 6th Road, BeizhakouTown, Jinnan District, Tianjin, China | BS 799-5:2010 | Approved for the shop fabrication of steel tanks in accordance with BS 799-5:2010 for which TNK numbers have been registered with WorkSafe NewZealand. Reference: TNK20554 | Name: Diesel Class(es): 3.1D, 6.7B | BAOKAI No. 15-3, Jianshe 6th Road, BeizhakouTown, Jinnan District, Tianjin, China | Baokai are authorised by Caterpillar Inc. and on behalf of Terra Cat (Terra Industrial New Zealand Limited) to fabricate listed TNK numbers. Approved for the shop fabrication of steel tanks in accordance with BS 799-5:2010 for which TNK numbers have been registered with WorkSafe NewZealand. Allocation of unique individual tank serial number to be stamped on each individual tank and recorded. Retention of individual tank fabrication, testing records and QA records for each tank. | 2029-03-31 | Fabricator of: TNK20554
TNK20563 | 2026-04-22 | Martin Engineering (PN) Limited | Martin Engineering (Palmerston North) Ltd. PO Box 5295, Terrace End, Palmerston North, 4441 891 Tremaine Avenue, Roslyn, Palmerston North, 4414 | AS 1692 | Tank Type: Above Ground, Steel, Double Skin Design Specification: AS 1692 Capacity: 495 litres Maximum; 480 litres SFL Drawing Numbers: MEL-495-DS sheets 1-14 Rev A Name of Designer: Martin Engineering (PN) Limited Description: Tank Model: MEL-495-DS(110%); Double skinned Category 3 1200mm x 1070 mm x 537 mm x 4mm WT primary and secondary tanks, greater than 110% secondary containment. Split Tank: No | Name: Diesel and Re-refined waste oil Class(es): 3.1D, 6.7B | Martin Engineering (PN) Limited 891 Tremaine Avenue Roslyn Palmerston North 4414 | Design meets the requirements for a tank supplying a burner or engine subject to Regulation Part 17: Subpart 11—Installations for burning class 3.1 substance or substance approved by EPA. Vent to terminate a minimum of 150mm above the tank top surface when fitted for use. | 2031-04-21 | FAB0045
TNK20564 | 2026-04-24 | Fuelchief Limited | FUELCHIEF LIMITED PO Box 160175, Hornby, Christchurch, 8441 Innovation Park Lot 15, 185 Kirk Road Templeton, ChristChurch, 7675 | UL 142 FAB0093 | Description: SuperVault - 22,885L above ground fire rated double skin horizontal cylindrical stationary tank Design Specification: UL 142 Tank Type: Above Ground Stationary Tank Drawing Numbers: SV4-22,800, Rev D, Date: 20/04/2026 Name of Designer: Fuelchief Limited - DL Capacity: 22,885 Litres Compartments: 1 | Name: Sarmix Oxcel C Class(es): 6.1B, 6.1C, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 6.9A, 8.1A, 8.2B, 8.3A | Fuelchief Limited Innovation Park, Lot 15/185 Kirk Road Templeton Christchurch 7678 | Design Specifications: UL142, SwRI 95-03, SwRI 93-01, AS1692 and AS1940. Approved For: The storage and transfer of Sarmic Oxcel C having a hazard classification of 6.1B, 6.1C, 6.5A, 6.5B, 6.6A, 6.7A, 6.8A, 6.9A, 8.1A, 8.2B, 8.3A, 9.1A. References: Design Review Certificate: M5679-DRS-001 R01 Pack_signed. SuperVault MH Tank SwRI certificate: Fuelchief Ltd_SwRI 95-03 Certificate, Document No: 08177-03-02. O'Loughlan Taylor Spence Ltd Design Certificate 3375/JSO. Babbage Consultants Ltd Compliance Letter 22/05/2015. Unique serial number to be allocated for each individual tank. Individual tank fabrication and testing records to be retained. The TNK register number is to be marked on the tank nameplate in addition to the manufacturer's serial number, date of manufacture, pressure test in kPa and safe fill level. All other markings to comply with Hazardous Substances Regulations. Re-certification required following any change to the referenced contents, original design, duty, service conditions, amendments to the referenced design drawings or applicable standards. | 2036-04-24 | FAB0093